## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | FD Installation Checklist |  |  |  |  | Yes | FD Installation Checklist | 013cc077-aa3a-48d3-a1ac-783939529381
checkpoint-status |  |  | checkpoint | FD Dimensions
text | 47fc8685-4c57-583b-8733-382dee4f9efc |  | textbox | Drawing #
label | d49ece0a-6887-5803-beaf-96410d97c743 |  | note | Min Penetration = (1.01W + 10mm) x (1.01H + 10mm)
label | 777d63e9-5d91-5700-b35c-7813d2d56f2c |  | note | Max Penetration = (W+F) x (H+F)
label | 4f7503ca-4191-569b-b896-dbbc3b846529 |  | note | F= Side of the angle against Fire Wall (mm)
label | 80bcaa5e-aa89-58c8-9478-4c1bad362b7b |  | note | AS.1682.2:2015
text | 37e3b955-cbb5-594e-ba08-52f1c889f3a6 |  | textbox | FD Size (W X H):
text | b58aedbf-de5d-5563-ab72-353827133b91 |  | textbox | Flange Size (F):
text | 81d02cfc-871a-51c9-814b-dbd223a368b3 |  | textbox | Minimum Peno Size (W X H):
text | 8c1adefd-b6af-5695-a809-5251ab6cd24d |  | textbox | Maximum Peno Size (W X H):
text | 4d8e8aea-fcba-5ba1-ae78-def79d318cc7 |  | textbox | Current Peno Size (W x H)
checkpoint-status |  |  | checkpoint | FD fully open; blades free to close and latch
checkpoint-status |  |  | checkpoint | FD orientation and air flow direction is correct
checkpoint-status |  |  | checkpoint | FD wholly within wall/ Slab; case is square
checkpoint-status |  |  | checkpoint | FD and Duct attached correctly/ Breakaway
checkpoint-status |  |  | checkpoint | Packing/expansion metal installed around casing
checkpoint-status |  |  | checkpoint | Opening in fire rated structure is correct
checkpoint-status |  |  | checkpoint | FD Flanges attached correctly
checkpoint-status |  |  | checkpoint | FD # corresponds to the one detailed on drawing
checkpoint-status |  |  | checkpoint | FD location corresponds to the one detailed on drawing
checkpoint-status |  |  | checkpoint | FD accessible for maintenance and service purposes
checkpoint-status |  |  | checkpoint | FD Installer Label complete
checkpoint-status |  |  | checkpoint | Fusible Link Fitted
checkpoint-status |  |  | checkpoint | Floor Mounted-2000 mm of Duct insulated above FD
checkpoint-status |  |  | checkpoint | Installation is approved
checkpoint-status |  |  | checkpoint | Corrective actions have been undertaken
checklist-flat |  |  | checklist | FD Installation Photos Checklist |  |  |  |  | Yes | FD Installation Photos Checklist | 10821078-9a56-4ce0-8505-04ff3c43ffd2
checkpoint-status |  |  | checkpoint | Penetration Width
checkpoint-status |  |  | checkpoint | Penetration Height
checkpoint-status |  |  | checkpoint | Left and/or Rigth Gap
checkpoint-status |  |  | checkpoint | Top and/or Bottom Gap
checkpoint-status |  |  | checkpoint | FD c/w Retention Angles
checkpoint-status |  |  | checkpoint | FD Open
checkpoint-status |  |  | checkpoint | FD Close
checkpoint-status |  |  | checkpoint | FD Break Away Joint
checkpoint-status |  |  | checkpoint | FD with AP
checkpoint-status |  |  | checkpoint | Gaps Around FD Sealed
checkpoint-status |  |  | checkpoint | Sticker
checkpoint-status |  |  | checkpoint | FD Open
checkpoint-status |  |  | checkpoint | FD Close
checkpoint-status |  |  | checkpoint | FD Break Away Joint
checkpoint-status |  |  | checkpoint | FD with AP
checkpoint-status |  |  | checkpoint | Gaps Around FD Sealed
checkpoint-status |  |  | checkpoint | Sticker