## ITP Cover Page
Waste water - Open Cut - Inspection and Test Plan
Project: Tauriko Enabling Project
Number and Revision: DN1210 - ITP 011 - Rev 0
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | Tauriko Enabling Project |  |  |  |  | ITP Number: |  |  | ITP 011
Project Number: |  |  | DN1210 |  |  |  |  | ITP Status: |  |  | Approved
ITP Description: |  |  | Wastewater- Open cut |  |  |  |  | Revision: | 1000 |  | 0
Contract Number: |  |  | 8287 |  |  |  |  | Drawing Sets: |  |  | 232735.02-WSP-DR-WST (03,10,102,103,201,202, 312,320,321,322, 323,324,325,326,327,328)
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | Section 22.1 to Section 22.13
Quality Specified: |  |  | ISO 9001:2015
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
0 | Draft for Approval | 22/10/2024 |  | Cordelia Girdler-Brown & Chris Benson | [5 empty] | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
[10 empty] | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection (Formal inspection activity to be undertaken and recorded) |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point (Review of text reports/records or other evidence of compliance) |  | SPEC | Specialist
SECTION 2A – ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM |  | CHRIS BENSON | [5 empty] | Downer PM |  | CHRIS BENSON
Downer QM |  | CORDELIA GIRDLER-BROWN | [5 empty] | Downer QM |  | CORDELIA GIRDLER-BROWN
Client (If Applicable) | [7 empty] | Client (If Applicable)

## ITP Master Body
Wastewater Inspection and Test Plan
Tauriko Enabling Works
DN1210 - ITP011 - REV 0
Item No. | Inspection and Test Point | Detail / Activity | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Testing Quantity Required (based from schedule qtys) | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | ConQA Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 1 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
1.1 | GENERAL
1.1.1 | Pipe Laying | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Wastewater Construction Work Pack- Open Cut Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
1.1.2 | Butt-Fusion Welding | Method statement | As Per Specification and IFC Drawings | PS- 22.9.4 | Wastewater Butt-Fusion Welding Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
1.1.3 | Electrofusion (EF) Welding | Method statement | As Per Specification and IFC Drawings | PS- 22.9.5 | Wastewater Electrofusion (EF) Welding Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
1.1.4 | Pipeline Pressure Testing | Method statement | As Per Specification and IFC Drawings | PS- 22.3 Appendix V | Wastewater Pipeline Pressure Testing Work Pack Sign off | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
1.1.5 | Extent of Line Setout | Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings. Identify any clashes before construction. LOT- markup | As Per Drawings & Markup drawing | Design Drawings | ITP Sign Off / Mark-up | Prior to Construction & Every Revision of IFC Drawings/Data. | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
1.1.6 | Existing Wastewater system (If any) | Confirmation of existing Wastewater network. | Survey Informations | Appendix V | Survey data | Prior to Construction | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
SECTION 2 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
2.1 | MATERIAL TESTING- Embedment
2.1.1 | Material grading: Materials (Imported sand and AP20) MDD | Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance. | Embedment Zone Material accordance with AS/NZS 2566.2 | PS 22.13.1 | Lab Test Report NZS 4407.3.8.1 | 1 Test for each additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  |  |  | Table 21.9 has been considered (we cant find table 20.10)
2.1.2 | Material grading: Materials (Imported sand and AP20) PSD | Bedding/Side Zone/ Overlay Zone/Embedment Zone compliance. | Embedment Zone Material accordance with AS/NZS 2566.2 | PS 22.13.1 | Lab Test Report NZS 4407.3.8.1 | 1 Test for each additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
2.2 | MATERIAL TESTING- Trench Fill
2.2.1 | Material grading: Materials (Excavated Pumice GAP65/AP65)MDD | Trench Fill and undercut material compliance. | Trench fill - TNZ F1 IFC Drawing WST-0320 PS- Stormwater Specification | PS 21.7.2 | Lab Test Report NZS 4407.3.8.1 | 1 Test for each additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  | .
2.2.2 | Material grading: Materials (Excavated Pumice GAP65/AP65)PSD | Trench Fill and undercut material compliance. | Trench fill - TNZ F1 IFC Drawing WST-0320 PS- Stormwater Specification | PS 21.7.2 | Lab Test Report NZS 4407.3.8.1 | 1 Test for each additional 1000m3 | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
2.2.3 | Weathering index: Materials (Excavated Pumice GAP65/AP65) | Trench Fill and undercut material compliance. | Trench fill - TNZ F1 IFC Drawing WST-0320 PS- Stormwater Specification | PS 21.7.2 | Lab Test Report NZS 4407.3.11 | 1 test per source | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
2.2.4 | Crushing Resistance: Materials (Excavated Pumice GAP65/AP65) | Trench Fill and undercut material compliance. | Trench fill - TNZ F1 IFC Drawing WST-0320 PS- Stormwater Specification | PS 21.7.2 | Lab Test Report NZS 4407.3.10 | 1 test per source | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG |  |  | .
2.3 | MATERIAL TESTING- Pipes
2.3.1 | Pipes (PE/ Sleeve) | Manufacturer's record and location of extrusion plants. Name of the proposed PE resin, the manufacturer, production information on the properties of resin. Full Traceability information and certification of analysis for the resin batch. | Engineer approval | PS-22.4.1 (d) | Full Traceability information and certification of Material and resin. Delivery Dockets | Prior to Procurement | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
2.3.2 | Green Dome Odour Filter | A Green Dome Odour Filter (Model GDOF36) complete with DN150 ducting. | IFC Drawing 0323-1 | Model GDOF36 | Delivery Dockets | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
2.3.3 | Valves, Adaptors, Flanges and Fittings | Have a pressure rating no less than the designed pressure. Mechanically, chemically and electrically compatible with the class and material of the pipe. Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose. | Engineer approval AS/NZS 4129 | PS-22.4.2 | Delivery Dockets | Prior to Procurement | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
2.4 | MATERIAL DELIVERY
2.4.1 | Pipe and fittings. (PE100- DN200 PN10, DN180 PN10, DN400 PN16, DN500 PN16). | Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | As Per Drawings | Design Drawings | Delivery Dockets / Inspection Checksheet (DG-QA-TP019) | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
2.4.2 | Valves, Adaptors, Flanges and Fittings | Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition. | As Per Drawings | PS-22.4.2 | Delivery Dockets / Inspection Checksheet(DG-QA-TP019) | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
2.4.3 | Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65/LRAP65 and Drainage aggregate) | Confirm Specification and material in good condition. | Site Engineer Approval | PS-22.4.1 | Delivery Dockets | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
2.4.4 | Bidim/Geogrid | BIDIM A29 Durogrid 30/30 or similar. | Site Engineer Approval | PS-22.4.1 | Delivery Dockets | Each Delivery to site | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
SECTION 3 – CONSTRUCTION ACTIVITY
3.1 | WASTEWATER FLEXIBLE PIPELINE- Excavation and Laying
3.1.1 | Foundation Compliance | On Granular or Cohesive Material | Granular Material: Scala 3 blows/100mm (Or) Cohesive Material: Vane Shear Strength 70kPa | Appendix V | Scala/Shear test result | One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole. | W Review of text reports/records or other evidence of compliance | SE
3.1.2 | Undercut approval | Trench Foundation | 300mm Max cut IFC Drawing Sheet 320 (Or) Engineers approval | IFC Drawing WST 0320. AS/NZS 2566.2/2002 | Lab Test Report / Wastewater line record | If Undercut required | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.1.3 | Undercut Backfill Compliance (PAP5) | On Granular Material / On each layer as per specification / on the trench foundation. | Visiual Inspection | IFC Drawing WST 0320 | Lab Test Report / Wastewater line record | Every Undercut | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.1.4 | Bedding Zone Compaction Testing (PE Pipe). | On Granular Material / On each layer as per specification (Imported Sand or GAP20) | Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench. Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD | IFC Drawing 0320-1 AS/NZS 2566.2/2002 | Lab Test Report | As per SW Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.1.5 | Laying of Pipes | Lay in straight lines, beginning at the lower end of the line. Lay all pipe with manufacturing codes and class markings facing upwards. | As Per Drawings. Facing upwards | PS22.7.1 C | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.1.6 | Pipe Installation on Curved Alignments | All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202) | AS Per POP 202 | PS 22.7.1 D | Visual Inspection / Wastewater line record | Every Line | M Monitor on Random Basis | SE
3.2 | WASTEWATER FLEXIBLE PIPELINE- Joint and Connection
3.2.1 | Flanges | Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification. | Flanges to AS/NZS 4087 | PS 22.7.5 | Visual Inspection | First flanged joint | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.2.2 | Bends | PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings. Fitting must meets the same PN rating as the adjacent PE 100. Fittings must be suitable for producing the joints shown on the Drawings. | PIPA POP 006 and AS/NZS 4129 | PS 22.4.2 | Visual Inspection | As per the IFC drawing | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.3 | WASTEWATER FLEXIBLE PIPELINE- Butt-Fusion Welding
3.3.1 | Butt-Fusion pre construction weld test | One weld on the most common size of pipes used for the project. One weld on the thickest wall (highest PN) pipe | ISO 13953 for tensile strength and failure mode. WMS Report | PS 22.9.6 (a) | Visual Inspection | Two test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3.2 | Butt-Fusion Welding | Use only semi-automatic or automatic welding machines. Maintain a site record for all butt-fusion welds. The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct. | Site Butt Fusion Welding record to be filled out. (Refer to CWP) WMS Report | Appendix 22. PS 22.9.4 C | Visual Inspection / Butt Fusion welding records checklist. WMS Report | Every Welding Point | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3.3 | Butt-Fusion Construction weld test | Test at least two welds from the first 50 welds. One of the welds to be selected by the Engineer for satisfactory result. | Tensile testing and ductility of welds. | PS- 22.9.6 (a) (iv) | Test report | Two welds for the first 50 welds | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.3.4 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.4 | WASTEWATER FLEXIBLE PIPELINE- Electrofusion Welding
3.4.1 | Electrofusion (EF) pre construction weld test | Use the designated welding equipment and the approved WMS. On the largest size of PE pipe used in this Contract | ISO 21751 (strip-Bend test) or ISO 13954 (Peel-decohesion test) WMS Report | PS 22.9.6 (b) | Visual Inspection | One test welds per operative(Welder) | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4.2 | Electrofusion (EF) Welding | Required if Butt fusion welding cannot be perform. EF Jointing in accordance with PIPA POP 001. The lead welder or welding supervisor must verify on the site record form. | WMS Report Checklist (refer to CWP). | PS 22.9.5 Appendix 22 | Visual Inspection / Electrofusion (EF) welding record checklist. WMS Report | Every Welding Point | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.4.3 | Electrofusion (EF) construction weld test | EF weld quality to be maintained. | EF coupler and EF saddle testing | PS- 22.9.6 (b) (iv) | Test report | 1 in 10 test | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
3.4.4 | Survey | Inspection of Pipeline Inverts | Vertical design Setout: Pipes ≤ 1% grade: +/- 10mm variance Pipes > 1% grade: +/- 20mm variance Horizontal design Setout: +/-30mm variance | PS- 21.7.6 Table 21.15 | Survey Data / As-built record | Pipeline invert to be surveyed at chainages as indicated in the drawings. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.5 | WASTEWATER FLEXIBLE PIPELINE- Backfill
3.5.1 | Emebment Zone - (Side Haunch Overlay ) | Granular Sand backfill Compacted in 200mm Layers. NDM/CleggTesting to be completed on maximum 200mm lifts of overlays . NDM BS to be Carried Out | in 200mm layers. More than 85% of MDD. Or Minimum Compaction- Trafficable 95% MDD and Non-Trafficable 85% MDD | IFC Drawing 0320-1 | Lab Report / Wastewater line record | One test per 20m evenly spaced intervals. 200mm lift | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.5.2 | Pipe Markers | Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings. Mark fire hydrant positions in accordance with SNZ PAS 4509 | AS Per Drawings. | PS 22.7.3 a | Visual Inspection / Wastewater line record | Every Line | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.5.3 | Backfill Compaction Testing | GAP65/AP65/LRAP65 Backfill Compacted in 200mm Layers. NDM Testing to be completed on maximum 200mm lifts of backfill. | GAP65/AP65/LRAP65 Backfill Compacted in 200mm layers. Testing to be completed on maximum 200mm lifts of backfill. LRAP65- achive 90% NDM on Grassed Area and 95% NDM on Shared and Carriageway. | PS- 22.13.5 NDM Standerd 25832 NZS 4402 Test 4.1.3 | Lab Report / Wastewater line record | As per SW Specification. One test per 20m evenly spaced intervals. | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE
3.6 | WASTEWATER FLEXIBLE PIPELINE- Inspection
3.6.1 | Pipe Inspection | Inspection of Drainage line | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Internal | Wastewater line record | Continious 1 per Line | I Formal inspection activity to be undertaken and recorded. | SE
3.7 | WASTEWATER FLEXIBLE PIPELINE TESTING
3.7.1 | Pressure Acceptance Testing | Backfill/cover with embedment before testing End caps in place, provision for filling the pipeline and bleeding air. | Wastewater Rising Main Pipelines – 800kPa Ensure the STP is not more than 25% above the rated pressure of any pipeline component. | PS 22.7.12(d) PS 22.7.13(b) | Test Report Pressure Log in.csv or .xlsx format | All Pipeline All valves | HP Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | ENG
SECTION 4 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
4.1.1 | Survey As-Builts | Quality Check on Nee pipeline and structure based on the tolerances in RITS | Meets spec as per drawings and capture any NCR or change to design. | Project Specifications | Red pen markup only | Post works completion of a lot | H Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point. | SE