## Table 1
Document Information
| Document Title: | [7 empty] | Pile Installation ITP
| Document Title: | [7 empty] | ITP-ME-01
| Subcontractor: | [7 empty] | K&T Construction Australia/United Civil
| Client: | [7 empty] | Chint
| Project: | [7 empty] | Maungaturoto Solar Farm
Revision History
| Rev |  |  |  | Date | [5 empty] | Description |  | Originator |  |  | Checked |  | Approved
| 1 |  |  |  | 2024-10-25 | [5 empty] | For Approval |  | GS |  |  | ML |  | ML
PILE INSTALLATION ITP
Contract: | [5 empty] | Maungaturoto Solar Farm | [11 empty] | ITP Number: |  |  | ITP-ME-01
Activity / Item: | [5 empty] | Piles Installation
Contact Details | [11 empty] | Summary of Requirements | [5 empty] | Reference Drawings/Manuals/Standards |  |  |  |  | Records
Customer | [11 empty] | Pile Installation | [5 empty] |  520_02_01_Maungaturoto_FS2V-23°- 12_DUO_EX  520_02_02_Maungaturoto_FS2V-23°- 24_DUO_EX  DD-2412.011-REP-C1  Maungaturoto SF NZ_Layout Schletter_30.07.24  MSF-EN-GEN-DRG-001_1.2  MSF-EN-GEN-DRG-001_1.3 |  |  |  |  | (MDR Insert as marked 3)
Client PM | [22 empty] | Inspect Release Cert
Construction Manager | [22 empty] | Deviations/Concessions
Project Manager | [22 empty] | Material Certificates
Subcontractors | [11 empty] | Traceability: | [10 empty] | Conformance Certificate
Design: | [11 empty] | Material |  | Alloy Verification: | [8 empty] | Welding Records
Drafting: | [11 empty] | Heat Treatment |  | Pressure Testing: | [8 empty] | Welder Qual. Register
NDT: | [11 empty] | Consumable: |  | NDT | [8 empty] | NDT Reports
Pressure Test: | [11 empty] | Welder ID: |  | WPS | [8 empty] | Report on Repairs
Surface Treatment: | [11 empty] | Electrical: |  | Instrumentation | [8 empty] | Heat Treatment Records
Surveillance / Inspection Key | [11 empty] | Heat Treatment: N/A | [10 empty] | Non-Conformance Report
HOLD POINT (H): Nominated point beyond which work shall not proceed without verified acceptance by nominee. 48 hours of notice must be provided prior to commencement of works. | [22 empty] | Pressure Test Records
[12 empty] | Dimensional Control: N/A | [10 empty] | Drawing & Data Sheets
Misc. Verification Records
WITNESS POINT (W): Points at which the nominee shall be notified and invited to witness an activity, but further work may proceed without the presence of the nominee. | [11 empty] | Testing (NDT): N/A | [10 empty] | Dimensional Records
Position
[12 empty] | Acceptance Specification: IFC Drawings | [10 empty] | Construction Manager |  |  |  | CM
REVIEW (R): Verify by examination of documentary evidence that inspection / tests have been satisfactorily conducted. | [17 empty] | Procedures /Reports |  |  |  |  | Project Manager |  |  |  | PM
[12 empty] | Pressure Testing: N/A | [10 empty] | Quality Representative |  |  |  | QR
[18 empty] |  Piling SWMS  AS-BUILT Pile Stake Out Report |  |  |  |  | Technician |  |  |  | T
SURVEILLANCE (S): Continuing evaluation of the status of methods, analysis of records and monitoring of activities on a random basis to ensure quality of requirements will be met. | [11 empty] | Elect. / Instrumentation: N/A | [10 empty] | Document Controller |  |  |  | DC
[23 empty] | Subcontractor |  |  |  | SC
[12 empty] | Notes: | [10 empty] | Elect. / Instrumentation |  |  |  | E/I
VISUAL (V): 100% Visual inspection of work / item to ensure compliance with code / spec
DIMENSIONAL (D): Measurement of critical dimensions to ensure work/item is within tolerance
Contract: |  |  | Maungaturoto Solar Farm | [15 empty] | ITP Number: |  | ITP-ME-01
Activity / Item: |  |  | Piles Installation
ITEM NO: |  | PROCESS ACTIVITY | [5 empty] | PROCEDURE / INSTRUCTION | [6 empty] | ACCEPTANCE CRITERIA |  |  |  | VERIFYING DOCUMENT |  |  | VERIFICATION |  |  |  | REMARKS
[22 empty] | EPC |  | CLIENT
1.1 |  | Permits and Approvals | [5 empty] | Ensure Permits are in place including, but not limited to:  Excavation Permits | [6 empty] | Excavation Permit |  |  |  | Working Party to have access and sign onto permits where required. |  |  | H |  | R
1.2 |  | Identification of underground services | [5 empty] | Use of DBYD and other methods to positively identify underground services. | [6 empty] | Engineer to verify DBYD |  |  |  | DBYD / Excavation Permit Survey (if required) |  |  | H |  | R
1.3 |  | Approval of SWMS | [5 empty] | Submission, review, and approval of all SWMS for the works | [6 empty] | SWMS Approved | [6 empty] | H |  | NA
1.4 |  | Conformance of Materials | [5 empty] | All delivered materials and procured items conform to project specifications and IFC drawings. | [6 empty] | As per Drawings and specifications |  |  |  | Delivery Docket |  |  | R |  | S
1.5 |  | Inspection Measuring and Test Equipment (IMTE) Registers | [5 empty] | Supply of all calibration certificates to the engineer including but not limited to: Survey Equipment | [6 empty] | Visual |  |  |  | Calibration Certificates |  |  | R |  | S
2.1 |  | Survey and set out of piles | [5 empty] | Mark the ground in accordance with Schletter pile location | [6 empty] | • Visual as per Schletter pile location spreadsheet. |  |  |  | • Survey As Constructed record • Pile location spreadsheet |  |  | H |  | S
2.2 |  | Pile distribution to respective blocks | [5 empty] | Distribute colour coded piles, dimensions, and length into allocated location | [6 empty] | • Visual. Piles distributed as per Schletter drawings i.e., correct colour code, dimensions, and length. • Pile location CSV file |  |  |  | • Survey As Constructed record |  |  | R |  | S
2.3 |  | Pile refusal |  |  |  |  | Drive piles to depth until it reached point of refusal. | [7 empty] | • Record pile location and mark on the drawing • Record actual pile embedment depth • Pile refusal in accordance with Pile Refusal Procedure • Pile Testing Procedure • Piles cut and holes drilled as per Schletter documentation |  |  |  |  | • Survey record • Pile marked on the drawing • 1. Schletter - ITC – Piling • ITC Data Tracker Excel Pile Monitoring Sheet - Embedment Depth - Reveal Height • Pile test result documentation |  | S |  | S
2.4 |  | Piles installation |  |  |  |  | • Install pile on correct location as per Schletter drawing • Install pile within the design tolerances • Piles should have no damage or deformation and in correct orientation | [7 empty] | Tolerances as per Schletter Installation Manual Section 7.2 Installation Tolerances: • North-South 3° • East-West ± 3° • Pile Twisting from axis:± 5° • Distance E/W: ±100mm • N/S: ±50mm Reveal Height: ±100mm  Height difference foundation posts within one row: ±50mm • Piles have no damage deformation and in correct orientation. |  |  |  |  | • Schletter - ITC – Piling • Surveyset-out data • ITC Data Tracker Excel Pile Monitoring Sheet • Pile(s) marked on the As- Constructed drawing/Red Line Mark- up • Punchlist • Survey record |  | R |  | S
2.5 |  | Cold Galvanising Repair, if required |  |  |  |  | Use two coats of zinc rich galvanising paint on damage, deform, and top of piles | [7 empty] | • Galvanising repaired as per manufacturer’s recommendation and procedure. • Visual |  |  |  |  | • Schletter - ITC – Piling |  | R |  | S
2.6 |  | As Constructed records – Red Line Mark-Up (RLMU) Drawings. |  |  |  |  | Engineer to compile and record changes on IFC Drawings, to be issued to Client . | [7 empty] | Visual |  |  |  |  | RLMU Drawings |  | R |  | S
2.7 |  | Develop Punchlist |  |  |  |  | Development of punch list with PM/CM and/or Supervisor | [7 empty] | Punchlist closed in a timely manner |  |  |  |  | Punchlist |  | R |  | S
2.8 |  | Final Walk Down |  |  |  |  | 100% visual verification required for each pile upon ITP sign off | [7 empty] | Visual |  |  |  |  | Punchlist, if required |  | H |  | H
Contract: | [9 empty] | Maungaturoto Solar Farm | [8 empty] | ITP Number: | [5 empty] | ITP-ME-01
Activity / Item: | [9 empty] | Piles Installation
|  |  |  | Sub-Contractor Representative | [12 empty] | Client Representative
|  |  |  | Name: | [12 empty] | Name:
|  |  |  | Signature: | [12 empty] | Signature:
|  |  |  | Date: | [12 empty] | Date:
Page 5 of 5