## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-ME-01 Piling | itp |  |  |  |  | ITP-ME-01 Piling
section | Preconstruction
checkpoint | 1.1 - Permits and Approvals
label | PROCEDURE / INSTRUCTION - Ensure Permits are in place including, but not limited to:
label | ○ Excavation Permits
label | ACCEPTANCE CRITERIA - Excavation Permit
label | VERIFYING DOCUMENT - Working Party to have access and sign onto permits where required.
label | VERIFICATION: EPC - H
label | VERIFICATION: CLIENT - R
holdpoint | HOLD POINT
checkpoint | 1.2 - Identification of underground services
label | PROCEDURE / INSTRUCTION - Use of DBYD and other methods to positively identify underground services.
label | ACCEPTANCE CRITERIA - Engineer to verify DBYD
label | VERIFYING DOCUMENT - DBYD / Excavation Permit Survey (if required)
label | VERIFICATION: EPC - H
label | VERIFICATION: CLIENT - R
holdpoint | HOLD POINT
checkpoint | 1.3 - Approval of SWMS
label | PROCEDURE / INSTRUCTION - Submission, review, and approval of all SWMS for the works
label | ACCEPTANCE CRITERIA - SWMS Approved
label | VERIFICATION: EPC - H
label | VERIFICATION: CLIENT - NA
holdpoint | HOLD POINT
checkpoint | 1.4 - Conformance of Materials
label | PROCEDURE / INSTRUCTION - All delivered materials and procured items conform to project specifications and IFC drawings.
label | ACCEPTANCE CRITERIA - As per Drawings and specifications
label | VERIFYING DOCUMENT - Delivery Docket
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
checkpoint | 1.5 - Inspection Measuring and Test Equipment (IMTE) Registers
label | PROCEDURE / INSTRUCTION - Supply of all calibration certificates to the engineer including but not limited to:
label | ○ Survey Equipment
label | ACCEPTANCE CRITERIA - Visual
label | VERIFYING DOCUMENT - Calibration Certificates
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
section | Construction
checkpoint | 2.1 - Survey and set out of piles
label | PROCEDURE / INSTRUCTION - Mark the ground in accordance with Schletter pile location
label | ACCEPTANCE CRITERIA - Visual as per Schletter pile location spreadsheet.
label | VERIFYING DOCUMENT - Survey As Constructed record
label | ○ Pile location spreadsheet
label | VERIFICATION: EPC - H
label | VERIFICATION: CLIENT - S
holdpoint | HOLD POINT
checkpoint | 2.2 - Pile distribution to respective blocks
label | PROCEDURE / INSTRUCTION - Distribute colour coded piles, dimensions, and length into allocated location
label | ACCEPTANCE CRITERIA - Visual. Piles distributed as per Schletter drawings i.e., correct colour code, dimensions, and length.
label | ○ Pile location CSV file
label | VERIFYING DOCUMENT - Survey As Constructed record
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
checkpoint | 2.3 - Pile refusal
label | PROCEDURE / INSTRUCTION - Drive piles to depth until it reached point of refusal.
label | ACCEPTANCE CRITERIA - Record pile location and mark on the drawing
label | ○ Record actual pile embedment depth
label | ○ Pile refusal in accordance with Pile Refusal Procedure
label | ○ Pile Testing Procedure
label | ○ Piles cut and holes drilled as per Schletter documentation
label | VERIFYING DOCUMENT - Survey record
label | ○ Pile marked on the drawing
label | ○ 1. Schletter - ITC – Piling
label | ○ ITC Data Tracker Excel Pile Monitoring Sheet
label | – Embedment Depth
label | – Reveal Height
label | ○ Pile test result documentation
label | VERIFICATION: EPC - S
label | VERIFICATION: CLIENT - S
checkpoint | 2.4 - Piles installation
label | PROCEDURE / INSTRUCTION - Install pile on correct location as per Schletter drawing
label | ○ Install pile within the design tolerances
label | ○ Piles should have no damage or deformation and in correct orientation
label | ACCEPTANCE CRITERIA - Tolerances as per Schletter Installation Manual Section 7.2 Installation Tolerances:
label | ○ North-South 3°
label | ○ East-West ± 3°
label | ○ Pile Twisting from axis:± 5°
label | ○ Distance E/W: ±100mm
label | ○ N/S: ±50mm
label | ○ Reveal Height: ±100mm
label | ○ Height difference foundation posts within one row: ±50mm
label | ○ Piles have no damage deformation and in correct orientation.
label | VERIFYING DOCUMENT - Schletter - ITC – Piling
label | ○ Surveyset-out data
label | ○ ITC Data Tracker Excel Pile Monitoring Sheet
label | ○ Pile(s) marked on the As- Constructed drawing/Red Line Mark-up
label | ○ Punchlist
label | ○ Survey record
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
checkpoint | 2.5 - Cold Galvanising Repair, if required
label | PROCEDURE / INSTRUCTION - Use two coats of zinc rich galvanising paint on damage, deform, and top of piles
label | ACCEPTANCE CRITERIA - Galvanising repaired as per manufacturer’s recommendation and procedure.
label | ○ Visual
label | VERIFYING DOCUMENT - Schletter - ITC – Piling
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
section | Postconstruction
checkpoint | 2.6 - As Constructed records – Red Line Mark-Up (RLMU) Drawings
label | PROCEDURE / INSTRUCTION - Engineer to compile and record changes on IFC Drawings, to be issued to Client .
label | ACCEPTANCE CRITERIA - Visual
label | VERIFYING DOCUMENT - RLMU Drawings
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
checkpoint | 2.7 - Develop Punchlist
label | PROCEDURE / INSTRUCTION - Development of punch list with PM/CM and/or Supervisor
label | ACCEPTANCE CRITERIA - Punchlist closed in a timely manner
label | VERIFYING DOCUMENT - Punchlist
label | VERIFICATION: EPC - R
label | VERIFICATION: CLIENT - S
checkpoint | 2.8 - Final Walk Down
label | PROCEDURE / INSTRUCTION - 100% visual verification required for each pile upon ITP sign off
label | ACCEPTANCE CRITERIA - Visual
label | VERIFYING DOCUMENT - Punchlist, if required
label | VERIFICATION: EPC - H
label | VERIFICATION: CLIENT - H
holdpoint | HOLD POINT