## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CC0408 - ITP-006 - Trenching, Laying and Backfill for Box Culverts and Headwalls | itp |  |  |  |  | CC0408 - ITP-006 - Trenching, Laying and Backfill for Box Culverts and Headwalls
section | 1.0 Preliminaries
checkpoint | 1.1 - Safety and Environmental
label | Ref docs - N/A
label | Acceptance criteria - Ensure all safety components including SWMS, Plant prestart inspections and workers inducted are completed prior to works commencing.
label | ○ View and understand the applicable Site Environmental Management Plans.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
checkpoint | 1.2 - Determine Lot Size
label | Ref docs - N/A
label | Acceptance criteria - Each line
textbox | Acceptance
textbox | to
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Work Lot Map
checkpoint | 1.3 - Survey Setout
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all drainage lines including manholes, temporary benchmarks, sewage wet wells etc.
label | ○ Clearly mark limits of works.
label | ○ Chainage, offsets, cut/fill level, cutting slopes, grades and cross sections specified or shown on the drawings, etc.
label | ○ Peg location of proposed underground services with levels from pit to pit.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Footing Compaction
checkpoint | 2.1 - Excavate to width and depth as per survey
label | Ref docs - MRH/A0/B/00-CV/DWG/0019
label | Acceptance criteria - Trench depth shall allow for 600mm minimum cover from top of culvert, unless otherwise stated in Civil Drawings.
label | ○ Trench Width shall be 300mm each side of Culvert
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
checkpoint | 2.2 - Place Bedding
label | Ref docs - MRH/A0/B/00-CV/DWG/0046
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | Acceptance criteria - Compacted Bedding material shall be 100mm. When the pipe sections are in position, the bedding material shall be placed in the Haunch Zone and compacted to Density Index DI 50
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Test Report, Material Certificate
checkpoint | 2.3 - Lay culverts
label | Ref docs - MRH/A0/B/00-CV/DWG/0045/46/47
label | Acceptance criteria - Culverts alignments to comply with Melbourne Water and IFC tolerances.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-built
checkpoint | 2.4 - Backfilling
label | Ref docs - IFC Drawings
label | ○ MRH/A0/B/00-CV/DWG/0031
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | Acceptance criteria - Side Zone: Class 2 or 3 Crushed Rock to 90% Relative density, or min density index of 60.
label | ○ Overlay Zone:
label | – Class 2 or 3 Crushed Rock to 0.3m above the top of Culvert to 98% SMDD
label | ○ Backfill Zone:
label | – Class 2 or 3 Crushed Rock to 98% SMDD
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Test Report
section | 3.0 Headwalls
checkpoint | 3.1 - Geotextile
label | Ref docs - MRH/A0/B/00-CV/DWG/0011
label | ○ MRH/A0/B/00-ST/DWG/0020
label | Acceptance criteria - Top Surface of the erosion control mat to match FSL
label | ○ Needle-punched non-woven Geotextile (mass > 250g/m2) to trimmed surface and buried to a depth of 300mm at the edges of beaching with 300mm - 500mm Overlap or as otherwise specified by the Supplier Installation Guidelines
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if required
checkpoint | 3.2 - Rock beaching (Ungrouted)
label | Ref docs - MRH/A0/B/00-CV/DWG/0047
label | Acceptance criteria - Bedding Min. 250mm depth of size 20- 100mm graded Crushed rock
label | ○ Rocks placed mechanically / by hand for uniform interlocking layer
label | ○ Infill mix placed between rockwork (mix size 0-100mm) shall be graded crushed rock
label | ○ All rocks shall have a mass 20 and 70 kg and at least 60% of the total by number shall be over 40 kg
label | ○ Rocks shall be of such size that the layer of beaching is not less than 225 mm thick
label | ○ Rocks shall be keyed into Ground surface one third Diameter of rock
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if required
section | 4.0 Conformance Check
checkpoint | 4.1 - Asset recording
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | Acceptance criteria - Survey Pickup
label | ○ Redline markup of drawings:
label | – Have all changes been approved and are within tolerance?
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-built
holdpoint | AUTHORITY HOLDPOINT
checklist | CC0408 - ITP-004 - Stormwater Drainage | itp |  |  |  |  | CC0408 - ITP-004 - Stormwater Drainage
section | 1.0 Preliminaries
checkpoint | 1.1 - Determine Lot Size
label | Ref docs - N/A
label | Acceptance criteria - Each run
textbox | Acceptance
textbox | to
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Work Lot Map
checkpoint | 1.2 - Survey Set out
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all drainage lines including manholes, temporary benchmarks, sewage wet wells etc.
label | ○ Clearly mark limits of works.
label | ○ Chainage, offsets, cut/fill level, cutting slopes, grades and cross sections specified or shown on the drawings, etc.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Approved Material Type
label | Ref docs - AS1260
label | Acceptance criteria - In accordance with IFC Drawings:
bool | EnviroPipe
bool | PVC
bool | RCP
bool | StormPro
label | ○ All pipework to be clearly labelled & detectable to identify it as stormwater drainage.
label | Acceptance
textbox | Size/Class
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Delivery Dockets /Material certification
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Excavation of drainage trench
checkpoint | 2.1 - Excavation
label | Ref docs - AS3500
label | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | ○ Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
label | ○ Keep trench width & depth to that required by the service & pits bedding method.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if require
checkpoint | 2.2 - Removal of Obstructions
label | Ref docs - N/A
label | Acceptance criteria - Remove obstructions including roots, stumps, boulders and the like which may interfere with the proper functioning of the service
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if require
checkpoint | 2.3 - Water Management
label | Ref docs - EMP
label | Acceptance criteria - Symal shall maintain all excavations in a well-drained condition.
label | ○ No bedding material or pipe work shall be placed in excavations containing standing or running water.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if require
checkpoint | 2.4 - Bedding Material
label | Ref docs - MRHA0B0-CTDWG0020
label | ○ AS3725 Table 6 & 7
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | Acceptance criteria - All Pipes shall be installed with well graded washed clean sand to AS3725
label | ○ Bedding material to be placed the full width of the trench and not less than 100mm in thickness.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Test Report (PSD) Material Certificate
checkpoint | 2.5 - Compaction of Bedding
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | Acceptance criteria - Bedding material shall be compacted to refusal handheld mechanical equipment to Density Index DI 50
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Test Report
section | 3.0 Installation of drainage pipe
checkpoint | 3.1 - Pipe Installation
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | ○ AS 3500
label | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | ○ Pipes shall be bedded evenly to ensure sockets to not bear on the base of the trench
label | ○ Pipe laying shall commence at upstream end at downstream end of the run.
label | ○ All pipes shall be laid with sockets pointing upstream.
label | ○ Lay at min grade 1:100
label | ○ Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
label | ○ Keep trench width & depth to that required by the service & its bedding method.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if required
checkpoint | 3.2 - Pipe Grade
label | Ref docs - MRHA0B00-CVDWG0032 – 0034, 0048
label | Acceptance criteria - Install piping in straight lines at uniform grades without sags as per long section of drainage drawings.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-built Survey Report
checkpoint | 3.3 - Tolerances
label | Ref docs - IFC Drawings
label | Acceptance criteria - Unless otherwise specified, tolerances as follows:
label | ○ Invert level of pipes +10mm and –25mm
label | ○ Minimum fall within pits between incoming and outgoing pipes should be kept as 20mm
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-Built Survey Report
checkpoint | 3.4 - Pipe Fittings, Supports & Fixings
label | Ref docs - AS3500
label | Acceptance criteria - Provide all bends, junctions, inspection openings and other fittings as necessary for the completion of all systems.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Material Certificate Specification
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Pit Install
label | Ref docs - AS3500 IFC Drawings
label | Acceptance criteria - Pits are to be constructed in accordance with project specifications, with internal surfaces and exposed surfaces finished smooth & true.
label | ○ All pipe break-ins are to be made neat and finished smooth without gaps/cavities.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Material Certificate Specification
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Survey of Installed Services
label | Ref docs - IFC Drawings
label | Acceptance criteria - Accurately record the routes of underground cables and pipes before backfilling.
label | ○ Include on the record drawings.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-Built Survey Report
section | 4.0 Backfill
checkpoint | 4.1 - Backfill Material
label | Ref docs - IFC Drawings
label | Acceptance criteria - After pipes & fittings have been set in the correct position, jointed, and tested, further bedding material shall be used to fill all recesses below sockets, and bottoms of trenches.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Test Report (PSD) Material Certificate
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Layer Thickness
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | Acceptance criteria - Backfill material must be placed and compacted in maximum 150mm (Haunch and Side Zone) 200mm layers (Overlay and Backfill Zone).
label | ○ Backfill trenches as soon as possible after satisfactory testing & approval of laid and bedded service.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Photos, if required
checkpoint | 4.3 - Compaction Testing
label | Ref docs - MRH/A0/B/00-CV/DWG/0031
label | ○ MELBOURNE WATER DRAWING 7251/08/419
label | Acceptance criteria - Haunch Zone: Bedding Sand compacted to Relative Density 90% or Density Index DI 60
label | ○ Side Zone: Class 2 or 3 Crushed Rock Compacted to Relative Density 90%
label | ○ Overlay Zone: Class 2 or 3 Crushed Rock to 150mm above the top of pipe to 98% SMDD
label | ○ Backfill Zone: Class 2 or 3 Crushed Rock to 98% SMDD
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Compaction Test Report
section | 5.0 Conformance Check
checkpoint | 5.1 - Clean & Finish
label | Ref docs - IFC Drawings
label | Acceptance criteria - On completion, each drainage line shall be free from dirt, debris, or other impediments.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | CCTV Report, Photos
checkpoint | 5.2 - Visual Inspection
label | Ref docs - IFC Drawings
label | Acceptance criteria - Do not cover or conceal work until it has been inspected by Symal.
label | ○ Leave pipe joints exposed to enable witness inspections.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Visual Inspection onsite
checklist | CC0408 - ITP-010 - Fire Service Installation & Commissioning | itp |  |  |  |  | CC0408 - ITP-010 - Fire Service Installation & Commissioning
section | 1.0 Preliminaries
checkpoint | 1.1 - Determine Lot Size
label | Ref docs - AS3500
label | Acceptance criteria - Full Ring-main¬
button | Acceptance - See Work Lot Map | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Work Lot Map
checkpoint | 1.2 - Survey Set-out
label | Ref docs - MRHA0B00-FPDWG0006
label | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all fire lines including hydrants and risers.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
checkpoint | 1.3 - Approved Material Type
label | Ref docs - MRHA0B00-FPDWG0004-0005 AS3500 AS2419.1
label | Acceptance criteria - All materials selected in accordance with AS4130 and MREH civil specification and drawings.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Proof of each delivery (Delivery dockets/photo)
bool | Test Report/Material Certificate
checkpoint | 1.4 - Fusion Welding Equipment
label | Ref docs - AS2033 CI4 & PIPA (POP-001 & POP-003)
label | Acceptance criteria - Prior to welding commencing ensure Fusion Welding Equipment Calibration Certificate (every 3 months) and Welding Operator Qualification Certificate (every 2 years) are correct/approved prior to work commencement.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Calibration Certificate and Verification of competency
section | 2.0 In Process Works
checkpoint | 2.1 - Excavation
label | Ref docs - MRHA0B00-FPDWG0004-0009
label | ○ AS3500
label | ○ Excavation permit
label | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
checkpoint | 2.2 - Removal of Obstructions
label | Ref docs - MRHA0B00-FPDWG0004-0009
label | ○ AS2033
label | Acceptance criteria - Remove obstructions including roots, stumps, boulders, and the like which may, in the opinion of Symal, interfere with the proper functioning of the service.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - N/A
checkpoint | 2.3 - Bedding
label | Ref docs - MRHA0B00-FPDWG0005
label | ○ AS35000.1, AS2033
label | Acceptance criteria - Pipes should be bedded and supported with river sand.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - PSD Report
section | 3.0 Installation of pipes
checkpoint | 3.1 - Pipe Installation
label | Ref docs - MRHA0B00-FPDWG0004-0009
label | Acceptance criteria - Work shall be carried out by and under the direct supervision of appropriately licenced personnel.
label | ○ During construction, temporarily seal open ends of pipes and valves to prevent the entry of foreign matter into pipe systems.
label | ○ Install piping in straight lines at uniform grades without sags.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - Visual inspection
checkpoint | 3.2 - Electrofusion Weld fittings/pipe/couplings
label | Ref docs - AS4130 PIPA (POP1/ POP3 / POP14)
label | Acceptance criteria - Ensure pipe is cleaned and scraped prior to welding.
label | ○ Ensure pipe is fixed firmly in position.
label | ○ Allow curing time as per specific fittings recommendations.
label | ○ Visually check all fittings have been welded.
label | Acceptance - Prior to Backfilling
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Welding procedure specification/Procedure specifications records
bool | Welder Qualification record
checkpoint | 3.3 - Sluice valve
label | Ref docs - AS2419.1
label | Acceptance criteria - To comply with AS2419.1 and Drawing MRHA0B00-FPDWG004~0006
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Visual Inspection
checkpoint | 3.4 - Cover
label | Ref docs - AS3500.1
label | ○ MRHA0B00-FPDWG0005
label | Acceptance criteria - Minimum depth of cover for buried pipes:
label | ○ Min. 750mm from FSL
label | ○ Min. 150mm cover from compacted overlay.
label | ○ Min. 600mm cover from bottom of the conduits.
label | ○ Min. 100mm from side of trench wall.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-Built Attached
section | 4.0 Backfill
checkpoint | 4.1 - Backfill Material
label | Ref docs - AS3500
label | ○ MRHA0B00-FPDWG0005
label | Acceptance criteria - After pipes & fittings have been set in the correct position and jointed, further bedding material shall be used to fill all recesses below sockets, and bottoms of trenches.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | PSD Report
checkpoint | 4.3 - Layer Thickness
label | Ref docs - IFC Drawings
label | ○ AS3500
label | ○ MRHA0B00-CVDWG008
label | Acceptance criteria - Backfill material must be placed and compacted in layers not exceeding 200mm. Compaction requirement & thickness follows Earthworks package:
label | – 200mm compacted layer
label | – 1 x test per 2 layers per 40 linear meters
label | – Bench Filling 98% Standard
label | – Road Sub grade 100% Standard
label | – Road Sub base 95% Modified
label | – Road Base 98% Modified
label | ○ Fire Hydrant marker tape to be placed prior to backfill.
label | ○ Backfill trenches as soon as possible after approval of laid and bedded service.
label | ○ Allow adequate cover over pipe (minimum 600mm).
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - W
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Compaction test reports
checkpoint | 4.4 - Compaction
label | Ref docs - MRHA0B00-CVDWG0008
label | ○ AS1289
label | ○ AS3798
label | Acceptance criteria - Undertaken using hand methods only for first 300mm.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Compaction test reports
section | 5.0 Fire Hydrant Install
checkpoint | 5.1 - Survey set-out
label | Ref docs - MRHA0B00-FPDWG0006
label | Acceptance criteria - Prior to the commencement of works, the contractor shall engage a suitably qualified surveyor to set out the works and clearly mark its limits.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - Visual inspection
checkpoint | 5.2 - Approved Material Type
label | Ref docs - MRHA0B00-FPDWG0004-0009
label | ○ AS2419
label | Acceptance criteria - Materials used for the installation of Hydrants to be in accordance with AS2419
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Proof of delivery (Delivery docket/photos)
checkpoint | 5.3 - Fire Hydrant Install
label | Ref docs - MRHA0B00-FPDWG0004 – 0009
label | ○ AS2419.1
label | Acceptance criteria - Ensure fire hydrants are located such that they do not impact vehicle access.
label | ○ Bollards are to be installed for physical protection.
label | ○ Confirm valve operability.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - Photo, if required
section | 6.0 Conformance Check
checkpoint | 6.1 - Flushing (Clean & Finish)
label | Ref docs - N/A
label | Acceptance criteria - On completion, each line shall be free from dirt, debris, or other impediments.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | SGJV Key - S
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - Photo, if required
checkpoint | 6.2 - Hydrostatic Testing
label | Ref docs - AS2419
label | Acceptance criteria - All pipe and hydrants to be pressure tested in accordance with AS2419
label | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Principal Key - W
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Hydraulic Test Report
bool | Test certification.
bool | Calibration certificates
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.3 - As-Builts
label | Ref docs - MRHA0B00-FPDWG0006
label | Acceptance criteria - Accurately record the routes of all underground pipes before backfilling.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | SGJV Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-Built Attached
holdpoint | AUTHORITY HOLDPOINT