## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | AE-ITCX-010 - Torque Settings for Bolts (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-010 - Torque Settings for Bolts (Rev 0 +Names) | 05a88f5a-4213-437e-8a89-545509efab0a
checkpoint-group |  |  | section | Reference Tables
checkpoint-status |  |  | checkpoint | Torque Setting Tables - Pass once tables are confirmed/read
label | 11bae325-f1e5-52f2-a2ee-85eb9afaf1cf |  | note | .. ..
label | 696bfca6-70a8-5e37-ba8d-07244a6c3f24 |  | note | Lugged Cables
label | 4cb673ef-19a0-58c3-9327-ed797bfdfb1d |  | note | M6 - Class 8.8 Zinc plated - 9 Newton Meters
label | 4b4ce0e5-d541-570b-8e19-598c38a83249 |  | note | M8 - Class 8.8 Zinc plated - 22 Newton Meters
label | cb650b69-1857-5512-95e3-5762558b8d5a |  | note | M10 - Class 8.8 Zinc plated - 44 Newton Meters
label | 29b57d1c-709d-54e0-8aa2-14aea2db89d5 |  | note | M12 - Class 8.8 Zinc plated - 77 Newton Meters
label | 1050551b-a15c-530f-ad62-01fd21fa8314 |  | note | M16 - Class 8.8 Zinc plated - 190 Newton Meters
label | b494e091-cbf5-557e-ab94-b2a50b5ff6f2 |  | note | .. ..
label | 87ca5f54-5168-54c7-874a-1b9ec32ba6c4 |  | note | Bus Bars
label | 749b5f1d-87d3-500b-8b44-066bf13d03ce |  | note | M8 - Class 8.8 Zinc plated - 35 Newton Meters
label | b32ff409-5b32-5fb7-ad8b-3740620bf612 |  | note | M10 - Class 8.8 Zinc plated - 50 Newton Meters
label | b7039db5-1ba8-5983-b324-e005c16d6738 |  | note | M12 - Class 8.8 Zinc plated - 75 Newton Meters
label | 96a8b719-ef91-53ce-b6da-f9149b5b7a22 |  | note | M16 - Class 8.8 Zinc plated - 190 Newton Meters
label | 03de6fc1-109d-5b84-acec-40d0988b94f9 |  | note | .. ..
label | f2feedd8-8429-5fa5-81b4-05574a86ba2e |  | note | ALL BOLTS SUPPLIED BY SWITCHBOARD MANUFACTURES, INCLUDING ALINE, ARE GRADE 8.8 BOLTS AND SHOULD NOT BE SUBSTITUTED
label | 42e8e05d-154e-5fc1-b20d-4e251516abd7 |  | note | .. ..
label | 40b1f191-65b6-5c44-8d90-01e768e798e4 |  | note | Torque Settings for SAGAME IPCs
label | 59d6466d-caab-5a51-b272-05de61bea9af |  | note | TTD051XFA - 16 to 95 (Conductor Size MM2) - 1.5-10 (Branch Cable MM2) - 9 Newton Meters
label | 5b849caa-9a1c-55ee-8990-828236a3cf00 |  | note | TTD101XFA - 6 to 54 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 9 Newton Meters
label | 4dcf69d4-8471-52fe-802e-d91d0f8a8a89 |  | note | TTD151XFA - 25 to 95 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 14 Newton Meters
label | 76353075-c93b-579c-98cc-dfd05e758e51 |  | note | TTD201XFA - 35 to 95 (Conductor Size MM2) - 25 to 95 (Branch Cable MM2) - 18 Newton Meters
label | 484e6daf-a5e5-575e-9734-4b984f94ed4b |  | note | TTD241XFA - 50 to 150 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 14 Newton Meters
label | 13d3c87f-d0a3-587c-bd80-cea83505bf7e |  | note | TTD251XFA - 50 to 150 (Conductor Size MM2) - 35 to 95 (Branch Cable MM2) - 18 Newton Meters
label | 4e6bd82d-6000-512f-ade4-900c6de7fc44 |  | note | TTD301XFA - 25 to 95 (Conductor Size MM2) - 25 to 95 (Branch Cable MM2) - 14 Newton Meters
label | b24d92c9-5c32-50bc-80dd-754241e31139 |  | note | TTD341F - 50 to 150 (Conductor Size MM2) - 6 to 35 (Branch Cable MM2) - 14 Newton Meters
label | c5312184-fd01-509e-986f-7821e8631747 |  | note | TTD351XFA - 50 to 150 (Conductor Size MM2) - 35 to 95 (Branch Cable MM2) - 18 Newton Meters
label | e8681a04-a1c7-573d-8614-1b18c351636f |  | note | TTD401XFA - 50 to 185 (Conductor Size MM2) - 50 to 150 (Branch Cable MM2) - 18 Newton Meters
label | a6a78d7e-b060-57bb-a67e-bf6ec3b98405 |  | note | TTD431XFA - 70 to 240 (Conductor Size MM2) - 16 to 95 (Branch Cable MM2) - 20 Newton Meters
label | 3bdea69c-d419-5bd4-807f-1fb22901ff2f |  | note | TTD451XFA - 95 to 240 (Conductor Size MM2) - 95 to 240 (Branch Cable MM2) - 25 Newton Meters
label | 3fb3b077-21f9-5717-8291-a44640987b75 |  | note | TTD551FJA - 120 to 380 (Conductor Size MM2) - 95 to 240 (Branch Cable MM2) - 37 Newton Meters
label | 96c2e52e-a3f3-51b1-9fbc-5a0af96b19cf |  | note | INSTALLATION NOTES FOR IPC’S: WHEN USING TWO BOLT CONNECTORS EACH BOLT MUST BE TIGHTENED A1/4 T0 1/2 TURN ALTERNATIVELY UNTIL THE SHEAR HEAD OPERATES
checkpoint-group |  |  | section | Test No.1
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 7c9b2b60-8d97-507f-9c61-58807ba964bf |  | textbox | Bolt Size
text | 2763fe1b-aee6-55e7-9d91-cf1acd14d695 |  | textbox | Switch/cable Identification
text | 40a778b7-a02f-55bd-a17c-1aab7e4793ae |  | textbox | Line/Load
text | 0d5b40d7-e902-53a9-9db3-02b4026d45a4 |  | textbox | Red Phase Torqued
text | 0177ebf2-9a6c-5773-967f-77e4341e3cb4 |  | textbox | White Phase Torqued
text | 88f4361a-121d-52df-ad8a-ccc26b5cf7e9 |  | textbox | Blue Phase Torqued
text | 2250d643-ebf1-5944-be09-0bbf3fe7eb30 |  | textbox | Neutral Torqued
text | bd8597c6-9f34-551b-8e67-bcd5bd3d621c |  | textbox | Earth Torqued
text | b1751f53-b248-5b14-bdb8-522ef76acf35 |  | textbox | Bolts Crossed With Black Texta
text | 676f919b-9054-5cfc-8cce-06d906ef47eb |  | textbox | Name
label | f2d591b1-c2cd-51b4-9d8e-adea182d875b |  | note | Signature added below
checkpoint-group |  |  | section | Test No.2
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | b7d50637-b9fb-5c53-8e31-44ab68cac9a1 |  | textbox | Bolt Size
text | e206ab70-816b-5710-a9c1-8ee8439c3e4c |  | textbox | Switch/cable Identification
text | 2d4715ff-7317-500c-9eec-e5c3341db034 |  | textbox | Line/Load
text | 5be2d7d8-9e0b-5577-97e3-da716bae3c0f |  | textbox | Red Phase Torqued
text | caa08847-de65-5857-ac69-f1bcea0ec8a3 |  | textbox | White Phase Torqued
text | 8688aff7-9598-59da-8c85-db64c9d988b2 |  | textbox | Blue Phase Torqued
text | 8ce5a772-edcb-57ec-85d8-0b9c690c61d0 |  | textbox | Neutral Torqued
text | bb993f09-4628-5231-ba59-c4bb8ff91d5d |  | textbox | Earth Torqued
text | 2160cdd3-157d-584e-97a2-cfdae7e448a7 |  | textbox | Bolts Crossed With Black Texta
text | b0f9a041-88d4-53e0-8ac4-b300921201bc |  | textbox | Name
label | a19a8bd4-a7c0-5da4-ada3-1ffed1c9c90f |  | note | Signature added below
checkpoint-group |  |  | section | Test No.3
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 5ee7212d-7111-516d-9e7f-3962652cde74 |  | textbox | Bolt Size
text | 8caef2f9-fcfd-570a-a36a-8ad43ff0bbbc |  | textbox | Switch/cable Identification
text | a64f6264-46ac-5468-8cd0-9d4d0f496a04 |  | textbox | Line/Load
text | 2c185f8f-593f-5fa2-ac2b-602e8a4bd9e1 |  | textbox | Red Phase Torqued
text | 806cc4a4-bf4e-54ca-8e32-f5feb4e6562c |  | textbox | White Phase Torqued
text | 5d1d0e03-7158-5da2-840b-f359d592515a |  | textbox | Blue Phase Torqued
text | 0ab1285a-91fe-53b4-83fd-4b97f1d1cc14 |  | textbox | Neutral Torqued
text | 8f05d1df-3497-54a8-b10e-667165ec1212 |  | textbox | Earth Torqued
text | ac2efc0a-be45-58f7-b836-9205e15b869a |  | textbox | Bolts Crossed With Black Texta
text | c9fc6830-f288-5d20-a7d1-01cb8d6b2e10 |  | textbox | Name
label | 8d6708dd-db71-52f1-96e4-23bd79640c43 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.4
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 1fa91145-4131-5d5b-a215-842774107908 |  | textbox | Bolt Size
text | e88bc601-687a-5c49-af83-a1aee14d1ac5 |  | textbox | Switch/cable Identification
text | 27af9b72-93c8-5952-9bc1-5bd6ed4d8708 |  | textbox | Line/Load
text | fc3b1920-fd72-51b5-a478-03cf3f885efb |  | textbox | Red Phase Torqued
text | ae04ba26-e8da-503b-8f94-5e3ef0e6615e |  | textbox | White Phase Torqued
text | 8a245c2d-dbf7-59c7-b70c-35eada9cd308 |  | textbox | Blue Phase Torqued
text | 73302499-41fa-5dac-b5a6-ee74830e5a13 |  | textbox | Neutral Torqued
text | 7ffe21ab-1d31-5743-a268-1b039064dbbd |  | textbox | Earth Torqued
text | 276f6cc6-61b3-5231-bf9b-17efa97ff64d |  | textbox | Bolts Crossed With Black Texta
text | b657e3f0-00b7-53a2-8e4d-c073cb3acf25 |  | textbox | Name
label | 6f2daaae-f239-5b56-92cc-88d8833605ec |  | note | Signature added below
checkpoint-group |  |  | section | Test No.5
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | d4b8941b-5e81-55f1-949e-213bd2c2a6b9 |  | textbox | Bolt Size
text | c30c946a-7230-5e5c-b049-92c576c3eb59 |  | textbox | Switch/cable Identification
text | 2110315c-9930-52e7-8c51-fc34240a91ea |  | textbox | Line/Load
text | 477c8817-a731-577e-b318-68a42928b9d7 |  | textbox | Red Phase Torqued
text | 82b4b592-543c-5d55-b330-d7caa5590d5c |  | textbox | White Phase Torqued
text | 4af1d013-5a38-5a5a-b240-057ee87c37ae |  | textbox | Blue Phase Torqued
text | 4eb99f60-6fa0-53b5-9ae2-fb30f535d996 |  | textbox | Neutral Torqued
text | 1a94ed31-ffea-534d-a9e6-b24a56006e43 |  | textbox | Earth Torqued
text | ee37a708-39bb-5e2b-bf46-0379cf5fb54a |  | textbox | Bolts Crossed With Black Texta
text | 5ae1ad26-3122-5d5d-859e-e1ede872a717 |  | textbox | Name
label | edc50af3-a809-5656-a963-94dd9cd85cdf |  | note | Signature added below
checkpoint-group |  |  | section | Test No.6
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 878b4288-efe2-5419-a5b0-d2fa41f3c1b9 |  | textbox | Bolt Size
text | a5288929-2c4c-5e36-8acd-835a66fff810 |  | textbox | Switch/cable Identification
text | 4a622d36-d3b7-54a1-b247-99d9e2df5e18 |  | textbox | Line/Load
text | 7a8e34fe-960a-5c4f-9989-958d16be7b2f |  | textbox | Red Phase Torqued
text | ae7bc992-053c-510a-93b8-826dac56cb7e |  | textbox | White Phase Torqued
text | 6cd96864-f7df-5fc4-93e1-744c043fa919 |  | textbox | Blue Phase Torqued
text | fa180fe9-b743-577f-8047-767533594afc |  | textbox | Neutral Torqued
text | 656239ed-9c49-5d10-99b9-e966559301df |  | textbox | Earth Torqued
text | 1ecae155-4c35-504b-9841-2703f1fad9d8 |  | textbox | Bolts Crossed With Black Texta
text | 5caab9ff-3674-5ad6-837f-39477def9cdd |  | textbox | Name
label | d5ab1cf2-68af-590d-87a5-e7a6dc00fe88 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.7
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | d36f1f78-9923-5c03-935a-d7a68debdab8 |  | textbox | Bolt Size
text | 877b6fe0-91be-5a6a-b1ac-e3168876369f |  | textbox | Switch/cable Identification
text | fded91bc-1189-56ee-9667-54414b3a6dce |  | textbox | Line/Load
text | 7d096b31-8182-5020-803d-f203c1cdcece |  | textbox | Red Phase Torqued
text | 31f2f5ff-c552-58c6-8c2b-6f406d9d1908 |  | textbox | White Phase Torqued
text | e995dce0-b3ba-59bd-a3da-530ff7450a21 |  | textbox | Blue Phase Torqued
text | cd7e9b12-182e-5dd1-bd00-40c2e903ffd7 |  | textbox | Neutral Torqued
text | 04638b25-d3c4-52c9-a100-dd2c17847f21 |  | textbox | Earth Torqued
text | 9c72042a-855d-5b33-a854-239b185433a9 |  | textbox | Bolts Crossed With Black Texta
text | 0cdfba8a-4d1e-5904-9b20-7cb883148909 |  | textbox | Name
label | 92b35aa3-5ad2-5233-8634-b34df56c205f |  | note | Signature added below
checkpoint-group |  |  | section | Test No.8
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 38e84460-0576-5f10-8909-d1e1d96636c0 |  | textbox | Bolt Size
text | 5419ea0b-9532-5b7b-845f-888eb0ab376d |  | textbox | Switch/cable Identification
text | caa7f328-2ec7-5f93-ba1f-1afbc1842185 |  | textbox | Line/Load
text | f3d19f5e-2a46-5778-a0e2-586cfaf325c5 |  | textbox | Red Phase Torqued
text | 6cf40fef-fa32-56d9-b533-a5849ec8d31c |  | textbox | White Phase Torqued
text | 1178d659-db38-59e3-92ff-e0f0cec677f7 |  | textbox | Blue Phase Torqued
text | 2555fb1c-6c11-5fe4-99e4-cd7812ac9e83 |  | textbox | Neutral Torqued
text | 417be456-a4a1-5eae-ab56-d045ed70c8bd |  | textbox | Earth Torqued
text | bec66abc-ba9a-5c85-81d5-07959fcd93bd |  | textbox | Bolts Crossed With Black Texta
text | 335a46b6-c99b-5097-96a7-8d5bf64f6756 |  | textbox | Name
label | c74c3c13-5acd-519d-8bbe-1acf8cec1176 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.9
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | d35e2b35-adaa-5761-9011-bbcdaae06f7b |  | textbox | Bolt Size
text | 0a8426e6-d250-536d-8754-cbc6264596ab |  | textbox | Switch/cable Identification
text | dda3efda-df6a-5d72-b955-0c07c63caecd |  | textbox | Line/Load
text | 21d455a6-fda9-5f20-ae45-7aa3fff78e34 |  | textbox | Red Phase Torqued
text | a0463d16-3a1d-58b3-9cb6-dee526e34f49 |  | textbox | White Phase Torqued
text | 565166f8-b567-519e-95aa-60a59af304c7 |  | textbox | Blue Phase Torqued
text | 090c76ff-ccf1-5a9e-a7d7-985de8b7c667 |  | textbox | Neutral Torqued
text | 1afbbc97-eb63-5b91-a383-3c68d1f1eff1 |  | textbox | Earth Torqued
text | b5ada329-7040-5619-b8f7-92d9188ade3e |  | textbox | Bolts Crossed With Black Texta
text | 27f2f7f8-27a5-53c1-b6e4-7a9e206a0e92 |  | textbox | Name
label | baf69b92-dc8d-5a63-8752-8e3de8a6987e |  | note | Signature added below
checkpoint-group |  |  | section | Test No.10
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | fbe2a154-14ca-5fba-8917-4b9dbfaed3f6 |  | textbox | Bolt Size
text | ca03ea7e-7b77-5339-a7e8-028ab41d8adb |  | textbox | Switch/cable Identification
text | 12976415-ebb0-540b-a6fd-38fcce8c6415 |  | textbox | Line/Load
text | 5695be4c-16b8-572f-9d0b-d672c361b97c |  | textbox | Red Phase Torqued
text | dffec2c3-5aae-5ff0-be66-004364f867ed |  | textbox | White Phase Torqued
text | 9729e159-96dc-5445-bc57-69c9ea251b19 |  | textbox | Blue Phase Torqued
text | a814d231-817c-572c-ba1c-81143cf8d26f |  | textbox | Neutral Torqued
text | 7c6ab659-040d-50e3-bab4-823bb5142f5d |  | textbox | Earth Torqued
text | 0968c249-23f2-5dd0-9825-64dc4931a405 |  | textbox | Bolts Crossed With Black Texta
text | bb76e6dd-366f-50f6-b891-6f8afeaf2599 |  | textbox | Name
label | 0a6b86ba-058e-5a92-a3d8-f0d1e37249cc |  | note | Signature added below
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Cable Tray works completed to specification/drawings - Area left clean & tidy
label | 2a48d172-abf3-5d10-86f3-f8b97d613069 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 163b12d5-8849-5079-9717-1097909580a1 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 9487823e-436e-52d5-995b-d8c990994b3c |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 33a5fa23-ef50-5489-9704-ac8121111101 |  | textbox | Other (Specify here)
select | c3e6d578-98be-5f87-9400-6a6487abfe94 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 5a6320a7-169a-55c5-b4a1-3ac30eeec8af |  | textbox | Other (Specify here)
text | f2fbc1e7-02ee-5b90-8ab5-3545606916a3 |  | textbox | Witnessed by (Builder/QAM)
label | 9f5a7aa8-3d54-5969-b8c7-f150657a2c88 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AF-502 - Electrical Services commissioning Sheet - Details & 10x Circuit Checklist (Rev 0 +Names) |  |  |  |  | Yes | AF-502 - Electrical Services commissioning Sheet - Details & 10x Circuit Checklist (Rev 0 +Names) | 0bb8557a-363a-4a6d-b05e-40ddec07e0ac
checkpoint-group |  |  | section | Electrician Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | b8572960-e4f4-570e-a184-11799dd90d83 |  | textbox | Test Date
select | 602e91bb-b69c-5b0e-8561-f7cd7856b314 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | e8673641-bb2b-58ea-aaf7-3b4f3a9d3a56 |  | textbox | Other (Specify here)
boolean | 670d8fb6-1d79-5571-a899-c9cf96f16de7 |  | tickbox | Signature added below
checkpoint-group |  |  | section | Circuit Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 204fb060-c11a-50e9-8670-7f13548b64fa |  | textbox | Designation of service
text | f4a8dc3d-30b7-573e-b9ff-9871861227ef |  | textbox | Location of Service
text | a001c8d2-a982-539c-a03a-844f83fda3cb |  | textbox | Test Equipment Model
text | 1c9e8171-48c7-560e-893c-3d2abdeff399 |  | textbox | Test Equipment Serial No.
text | 2269c826-135e-5a6c-81c9-76f84534ff63 |  | textbox | Method of Fault Protection
text | 92ac57bb-e51b-5800-8b4b-f53ca463e523 |  | textbox | Prospective Fault Current
text | fb89fddf-5d81-5558-8e7b-c005843a9277 |  | textbox | ZE
label | 7c61ed71-8389-5647-b552-29b1d2a5e7d2 |  | note | .. ..
label | 49f16bfa-6990-5112-8ecb-b010ffdea085 |  | note | Specify Board Type below,Pass to applicable, N/A to irrelevant ones
checkpoint-status |  |  | checkpoint | Main Switchboard
label | 0037fbca-9471-5a6e-93fe-dbcf6c4cac83 |  | note | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance
checkpoint-status |  |  | checkpoint | House Dist. Board
label | 9f1d863e-3d27-5b89-bacf-bdf38e315d5a |  | note | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance, RCD Test (Where installed)
checkpoint-status |  |  | checkpoint | Apartment Dist. Board
label | bc80102c-40b2-5505-9fe8-ee66a1f33487 |  | note | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance RCD test
checkpoint-status |  |  | checkpoint | Mains Reticulation
label | c5cc075c-b6b4-5010-82d4-0d16b7c46561 |  | note | Visual inspection, Earth continuity, Insulation resistance, Polarity, Correct circuit connection, Fault loop impedance
checkpoint-status |  |  | checkpoint | Other (Specify below)
text | 6a7207e7-12df-56d1-8ce8-f8263a156643 |  | textbox | Other (Specify here)
label | 60ee6546-31af-5902-b60f-0d76d122a88a |  | note | To be determined by competent/qualified technician
checkpoint-group |  |  | section | CB 1
checkpoint-status |  |  | checkpoint | CB Details
text | 3dae2aa9-0754-5d17-aa29-32333533fe50 |  | textbox | CB #
text | b5dee0ab-8833-5647-9a88-7b4f2c56ff30 |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 2
checkpoint-status |  |  | checkpoint | CB Details
text | c4a33895-7bbc-5e19-ac05-8173a5af53ef |  | textbox | CB #
text | ba7e0db5-0a3c-5ce9-89c3-6dba95d35083 |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 3
checkpoint-status |  |  | checkpoint | CB Details
text | 21285b2b-a862-532b-904d-e1e27f3af6da |  | textbox | CB #
text | e16b3453-2da6-5b06-b31c-d8b8ec97e07b |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 4
checkpoint-status |  |  | checkpoint | CB Details
text | d846a5a0-c538-5ff5-8306-76a86c2b4217 |  | textbox | CB #
text | ed2390de-8eaa-5522-9c4e-7ff45fa6fbdb |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 5
checkpoint-status |  |  | checkpoint | CB Details
text | b8c6670e-ced8-517b-9ddc-8a03e6b51c77 |  | textbox | CB #
text | 430b606b-c55a-586e-ace5-1c2a18e48a8b |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 6
checkpoint-status |  |  | checkpoint | CB Details
text | 81add881-12e8-5392-906a-bc9efbe0c0b0 |  | textbox | CB #
text | a6d7d7ac-8392-5df6-938f-f2d3b7ec44a3 |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 7
checkpoint-status |  |  | checkpoint | CB Details
text | 1585c28c-2003-5e7d-b36b-0f6e90560551 |  | textbox | CB #
text | 13e9db7d-86d3-5c10-951c-4a3ab0616f4f |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 8
checkpoint-status |  |  | checkpoint | CB Details
text | 354f7128-4f2b-5ddc-804a-eebadeb6e67e |  | textbox | CB #
text | 126d3c33-9c40-54cf-88ee-28a685d7ddd9 |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 9
checkpoint-status |  |  | checkpoint | CB Details
text | ab3a4b14-ae0d-5c9e-b2f2-7d1fa3ffd45f |  | textbox | CB #
text | e4c86842-11f7-570b-afff-1f527280438e |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checkpoint-group |  |  | section | CB 10
checkpoint-status |  |  | checkpoint | CB Details
text | a17592b3-c011-529b-93e2-54d0d60541c3 |  | textbox | CB #
text | ee6deb89-46b0-5369-8a36-8d8315d94778 |  | textbox | Circuit description
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity (Pg. Resistance)
checkpoint-status |  |  | checkpoint | Insulation Resistance (Pg. Insulation)
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connection
checkpoint-status |  |  | checkpoint | Fault Loop impedance (Pg. Resistance)
checkpoint-status |  |  | checkpoint | RCD Test (Pg. Proactive)
checklist-sectioned |  |  | checklist | AE-ITCX-004 - Construction Emergency and Exit Lighting to AS 2293 Logbook (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-004 - Construction Emergency and Exit Lighting to AS 2293 Logbook (Rev 0 +Names) | 0f60a4c1-c36e-4d77-92ef-a4c8ace09ccd
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 9f7b0799-5149-5a50-b8f7-dc2198087996 |  | textbox | Building/Level
text | cd2821ef-977b-5882-a56b-8bbffaba6e5a |  | textbox | Switchboard No.
text | 077e8f6d-fa75-587b-8d1b-ca8aa5615b25 |  | textbox | Circuit No
text | 62bfcd5c-fc31-5105-8096-195cd81019b2 |  | textbox | Test Date
text | 881b12b4-cf11-5745-98aa-d88ac0bd523c |  | textbox | Start Time
text | 1af322b6-31fb-5638-898c-03b0d92778be |  | textbox | Finish Time
select | 80c3b5a7-d9a0-5477-a10b-5fc85b124478 |  | dropdown | Tested By | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | de504d54-f6cf-5e43-8b8e-7d31cf526640 |  | textbox | Other (Specify here)
boolean | 8a690860-82d9-5908-9fce-adf79391272f |  | tickbox | Signature added below
checkpoint-group |  |  | section | Fitting No.1
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 1f84307a-f99e-5ec8-83c3-8912320446d0 |  | textbox | Fitting No.
text | fed90127-488c-5de6-b123-404cc6fc65e3 |  | textbox | Fitting Type
label | f5710826-6b56-5979-b5cf-f61732239de6 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.2
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 01da2c39-45a2-59b3-9cf5-95a140219470 |  | textbox | Fitting No.
text | aee491e6-937f-5123-bc08-a532ec15fdfc |  | textbox | Fitting Type
label | 054eca56-e6a5-56e7-a2d3-06345c423443 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.3
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 11fd65fb-b9e8-5b76-9070-c2a43c866459 |  | textbox | Fitting No.
text | 0ec86aac-717b-556f-8583-4726c6e9c52c |  | textbox | Fitting Type
label | de9002f0-c425-5258-8691-b6e3c50853f8 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.4
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | d166484e-5477-5eb0-8489-60db0561078d |  | textbox | Fitting No.
text | faaedc6e-a5da-5997-99c2-727a32c9eee5 |  | textbox | Fitting Type
label | 45630d8a-ae9e-5d6b-bbb4-b64492e4e258 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.5
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 3080cfa5-590c-5559-bf78-d67e4af671e8 |  | textbox | Fitting No.
text | 466ad44a-6e72-5335-aa3b-5641d76ba67c |  | textbox | Fitting Type
label | 2bbcbdf5-46c8-59d4-a77e-e98ca5fe44af |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.6
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 7a99dda4-e2be-50f1-863a-acd037f1c0c0 |  | textbox | Fitting No.
text | 6c0b35d2-f1ce-53da-b90d-bf7163846045 |  | textbox | Fitting Type
label | 694bca91-8ea9-5be5-ac98-0ba4b04d2dd2 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.7
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | e8438eff-0361-5f2c-94a2-2620cadfe92e |  | textbox | Fitting No.
text | 08f11cce-4869-5f53-908b-9ea824aa086d |  | textbox | Fitting Type
label | 31590c1c-d3a2-5959-bc60-e5e4809388fb |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.8
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | dd265942-87ff-5c0c-a2e7-0bd7bb8c949a |  | textbox | Fitting No.
text | 058e29eb-03d6-56d9-9603-c89bda9985cb |  | textbox | Fitting Type
label | 3202a021-8c13-521d-a252-b7b975063541 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.9
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 95c31de1-285c-5528-93b7-fabac2a4e8b1 |  | textbox | Fitting No.
text | 571193ba-9ade-5579-9894-265a22fadb8b |  | textbox | Fitting Type
label | 21199aea-500c-54f5-8f20-1fbef244e814 |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checkpoint-group |  |  | section | Fitting No.10
checkpoint-status |  |  | checkpoint | Fitting Details - Pass once entered
text | 8ce3c415-9757-50e9-9df6-3c733d1db8f7 |  | textbox | Fitting No.
text | 9fd56956-96de-50f5-a0ac-4091fe25c74e |  | textbox | Fitting Type
label | 71bc07d6-c706-5249-af0c-973b2afd48ca |  | note | Report/Repairs undertaken photograph/comment below
checkpoint-status |  |  | checkpoint | Fitting Condition
checkpoint-status |  |  | checkpoint | Lamp Operation
checkpoint-status |  |  | checkpoint | Operating Time
checklist-flat |  |  | checklist | AE-ITCX-033 - Busduct Installation (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-033 - Busduct Installation (Rev 0 +Names) | 15b3ab89-aa13-4c1b-8e06-f4fe4efff384
checkpoint-status |  |  | checkpoint | Busduct Details - Pass once entered/confirmed
text | a07f68aa-a20f-549e-8d14-924e2f3f3500 |  | textbox | Drawing & Revision # (or Attach photo below)
text | 92e3683b-5602-5cd7-8fbf-8621b4c8fe01 |  | textbox | Run details
text | 6490ce8a-cb31-5aa0-93a6-544647689299 |  | textbox | Package #
text | 072fe337-3907-59b9-92c9-c1cbb7f56576 |  | textbox | Approx weight (kg) - Excluding Packaging
checkpoint-status |  |  | checkpoint | Piece 1 - Item onsite - Pass=Yes / Fail=No
text | 72840ed7-8492-55ef-817c-c30b272063a2 |  | textbox | Vass Shop Drawing Piece Number:
text | 4796ef01-d6ca-534b-b5d8-de102f230f99 |  | textbox | Piece weight
select | fd252839-8908-53b4-847f-ba42663c5351 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | 71fcc66c-3689-5a00-9e08-d8f03fe6a921 |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 2 - Item onsite - Pass=Yes / Fail=No
text | 0d362c89-5a72-5b65-b81c-2feb7760d6ef |  | textbox | Vass Shop Drawing Piece Number:
text | 1d59344f-9838-501c-b26d-9b0fbdc143ec |  | textbox | Piece weight
select | 5ec3f129-fb6e-52d3-9e8b-daf664dddf49 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | c4b19fb8-a778-5dbe-b431-e4a3eb28040c |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 3 - Item onsite - Pass=Yes / Fail=No
text | 6741f8bc-3577-5ec5-ac26-c77cbca1abd9 |  | textbox | Vass Shop Drawing Piece Number:
text | 4d111b63-ac95-514b-8932-923f93e4d685 |  | textbox | Piece weight
select | e0f68ae9-32be-5e95-b7ee-3a2cb6fcb7a8 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | d7751e8a-c8f4-50ff-92cb-98e4929f753a |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 4 - Item onsite - Pass=Yes / Fail=No
text | 741c0743-71af-5c9c-b628-504afb470ed5 |  | textbox | Vass Shop Drawing Piece Number:
text | b0b002d4-a3b0-5bf3-ac64-c80e4b3f9456 |  | textbox | Piece weight
select | 84346fb7-1a48-57b4-9777-d271a57529a5 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | 963a5dc4-0a97-5a0c-94ce-81dc4a2550ba |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 5 - Item onsite - Pass=Yes / Fail=No
text | a07bc229-c1ee-56b9-8662-05d4117a4c45 |  | textbox | Vass Shop Drawing Piece Number:
text | 4694f297-1f62-5acc-8d1a-741a2dea7aa0 |  | textbox | Piece weight
select | d306c4ba-8595-5fdc-a9f9-36291f0ae086 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | 79024601-c9aa-5ac1-99c8-ac5661d4cc5b |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 6 - Item onsite - Pass=Yes / Fail=No
text | 54c5c588-5e29-5011-9d35-ff8fc9ef8c85 |  | textbox | Vass Shop Drawing Piece Number:
text | f076733c-32b9-56d1-ac3c-cca091301746 |  | textbox | Piece weight
select | 10d5771d-1675-5846-a2e6-a8b4efc7b1e0 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | a4c090a9-07f2-5c36-a3dc-61389d504e74 |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 7 - Item onsite - Pass=Yes / Fail=No
text | bfb5a69d-1dbe-56e3-8548-858fd5a2dcb5 |  | textbox | Vass Shop Drawing Piece Number:
text | 95771c6c-6e8b-5ecb-bd52-c40419991905 |  | textbox | Piece weight
select | 538a7265-848a-54dc-b0b6-804c4cdc248f |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | 9237994e-41d3-5a65-a92b-8182a55a6672 |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 8 - Item onsite - Pass=Yes / Fail=No
text | 9d216b3d-13af-56d1-81ba-b3c359f02c70 |  | textbox | Vass Shop Drawing Piece Number:
text | d0c98f4f-c85c-52b2-9bad-c8efa814778a |  | textbox | Piece weight
select | 91461529-fa8d-56c7-ae6d-4ad1df7c1178 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | ad4249eb-d8e5-57b4-89f0-5d707a0cc4eb |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 9 - Item onsite - Pass=Yes / Fail=No
text | 62e5ce60-1bc1-5e50-ac8c-8db3e1dfa47b |  | textbox | Vass Shop Drawing Piece Number:
text | 6160212b-5087-5459-9638-7dfc254f4693 |  | textbox | Piece weight
select | 2849eb3a-6dfa-5e78-ba42-274283c89a9d |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | f81c78a5-d6b9-531a-90a6-6c62d6248850 |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Piece 10 - Item onsite - Pass=Yes / Fail=No
text | 244275c6-3997-5884-9bce-2f99f13c4811 |  | textbox | Vass Shop Drawing Piece Number:
text | 034056a3-21fb-5c59-972d-5ae215cae8a8 |  | textbox | Piece weight
select | 6ba0145d-f6c2-50af-8c16-e324b186ae34 |  | dropdown | Any Damage - If Yes, attach photographs/comments below | Yes, No
text | 52eff061-ba25-5e93-804d-94d6f6295774 |  | textbox | Final location
checkpoint-status |  |  | checkpoint | Sign-Off - Busduct Installation completed to specification/drawings - Area left clean & tidy
label | 31267101-fe59-5f03-9232-8d4ed20d8861 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 1febcb60-5eb2-5c44-baf3-5263931d74fc |  | note | Any Corrective Actions to be Photographed & Commented below
select | f98b2b83-52d8-53d4-8e1c-c1b58af18584 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | d5af3727-01db-588b-a5af-b34c1108883d |  | textbox | Other (Specify here)
label | dc437cf0-0a2f-5f2c-b0c0-3aec052de449 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-014 - Meter Panel Visual Inspection Checklist (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-014 - Meter Panel Visual Inspection Checklist (Rev 0 +Names) | 20ef4edf-ccc8-43d9-be39-5f3be5e54ddc
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 78cfa149-1b33-5534-96f6-f7ca5299075f |  | textbox | Meter Panel Info
text | a4fc86fd-823c-53a3-b3d0-ade85355e567 |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | Wiring Neatly Loomed
checkpoint-status |  |  | checkpoint | All connection points tight Inc. fuses and panel isolators
checkpoint-status |  |  | checkpoint | All factory fitted connections tight
checkpoint-status |  |  | checkpoint | Panel, cover plate, door, lock and pole filters
checkpoint-status |  |  | checkpoint | Supplier checklist (e.g. Aline) Completed and Attached
checkpoint-status |  |  | checkpoint | Meter panel installed as per Appselec shop drawing
checkpoint-status |  |  | checkpoint | Meter panel and cupboard cleaned
checkpoint-status |  |  | checkpoint | Apartment sub-main relabelled at entry point.
checkpoint-status |  |  | checkpoint | Meter panel face wiped and cleaned
checkpoint-status |  |  | checkpoint | Glands tight
checkpoint-status |  |  | checkpoint | Cables fire sealed where required
checkpoint-status |  |  | checkpoint | Wago Plugs installed, labelling is correct & polarity is correct
checkpoint-status |  |  | checkpoint | Meter Panel Visual inspection completed to specification/drawings - Area left clean & tidy
label | 68246413-1aac-56c5-b0ce-f400db117aa3 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | a60af06a-e995-5a6c-be3f-ebaadb8ad712 |  | note | Any Corrective Actions to be Photographed & Commented below
select | cb04f977-6906-5bfe-995d-089a4f84a6aa |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | a86f5e1b-a5a2-5ed0-a6a7-a183f648c59e |  | textbox | Other (Specify here)
select | 884dd1e6-7935-5364-bf36-0639dc86787c |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 19f343b9-9084-56b2-8286-7e6d282c3ba0 |  | textbox | Other (Specify here)
label | a5c51279-dc57-5797-88f4-584beaab0c4c |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AE-ITCX-022 - Emergency & Exit Lighting to AS 2293 Logbook (Rev 0) - TBC W/CONQA |  |  |  |  | Yes | AE-ITCX-022 - Emergency & Exit Lighting to AS 2293 Logbook (Rev 0) - TBC W/CONQA | 29b3d2a3-9fb4-47d6-a6c5-cfab5b324248
checkpoint-group |  |  | section | Preface
checkpoint-status |  |  | checkpoint | Summary of Information - Pass once confirmed
label | e9e0693f-e792-56ad-bdfa-27c4f41b6d14 |  | note | This logbook has been compiled in accordance with the requirements of Australian Standard AS 2293. Persons using/completing this logbook should be familiar with all parts of AS 2293
label | e6aa47cc-6bc0-5600-9fbc-630d49c210b5 |  | note | .. ..
label | 7427b723-587b-54b6-8d6e-76231a81d93f |  | note | Summary of Test Procedures as required under AS 2293 Part 2 Section 3. Six (6) monthly inspection and test procedures for Single Point Systems
label | 5c273bbc-c6c8-56d8-ad93-ef10087f353e |  | note | 1. Test procedures should be carried out at intervals not less than 6 months
label | 323b6ad1-c979-5d1d-ad13-44e0611f2937 |  | note | 2. Check to ensure that no interruption has taken place to the power supply of fittings to be tested for at least 16 hours prior to carrying out testing
label | 5a79d6de-74fd-568e-b7f1-f9d6b34aafcf |  | note | 3. Carry out visual inspection of all fittings prior to conducting testing to ensure that power is connected, tubes are functioning correctly and fittings are free of damage that may otherwise affect the test results
label | 0f2d187f-a34b-5ac8-97ef-a66f8aed0145 |  | note | 4. Operate the emergency and exit luminaires from their battery supply by simulating failure of the monitored supply. All emergency and exit luminaires shall remain illuminated for a period of not less than 90 minutes or 2 hours for initial test of new fittings
label | 0b944851-e52c-5808-a0b7-242afed95920 |  | note | 5. Restore all emergency and exit luminaires to normal monitored supply and check battery charge operation is functioning
label | abb5513a-9d65-504f-981e-469cdc228e5d |  | note | 6. Enter test results into logbook
label | 1e0b4b30-bc41-566c-a366-be6a14915e84 |  | note | .. ..
label | a96d4922-de13-5888-8140-d3966261f080 |  | note | Summary of Test Procedures as required under AS 2293 Part 2 Section 3. Annual inspection and maintenance procedures for Single Point Systems
label | 75e3205e-6911-5999-b3c7-76884f3c16d3 |  | note | 1. Carry out all functions listed above as per six (6) monthly
label | ee645e93-99a1-5904-a986-aeb99a5b9d88 |  | note | 2. Clean all light emitting and reflective surfaces of emergency and exit luminaires as required
label | 79bf62b9-2e05-5829-9660-c793970a5601 |  | note | For further information regarding the testing of emergency and exit lighting, please refer to AS 2293-2
checkpoint-group |  |  | section | Emergency Light Fitting Legend
checkpoint-status |  |  | checkpoint | No.1 - Details Completed and Entered below
text | c6ab7571-277e-53f1-a2b0-455ecae4eb64 |  | textbox | Legend
text | 04b3fb91-d9b1-5d81-b255-3db928313ee0 |  | textbox | Manufacturer
text | 3c4c519d-c095-5646-a040-75f17567d8d6 |  | textbox | Cat Number
text | 6bfdae0d-ee06-5716-8eed-b7c0be31d6ad |  | textbox | Description
text | bb371fac-ed41-5bfa-8e48-d27cb7fbea1c |  | textbox | Lamp
text | ed030106-489b-5022-ab6c-effd7d99c851 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.2 - Details Completed and Entered below
text | 1c8b0d63-6c77-5fad-bba9-b7fabd85f827 |  | textbox | Legend
text | d87a22ef-a659-5ba2-80ad-8c038e54b058 |  | textbox | Manufacturer
text | 158f2d90-00f6-510e-9493-805c47b77ff0 |  | textbox | Cat Number
text | cba5e6f8-eb24-5ba0-8f45-140333507655 |  | textbox | Description
text | 6f604489-1c95-5182-a7e6-95d052a5f93b |  | textbox | Lamp
text | 06de5c0f-0d56-5739-9f79-b2018e842eee |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.3 - Details Completed and Entered below
text | f9854d75-f983-5b02-abc1-6ff775057a76 |  | textbox | Legend
text | c4bfd65f-76b2-5e6f-9f1a-0f27b5d8988b |  | textbox | Manufacturer
text | d7e6f45b-e49e-50d0-96cd-601ab0331cf8 |  | textbox | Cat Number
text | 44faa5bf-7807-5801-b9f5-980ddbcf4ae9 |  | textbox | Description
text | dcbbaae4-57c9-569a-aa0b-0b2667a311f7 |  | textbox | Lamp
text | 5b607c12-0491-5e35-a718-72151a53c977 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.4 - Details Completed and Entered below
text | 197f98cb-7ff5-5b0f-bb6a-6a40d202ccc9 |  | textbox | Legend
text | 5ea41766-2752-5eeb-a2ee-7f69e3f61d39 |  | textbox | Manufacturer
text | 3a278041-d77e-5ea8-a2a2-c2e05e8cfb31 |  | textbox | Cat Number
text | 36488b0a-c12c-5c8b-9c13-61238ec196e8 |  | textbox | Description
text | 59d3c296-cddc-5a6b-b585-7bdfc73dc924 |  | textbox | Lamp
text | 345a241a-c62b-5bfd-8969-2a3451124e70 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.5 - Details Completed and Entered below
text | c358358e-d855-59b9-b501-93f6face1024 |  | textbox | Legend
text | deb2cdbd-f310-5e1a-be7d-56f61f810d12 |  | textbox | Manufacturer
text | 721a3b9a-c5f6-53d0-9409-2f0fcca1b955 |  | textbox | Cat Number
text | fc76e424-1280-56e4-8b02-9f1ea4ff3acc |  | textbox | Description
text | 7473464b-5da7-50c9-9c89-18edd20b6f0a |  | textbox | Lamp
text | 02c67fd2-8be3-5b35-8f59-1ce193b11e28 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.6 - Details Completed and Entered below
text | 67b3119f-92b6-5664-8a8d-11aeed7c3d14 |  | textbox | Legend
text | 69f9ed43-0998-52b0-90cb-be2307928080 |  | textbox | Manufacturer
text | 8e60b8b3-9558-5b8b-9c0b-87acaac9f3c6 |  | textbox | Cat Number
text | 8b0d39ca-3a1a-5200-a438-22b29011b1d1 |  | textbox | Description
text | e23f6303-e32f-5c67-8549-d2a4cf165e92 |  | textbox | Lamp
text | e8ae0acf-f7d0-5985-94c1-d9088f36c749 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.7 - Details Completed and Entered below
text | 6f945ec8-21c5-5a46-af7e-df8c664bf278 |  | textbox | Legend
text | ed05ea4d-1283-5bcb-8a32-00f410783b19 |  | textbox | Manufacturer
text | 9f93824a-3e9c-5207-a722-7a8053115342 |  | textbox | Cat Number
text | e1f18db8-822f-59ae-9555-8e3c9d4f7eec |  | textbox | Description
text | a31b3c8f-b79b-5cdd-9d23-415e5ee084d6 |  | textbox | Lamp
text | d582e16d-039c-58ff-a3c2-f9ab36442415 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.8 - Details Completed and Entered below
text | 47dda54a-b7a9-5753-ad60-0614632eaae1 |  | textbox | Legend
text | 30cf4f51-8d6d-524e-8722-f11c976d107f |  | textbox | Manufacturer
text | d3b2f7d3-94a8-58cb-9705-148f621dca4a |  | textbox | Cat Number
text | 82e62279-6add-5d03-884b-6ebbea0becfe |  | textbox | Description
text | e7525619-e8f9-5112-b0f2-65575f076ad9 |  | textbox | Lamp
text | 5182c363-50e2-595b-9741-0b90d55bfafd |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.9 - Details Completed and Entered below
text | 2ff6f2b7-2094-5b9e-8c43-012c56650fe7 |  | textbox | Legend
text | 041470fb-0de9-5817-b551-23d373c0b6f1 |  | textbox | Manufacturer
text | 837aff09-004c-5f60-8d37-4cd476ce8ca8 |  | textbox | Cat Number
text | bd5f71d6-03a6-5767-a93a-925c9239684c |  | textbox | Description
text | 43ee4bba-98e4-5553-b3da-5671c6b1e7ad |  | textbox | Lamp
text | 0bf195f9-8855-53b5-8f5b-12f2b12ee869 |  | textbox | Battery
checkpoint-status |  |  | checkpoint | No.10 - Details Completed and Entered below
text | 0fd0804c-dc89-54fe-8973-de307c3e45c0 |  | textbox | Legend
text | ad89c9b7-c1c0-5be6-8672-13dc26ddb959 |  | textbox | Manufacturer
text | 769c3a9f-2051-5375-b5ce-20a0af42adbc |  | textbox | Cat Number
text | b0e01bc2-a28b-58bd-b0bb-19ccb8eb85d8 |  | textbox | Description
text | a333e561-e0b3-5f0e-ae56-022e44880bf9 |  | textbox | Lamp
text | d1c6d049-15d8-59b9-a856-3625bce0afcd |  | textbox | Battery
checkpoint-group |  |  | section | Fittings
checkpoint-status |  |  | checkpoint | Fittings Details - Pass once entered
text | 42a45ecb-e1f5-50c1-9572-606e4c5be907 |  | textbox | Fitting Number
text | e971772e-4188-5442-b8fe-f8ff3a6325c3 |  | textbox | Fitting Type
text | 0e5347f2-0b01-57b9-ae80-475816a8430a |  | textbox | Controlled from Switchboard
text | 3e8d2c3f-df8b-5b7b-b802-1631257ba247 |  | textbox | C/B Number
checkpoint-status |  |  | checkpoint | Fitting No.1 - Pass once completed
button | ce6d9529-a026-5e5f-8ce0-3a5faea748ae |  | button | Fitting Condition | Pass, Fail
button | 8593a72c-6ff4-5544-9376-a249760f40c2 |  | button | Lamp Operation | Pass, Fail
boolean | 0a6bb8b0-7142-56ed-b8de-497fbd04351a |  | tickbox | Clean Fitting
label | f280ae95-ae48-521d-bf87-82160fb37607 |  | note | .. ..
label | f98c2c01-5dbf-5131-9fbe-83915783d4c8 |  | note | Operating Time
text | 660ffab8-cc78-5709-8e33-9d6aed2cee1c |  | textbox | Time
text | 2cee80d2-c8e3-5fa5-bef2-99816c52497a |  | textbox | P/F
label | a2fa367a-b45a-5b6d-aba3-95a7c5d710ef |  | note | Any repairs photographed/commented on below
label | 68ccf786-da96-587f-a073-eb87e3ac7bf1 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.2 - Pass once completed
button | bfcf3dae-f86a-58cc-b6b1-daf9cfbcfb1c |  | button | Fitting Condition | Pass, Fail
button | fb4e93cb-0de5-51af-89c9-069e67da18d9 |  | button | Lamp Operation | Pass, Fail
boolean | 240fec19-158a-54c9-ad8a-8a38a03bfe1e |  | tickbox | Clean Fitting
label | 81fe23c5-1678-5d25-9f1e-ede11d424253 |  | note | .. ..
label | 727ef6ed-2743-5370-94eb-6f820f9692b1 |  | note | Operating Time
text | 3e7225b5-28ee-5b6a-a621-31d47aea2e0c |  | textbox | Time
text | 9069ae25-7f88-5d29-9926-000761effecf |  | textbox | P/F
label | 3bb2ab1a-1c1d-5fb2-8e7b-982acb1f5bdd |  | note | Any repairs photographed/commented on below
label | 357549e2-c227-5577-b20c-2cd5f9dea424 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.3 - Pass once completed
button | 48885cc3-81d2-5797-9e28-cf1f3a47131e |  | button | Fitting Condition | Pass, Fail
button | 50808926-8917-55d8-834d-7feb611361c8 |  | button | Lamp Operation | Pass, Fail
boolean | 015d2510-91a7-5934-81c2-07438e9d2c55 |  | tickbox | Clean Fitting
label | 3515ae2c-5c98-56f2-a22c-f4bd393e6809 |  | note | .. ..
label | 8569eb61-8d37-591f-b238-1dca1b62a278 |  | note | Operating Time
text | 4b02b6ac-6570-5106-9887-70951c927b4e |  | textbox | Time
text | 8bbf694f-a39a-53a0-ad7f-63f189dc930f |  | textbox | P/F
label | e97c03b6-596f-5687-a1d8-7e9cb7b8f1fc |  | note | Any repairs photographed/commented on below
label | 0dfbe822-d7b0-554b-994f-b0881aebcc8e |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.4 - Pass once completed
button | 2ec92cf1-4128-53d5-95c2-261796173794 |  | button | Fitting Condition | Pass, Fail
button | eb20f0b0-9bbc-53ab-b8ff-ee506b2d6ae2 |  | button | Lamp Operation | Pass, Fail
boolean | f5f7c966-13cb-5a2f-a31a-2cd82d2d47bd |  | tickbox | Clean Fitting
label | 57378a15-37f8-5e63-b5f9-cb15805514dc |  | note | .. ..
label | eeb4b429-9138-5e4a-9160-62acb9684a23 |  | note | Operating Time
text | 929bfd36-f0c1-51b6-a7e4-922af228e222 |  | textbox | Time
text | f04d5811-8d6c-541d-8aee-ad3851d38ef0 |  | textbox | P/F
label | 888fe19d-ba7c-56b9-b840-fe0d36941c5c |  | note | Any repairs photographed/commented on below
label | a3cf081b-417b-565c-b774-86044a4fbc5c |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.5 - Pass once completed
button | 4ce5e95c-931c-5745-8e49-9bd9d8c187ea |  | button | Fitting Condition | Pass, Fail
button | 0f300db5-23d8-50f5-8948-0f6f72fd26ff |  | button | Lamp Operation | Pass, Fail
boolean | d9897824-2fc0-5fd9-8200-a31b4daf1d84 |  | tickbox | Clean Fitting
label | f0ce9e87-72a5-5bc7-b382-7a9f3cceb2d1 |  | note | .. ..
label | de4e80bf-0244-5a73-89e0-1dd67853b5d7 |  | note | Operating Time
text | a7402297-a3a0-50a2-89ed-2372872f4f42 |  | textbox | Time
text | cea0fe7a-6ce1-588b-80a3-9976fa18ad4d |  | textbox | P/F
label | ff6879b6-3ff6-5ad8-b18f-efd6e5025250 |  | note | Any repairs photographed/commented on below
label | 14d3249e-c952-5ae3-8b33-7bd2649f9221 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.6 - Pass once completed
button | a143926d-d722-55fb-b02b-fb43c54546af |  | button | Fitting Condition | Pass, Fail
button | 91168cb8-81ae-5098-9482-82d411f52768 |  | button | Lamp Operation | Pass, Fail
boolean | 788a6a93-57a4-584d-8cfb-57cd728b5a1e |  | tickbox | Clean Fitting
label | 88c81a12-2de0-5eb1-baee-839a97c47e10 |  | note | .. ..
label | 215d09d2-630f-500c-93b4-be2cf594feef |  | note | Operating Time
text | 7a10f288-5a6d-51da-bc8d-5eb36f9a1f08 |  | textbox | Time
text | 9ffb9471-8c8c-5008-81be-814525b29544 |  | textbox | P/F
label | 2100b2d7-c7fa-52dc-ae4c-e45af212666d |  | note | Any repairs photographed/commented on below
label | 39316de9-91a9-5566-a58f-b6a36365b614 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.7 - Pass once completed
button | cac53a02-887a-5212-887c-84e0be35c262 |  | button | Fitting Condition | Pass, Fail
button | 706dadd4-5d19-595d-ac6c-0cf0b085e524 |  | button | Lamp Operation | Pass, Fail
boolean | 0badaae0-18af-5b6d-811d-e78c92730caa |  | tickbox | Clean Fitting
label | f8f9e8ea-e5d3-5005-8543-3836c5dc3ace |  | note | .. ..
label | 8d734094-9f77-59fa-9ea4-5b38c39a00bb |  | note | Operating Time
text | 663f713d-d1a9-5491-b54f-dd156400dedc |  | textbox | Time
text | 2f96d9eb-e4ed-5158-b9c1-eb58c9f982f9 |  | textbox | P/F
label | 9d01c0e2-a168-5f54-bca5-591b7ff28f2b |  | note | Any repairs photographed/commented on below
label | b4b05f21-04d5-5ea9-a165-428bd3100741 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.8 - Pass once completed
button | 5e8f9e8e-2321-5dbc-aad2-05e434357fa9 |  | button | Fitting Condition | Pass, Fail
button | 168f7613-fba0-57ed-8789-b83b829ba1f2 |  | button | Lamp Operation | Pass, Fail
boolean | 572ba6d7-9271-5353-9c27-2817bbdc7fba |  | tickbox | Clean Fitting
label | 41ec74e2-9e92-5e44-a74d-3c0ae8bd4db4 |  | note | .. ..
label | 17f8ca39-326b-5d4f-9466-8ca2bd4e23c0 |  | note | Operating Time
text | f4e3be72-e46b-5d8f-8451-50b9388b7da3 |  | textbox | Time
text | 88adce1a-de40-54da-a46e-0bfacb175d7f |  | textbox | P/F
label | 4cd92d11-edf8-50eb-9f4c-a510fa758284 |  | note | Any repairs photographed/commented on below
label | 2c94590e-8f5e-5b58-88ee-1ed019106b96 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.9 - Pass once completed
button | 85b7f721-ae39-5706-b889-d22751c1faed |  | button | Fitting Condition | Pass, Fail
button | deaa252a-8d03-5133-9738-9d1d50ab55d3 |  | button | Lamp Operation | Pass, Fail
boolean | 956e77d7-fcb0-5e93-86e3-515465423cc4 |  | tickbox | Clean Fitting
label | f248a27b-ee25-5476-a533-87e61c0e1119 |  | note | .. ..
label | ace80671-620e-5943-adde-b8631aa4e0a7 |  | note | Operating Time
text | e9b02841-f613-5f78-933b-61910d8243c5 |  | textbox | Time
text | 041071ec-ab82-5d92-89f8-534f1b2869cc |  | textbox | P/F
label | ed77c596-8d1c-5fb7-8d97-c9eac13d1993 |  | note | Any repairs photographed/commented on below
label | f3fd902d-88d0-5910-ab31-32c8857a1e59 |  | note | Attach Signature Sign-off below once completed
checkpoint-status |  |  | checkpoint | Fitting No.10 - Pass once completed
button | fab7f0fb-2a22-5636-a114-e1a9bfe4f9fc |  | button | Fitting Condition | Pass, Fail
button | 0329baee-3d67-559d-88a4-a9e167d26bcb |  | button | Lamp Operation | Pass, Fail
boolean | 20f11176-0842-5ab6-9f12-e17a6047b470 |  | tickbox | Clean Fitting
label | 060a0b6c-6c35-54dd-b7f8-b28554021fa4 |  | note | .. ..
label | 12d4f7db-3775-5a49-9caa-419f3dcebe9f |  | note | Operating Time
text | a78acaec-7734-5a42-8727-1cea937fe464 |  | textbox | Time
text | 8ad8d2b2-918c-5bfa-bcd8-9a4444eaaed5 |  | textbox | P/F
label | 8fd7e344-3e98-503c-8540-13abc6b74c1c |  | note | Any repairs photographed/commented on below
label | 53ac9026-83b6-5e29-8a72-f5c855046b0c |  | note | Attach Signature Sign-off below once completed
checklist-sectioned |  |  | checklist | AE-ITCX-002 - Monthly RCD Test Sheet (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-002 - Monthly RCD Test Sheet (Rev 0 +Names) | 3d4c9b54-2d0f-4e33-9883-05a2614f3a6b
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | e35b050c-d10d-5859-ac08-57afaf22799e |  | textbox | Test Date
text | ad3a455b-abfd-56df-aa94-557a53272333 |  | textbox | Switchboard No.
text | a7497d18-209c-565f-8108-0783b63791fc |  | textbox | Tag No.
select | c6e74167-bb66-5a47-907e-673e4dc9d40f |  | dropdown | Tested by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 8694f20b-131f-5142-8f4f-81207545740b |  | textbox | Other (Specify here)
boolean | d432ee6b-2150-5a08-8cf2-567502222771 |  | tickbox | Signature attached below
checkpoint-group |  |  | section | RCD Test 1
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 92ac4f78-e85a-5bb4-8596-e80d832f81ac |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | f63a553f-2550-59da-916b-a53b67ba4a4c |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 92aed026-362f-54f9-869c-181bfacca9d7 |  | textbox | RCD No
text | 37e885c6-200b-5d0c-82c1-02b97c573f56 |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | a78b67b8-9eb4-5285-ac5e-559eb7f17ed5 |  | textbox | 0.Deg (ms)
text | 58f9fd1b-309a-54ce-85d7-3e6ca7dca69f |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | a9d8b1df-97f6-5a3b-9a6e-8b0d528569a3 |  | textbox | 0.Deg (ms)
text | 86cfcaa5-39ca-5a14-a601-19b8d41b9bf7 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | e78505d2-5029-5002-a39a-0c25b7c8d876 |  | textbox | 0.Deg (ms)
text | bafa7e4f-99ee-5ca8-bbe5-a2ee0f3009d0 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | ab800fb6-09d1-570f-a577-a7e22b866d7e |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 2
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 2500d925-a9e2-5917-a965-b429181d98a8 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 2b996b10-4233-516b-85b9-c7e0cc9e8b57 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 54936c09-7168-576b-b980-29bf4c27a356 |  | textbox | RCD No
text | 7dc6d4e2-8904-5e44-a0ac-72438b7c2d4c |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | e3c3b2db-fd63-5fe1-ac78-37a69932ba9d |  | textbox | 0.Deg (ms)
text | 176e7426-b99a-5cf3-be49-730fe4ec5909 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | c80650c3-039b-5cbe-b3cd-a203e45fb754 |  | textbox | 0.Deg (ms)
text | 778445a8-9029-5c5b-b85b-a065b5e78fb9 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | c8c4cb18-b5d0-50ec-95db-3a4187807e6b |  | textbox | 0.Deg (ms)
text | 82265ca7-c92f-527a-9927-fc256151c2b0 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | bbc2f11f-3130-5445-8562-f592049afbfb |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 3
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 262ca702-96bd-549e-9535-5b58290af8d5 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 1e951f9d-f85d-5e99-bffa-d87ee1e13be9 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 04a00187-fda0-53a1-b974-56369f6f4b1f |  | textbox | RCD No
text | 43b0638d-390a-56f6-8fa5-34b7e691961e |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | f097a684-f1ee-5c1f-8ffb-d397391933f0 |  | textbox | 0.Deg (ms)
text | ca2c998a-fcb7-56b0-927c-198145e0276a |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 49577dab-1d55-5745-ab1f-c65b38114107 |  | textbox | 0.Deg (ms)
text | dc0c9efc-6931-5114-8402-f69f73ce75e9 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | ade596d0-e828-51f5-b1f3-f319cfc54048 |  | textbox | 0.Deg (ms)
text | e251900d-9fbc-524b-acf8-58270fc43ca7 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | cf7679bb-ce53-544f-ac32-cf07d6675cf0 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 4
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 48b2805b-87df-51b1-995e-ced4ae6fd231 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | ad770f0f-bb4b-5051-a402-a4a984974aec |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | c5243d6a-7f8a-54d3-8e7c-c677a40664c1 |  | textbox | RCD No
text | b10f9ce4-a2dd-5761-9de7-5a81ebae32ac |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 4efea602-2748-5f8e-a5f8-a33201fd65be |  | textbox | 0.Deg (ms)
text | 1672a49a-c81f-52aa-a50f-3aab5b5bd1c7 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | cbc87807-f050-582f-b711-73c20d34983d |  | textbox | 0.Deg (ms)
text | 598faf07-2162-5ba7-a77d-ec61fd4b7bbb |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | e6a4e3c6-8a6f-53b0-a724-80c99ef3f3ae |  | textbox | 0.Deg (ms)
text | e2c7cf93-faf4-5e04-ba57-3e979689f8b7 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 9ccf802b-a9fd-59c7-8e81-e1c0926fce0b |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 5
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 2f7d5726-93ac-5d00-bb76-1e1825883939 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 981cec8e-0f00-51e2-a5cb-a83672a18774 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 15f5e7e5-4c3d-52fe-a3bc-2d27fd4066b8 |  | textbox | RCD No
text | adf84622-2851-5197-9941-95aaabbae1f8 |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 99dfb392-626c-52bb-8d6f-b2d6266ff57f |  | textbox | 0.Deg (ms)
text | d5418340-165e-5f5d-aacd-71565c55a7e9 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 060eea98-3732-54ca-bc5f-322bd5a2792a |  | textbox | 0.Deg (ms)
text | 5cc98264-15eb-5a07-8b0a-f38b46798f30 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | f83c427f-4e4a-5c27-9fa8-29766aca57a2 |  | textbox | 0.Deg (ms)
text | be056345-27c7-57e6-814d-079e6146e4a1 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 53eb65b3-93b6-5219-97fc-d2c2e5180c86 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 6
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | abc759e0-2697-5b9c-8e62-6e9919e3732f |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 80566cda-e51c-5cd8-8c78-98de8a0d455e |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 2b830959-79f7-5c8f-8bf5-1e45e3c54fcf |  | textbox | RCD No
text | bebdc8fb-1e05-5c83-a0ef-90eb30eb6f33 |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 771c03aa-e0d0-55e3-88b6-8dedbaadd79f |  | textbox | 0.Deg (ms)
text | 726837ee-6372-5ffc-9035-cbc3a466d44c |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 91316e09-bb44-5837-a0e0-cbcaabb89698 |  | textbox | 0.Deg (ms)
text | ff5128c1-8b62-5a5f-9eee-02c8e8d2e18e |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | f44ba1d1-42f1-581c-a000-b8e76eb70374 |  | textbox | 0.Deg (ms)
text | 94fc8b8b-51b7-5815-8e59-471b1a3a25a6 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | a266dda9-a750-5a5b-91fd-81d3a6ccfa5c |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 7
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | db74813a-7211-5ca2-b7da-f6127677735a |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 3c05603d-d35e-5d0b-a632-d193da11cd54 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 299d3a78-d886-55a9-ba86-6b1fdab0dccb |  | textbox | RCD No
text | 006eccf0-a3b0-5ab0-ada8-9d39f930f3e4 |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 5e28b2a7-b4e1-5c06-bcd5-4a74c120cf91 |  | textbox | 0.Deg (ms)
text | 3c88fbbf-dae9-5e68-b69c-fb5f48610d89 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | b629aa79-5d81-55d9-b64a-73c665b80529 |  | textbox | 0.Deg (ms)
text | 57ccfbcc-712c-5519-8de6-2b8fb230e4b5 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | f2c07dab-10ad-5830-9b8a-9864bba3671d |  | textbox | 0.Deg (ms)
text | 5bd9bd9e-b008-5d9c-81e9-407872cb6356 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 2466b889-6028-55e6-bcc2-0c8cb7e9eaf0 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 8
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 45f58dd4-641e-5f02-a428-837dcdb09a33 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | f4942627-c34a-5dc3-a502-1cb722293143 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 400dc278-9ec7-50db-877b-14cfb99f733d |  | textbox | RCD No
text | 972f39bd-4e70-5855-b312-89723aa0531b |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 237e24a8-280d-5bb4-af24-0cb5dede0708 |  | textbox | 0.Deg (ms)
text | 6dbfda1b-2986-5605-aff0-f6f40c9e7f00 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | c80878d2-d87b-56f4-b131-799dbfc376c4 |  | textbox | 0.Deg (ms)
text | fb35c911-93b1-570a-9696-8f88e5e956d9 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 6e0eff6d-7735-5f26-9335-3f0764bdfc60 |  | textbox | 0.Deg (ms)
text | 5cecd341-44e0-555a-8967-04681eaa5c4f |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 8653fcd1-a84d-57c1-8f35-001ef8dbcace |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 9
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 8049bebc-595f-5aa0-891b-b494edc4c743 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | ee732a49-8e87-544d-b4d4-334872f687f6 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 27bb8278-2393-5d16-8fa3-8376c31c01bc |  | textbox | RCD No
text | 88480da7-8a1e-5d31-b223-e221eea7cf3f |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | ebdc4d25-cbd0-5bab-80f5-c17b809f9c4c |  | textbox | 0.Deg (ms)
text | 8f1af36e-6f75-5f0b-9852-b53148c0f3e1 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | f058665c-faf6-5a57-8591-ae4a69957deb |  | textbox | 0.Deg (ms)
text | e229bb4c-f301-507d-bb52-d96595b6f8e9 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | f3f4aaef-5b94-5c28-87b2-0432c40033b1 |  | textbox | 0.Deg (ms)
text | df43d1d5-0ae2-5a4e-b37c-df3ce1c5123f |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 1e35cb7b-63d3-53af-b57c-0f9263b871da |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 10
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 1535ad4d-d651-575c-aad5-9113aad5f52e |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 5ff7711c-a898-55bb-bd72-6e1826d3be33 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
text | 7c25642f-35d3-5a1e-87d6-66e27412212b |  | textbox | RCD No
text | 6abe3e58-7734-5bb1-821d-96e34fefa384 |  | textbox | Nominal Trip Current (mA)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | f004d289-249b-5bc6-9f78-c8b742be1bda |  | textbox | 0.Deg (ms)
text | ac4c8697-13d8-5810-80ca-4b69b1a46f62 |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 5bcfd858-b8ff-5011-ad5d-598505eeb663 |  | textbox | 0.Deg (ms)
text | 0375be40-39a8-540d-8ddf-aabb627695ad |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 270daa67-99cf-56e7-ae73-c9229a41f44e |  | textbox | 0.Deg (ms)
text | 7a2be255-3a44-5911-b928-6d41aaced53a |  | textbox | 180.Deg (ms)
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | f5723a1f-42d5-5875-adc0-047f0d322770 |  | textbox | Action taken
checklist-flat |  |  | checklist | AE-ITCX-012 - MEN & MSB Meter Panel Checklist (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-012 - MEN & MSB Meter Panel Checklist (Rev 0 +Names) | 3ea7beab-3862-4c04-924b-7ec55e4d4a32
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | b6240f9d-60b3-5682-8554-e2710e5f2233 |  | textbox | Drawing & Revision #
text | 1c9b492b-e748-5f42-9fc3-80a857513d48 |  | textbox | Switchboard No.
checkpoint-status |  |  | checkpoint | Incoming Service Protection Device
text | 86ecd2b1-f06f-5c29-9d71-56ac7cfa83ae |  | textbox | A
text | b0fa9d1e-5e0e-53f6-963f-3a7e24072608 |  | textbox | kA
checkpoint-status |  |  | checkpoint | CTs Installed
text | 62b678c3-510c-5c93-98bc-5c25b7b0e401 |  | textbox | CT Ratio
checkpoint-status |  |  | checkpoint | CT Rated to Suit Supply
checkpoint-status |  |  | checkpoint | CT - Meter Mounted
checkpoint-status |  |  | checkpoint | CT - Metering Loom Installed
checkpoint-status |  |  | checkpoint | Voltage Fuses checked
text | 29dbae4b-65b3-52e2-a9f2-55fc57c4d002 |  | textbox | Amps
checkpoint-status |  |  | checkpoint | Isolation Circuit Breaker checked
text | becde662-ff2f-53c2-981b-282b8fd1d658 |  | textbox | kA
select | 33c620fb-6156-51ef-8517-5b2c3d36e8fa |  | dropdown | Isolation Method | Circuit Breaker, Isolator
checkpoint-status |  |  | checkpoint | Earthing Testing Completed - As per below
text | dac4d3a3-4cae-51ea-ad36-5dd39327cf4f |  | textbox | Main Earth Resistance Test (Substation) - Ohms
text | f7b6a828-2861-5169-9113-50e889b0f329 |  | textbox | Earth Resistance
text | 6843ff61-7bec-5102-84b3-ef5bf5abc7f4 |  | textbox | Earth Stake
select | 4ec084e6-ff43-5cb1-b278-f98256f351e0 |  | dropdown | MEN Position | Wall Switchboard, Main
button | 0720b039-4251-546a-aaae-08532d4d5752 |  | button | MEN Size Equal to Neutral | Yes, No
button | b3ab76f6-b5aa-56dd-9fb1-d924e407b5e8 |  | button | MEN Bonded to Switchboard Chassis | Yes, No
checkpoint-status |  |  | checkpoint | Bonding Testing Completed - As per below
text | a473ad8a-fded-5bc4-ba87-0ff5434c6c8a |  | textbox | Cold Water
text | 67bcc1dc-513f-5faa-88a8-ef1313fd5e83 |  | textbox | Cable Support Systems
text | b1bf8470-51be-50a9-b891-cbd7d31ceb75 |  | textbox | Fire Hydrant
text | 336f713d-0505-5002-9a76-21e9c5e48910 |  | textbox | Gas Services
checkpoint-status |  |  | checkpoint | Labelling Inspection - DB Labels installed
checkpoint-status |  |  | checkpoint | Labelling Inspection - Cable Labels installed
checkpoint-status |  |  | checkpoint | MEN & MSB works completed to specification/drawings - Area left clean & tidy
label | 794eaf83-bde1-54b7-b6a7-666256d5907c |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 56ea68b0-7306-581b-83b3-67cf195c2e83 |  | note | Any Corrective Actions to be Photographed & Commented below
label | eecad978-a1d7-513b-953c-0f92005984c0 |  | note | .. ..
text | ca15535d-de98-5a10-912a-24ded922e309 |  | textbox | Test Equipment Tester Type
text | 441b263e-5e92-54a3-a2f3-60ebb5a32a8d |  | textbox | Serial No.
text | 09aacf2b-e294-5a8d-a652-4a55d428d2e5 |  | textbox | Calibration Certification Date
select | e98cd903-8f16-5610-9ee7-517ec7230948 |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 3642eabc-aed3-57e8-9917-33cb450b9e58 |  | textbox | Other (Specify here)
select | 24241fe0-d75c-5b6b-a47d-46854985a26f |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 3a0babd7-df06-5ca9-b839-63cd815f3a18 |  | textbox | Other (Specify here)
label | ccb04c19-2c17-55f9-a91f-3482bf08482f |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-031 - Fit-Off General Checklist (Rev 1 +Names) |  |  |  |  | Yes | AE-ITCX-031 - Fit-Off General Checklist (Rev 1 +Names) | 45ef61d2-47a4-42fd-94c8-f1a67ef99e03
checkpoint-status |  |  | checkpoint | Wall Fit Off - Light and Power
button | 1ab8279c-048b-5e89-9fdf-a2a2c6a758c8 |  | button | Power outlets fit off including GPOs, isolators & hard wired equipment are all fit off, straight and installed by installer with black texta | Yes,No
button | c05ffa27-c4c8-5d62-b97d-025dfd1e1472 |  | button | All Light Switches and LCP's are fiit off and switch plates initialled by installer with black texta. | Yes,No
label | 1f048da9-ea6a-5893-84c1-44dab79cadac |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
label | e48f52b4-af38-5c74-ade3-6b284f62601c |  | note | Additional Photos as required.
checkpoint-status |  |  | checkpoint | Ceiling Fit Off - Light and Power
button | 0a54d677-dd2b-581c-9af5-9b4f7ff3ea85 |  | button | All Light Fittings, drivers, PUKS etc are fit off as per shop drawings | Yes,No
button | bc193007-68c8-5313-ba76-c87cf922aee0 |  | button | All LED, joinery and feature lighting is completed as per shop drawings | Yes,No
button | d552cb9b-e5d7-5ab7-8917-07b3e7cfd7b0 |  | button | All external Lighting, 240V Motion Detectors and Smoke Detectors are completed as per shop drawings | Yes,No
button | 64e876b1-649e-574b-84a7-3aea7d0cc17c |  | button | All required EMG and Exits are installed labelled and unobstructed from required view as per shop drawings | Yes,No
button | 9121ed5e-ef4b-5c1a-9446-8fb20788ab31 |  | button | This installation is considered ready to hand over to Commissioning crew. | Yes,No
label | 49be55a0-4190-58ef-ba12-228c51b4e5e6 |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
label | eaad6f75-4f68-5207-ba6c-03e11ac1650d |  | note | Additional Photos as required.
checkpoint-status |  |  | checkpoint | MATV and Cat6/6A
button | 8ea5e6b4-26c1-590f-b9b4-f82ec7704adf |  | button | MATV outlets and splitters are fit off and splitters are fit off with correct F-Connect Tools (no frayed copper strands!) | Yes,No
button | 22435a8e-1d60-55fe-8a8d-d3568700c0bc |  | button | All Cat6/6A outlets are fit off with outlet label on switch plate (behind cover) along with the initials of the installer. (check CCTV and Intercom when applicable) | Yes,No
label | 7599a373-5ad2-5263-9e37-fd410b0ced16 |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
label | 63f58121-d6fc-56d0-bcc2-fba832d8251d |  | note | Additional Photos as required.
checkpoint-status |  |  | checkpoint | Fit-Off completed to specification/drawings - Area left clean & tidy
label | 7e4f13df-f79b-5817-9227-c7027550b7d2 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 50599ad4-8e1f-5890-940c-884e89c39576 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 146f3c26-3032-5717-870c-7be94b0e6a36 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622, ADAM STRONG - AGrade: A38815 - Employee#: 2002, ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794, ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684, ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863, ALAN BIRCHALL - Agrade: A18981 - Employee#: 379, ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111, ALI HASAN - Agrade: A48087 - Employee#: 1654, ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015, ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972, ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309, BEN DARBY - Agrade: A53332 - Employee#: 1702, BEN FINDLAY - Agrade: A41429 - Employee#: 2006, BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933, BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733, BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801, BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850, BRENTON HILL - Agrade: A47213 - Employee#: 1729, BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887, BROCK DOWNIE - Agrade: A53290 - Employee#: 1849, BROCK LLOYD - Agrade: A44808 - Employee#: 1680, CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193, DANIEL BENDINELLI - Agrade: A67728 - Employee# 2097, DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937, DAVID OLSEN - Agrade: A42915 - Employee#: 1685, DEAN NGUYEN - Agrade: A48514 - Employee#: 1515, DEREK JACOBS - Agrade: A67318 - Employee#: 2078, DWAYNE KLOET - Agrade: A48278 - Employee#: 1239, ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782, EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895, FERGUS COATES - Agrade: A59054 - Employee#: 1774, FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679, HUY DO - Agrade: A40954 - Employee#: 873, IMMANUEL KAWITI - Agrade: - Employee#: 2023, JACKSON SHARPE - Agrade: A53801 - Employee#: 1540, JAMES MARASCO - Agrade: A55184 - Employee#: 1758, JAMES PLEASANT - Agrade: A62956 - Employee#: 1976, JAMES SPOKES - Agrade: A48756 - Employee#: 1770, JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756, JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719, JASON PERL - Agrade: A36692 - Employee#: 1868, JASON SALE - Agrade: A28662 - Employee#: 1615, JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029, JESS ZAHRA - Agrade: A52969 - Employee#: 1403, JOEL BASSETT - Agrade: A39498 - Employee#: 1958, JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908, JOHN GREEN - Agrade: A55589 - Employee#: 1734, JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682, JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720, KALE BLACKLER - Agrade: A39293 - Employee#: 1751, KAYNE WALKER - Agrade: A38805 - Employee#: 1718, KEVIN MURPHY - Agrade: A63544 - Employee#: 2022, KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698, LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834, MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308, MARK D_ANGELO - Agrade: A40610 - Employee#: 1832, MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352, MATTHEW COX - Agrade: A42092 - Employee#: 1704, MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894, MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915, MICHAEL BRASHER - Agrade: A29237 - Employee#: 954, NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748, PAT DOUBLE - Agrade: A46604 - Employee#: 1118, PAUL HARMAN - Agrade: A26306 - Employee#: 1728, PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190, PETER LEWIS - Agrade: A53556 - Employee#: 1749, PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612, ROB POLLARD - Agrade: A56906 - Employee#: 1754, ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132, RYAN DEPRADA - Agrade: A41361 - Employee#: 1848, SCOTT RYAN - Agrade: A59062 - Employee#: 2017, SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034, SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771, SIMON COLLARD - Agrade: A32749 - Employee#: 883, STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829, TOM HAMILTON - Agrade: A48254 - Employee#: 1434, VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218, WILLIAM FISHER - Agrade: A20679 - Employee#: 859, Other (Specify below)
text | d92c63ad-cb59-5790-b913-6a7e90ad7241 |  | textbox | Other (Specify here)
label | 7fe77e14-3836-56da-9aa4-3a8fd2be3260 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AF-502 - Electrical Services commissioning Sheet - DETAILS & 10x Circuits- Insulation Resistance (Rev 0 +Names) |  |  |  |  | Yes | AF-502 - Electrical Services commissioning Sheet - DETAILS & 10x Circuits- Insulation Resistance (Rev 0 +Names) | 4cf2bfed-805a-4ed5-870e-d10822c1f0e6
checkpoint-group |  |  | section | Electrician Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 1fe907a4-fc06-558f-9d80-86f142d8bb27 |  | textbox | Test Date
select | ab83fc2a-bdca-5289-80bc-d09825544f10 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 66a1c52a-20c0-5d2b-a629-3452228b40dc |  | textbox | Other (Specify here)
boolean | 6e421532-5829-544e-8408-66ddb5b27651 |  | tickbox | Signature added below
checkpoint-group |  |  | section | Circuit Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 2b418224-e1b4-59f6-9f46-291fa45e485d |  | textbox | Designation of service
text | 5bbb7c1b-6725-5c36-a3ba-ee538320d50f |  | textbox | Location of Service
label | d26c8e43-fe85-55b5-b5c3-7f4f5530ca53 |  | note | L1= Red Phase, L2= White Phase, L3= Blue Phase
label | 779c721c-13a7-5fb5-adb8-e6cdb36ea134 |  | note | Where a single phase circuit is being tested, enter the result in the column that corresponds to the supplying phase, enter N?A for the other phases
checkpoint-group |  |  | section | No. 1
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 0e0a84c3-e5e0-5802-a37f-6bd880cdbf77 |  | textbox | L1 - N
text | 52f89146-8a57-5443-b542-8f7469c0e358 |  | textbox | L2 - N
text | 6d5dbfc6-87ee-59b9-8e6d-7dc36fc53989 |  | textbox | L3 - N
text | 2e4e1425-071e-51d9-900c-dfb0a9f427f2 |  | textbox | L1 - E
text | e3bbba2c-8f68-53ce-8260-8361fb4947bb |  | textbox | L2 - E
text | 10248b98-f62f-590d-b043-cc4ce136f847 |  | textbox | L3 - E
text | 0d96f7f9-601c-567a-95cf-a4aab8bc7415 |  | textbox | N - E (MEN Disconnected)
checkpoint-status |  |  | checkpoint | L1-L2 (N/A if 1 Ph)
text | c7929a0e-ceff-5dfe-8db0-ee0d97be5c4e |  | textbox | Calculation
checkpoint-status |  |  | checkpoint | L2-L3 (N/A if 1 Ph)
text | 3df74268-a5ee-5180-8fa7-8208a7f3f2cb |  | textbox | Calculation
checkpoint-status |  |  | checkpoint | L1-L3 (N/A if 1 Ph)
text | 38779916-0474-52d8-9d8b-cc4719a1290f |  | textbox | Calculation
checkpoint-group |  |  | section | No. 2
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 480dbbdd-3f55-5500-aa8f-a9a00d3f42e1 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | aec42422-b76d-5555-97ef-e07e4a4faabc |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | dd4ba209-e52a-5389-9824-1eab3e174b15 |  | textbox | Rating in (A)
text | 1e223a1e-9fbd-54da-bccc-0894216f954f |  | textbox | (A) Active CSA mm2
text | a490f444-c658-5160-a41e-b697bb8181ec |  | textbox | (B) Earth CSA mm2
text | 2aadbcd5-a751-5d4c-8731-143dfaddf270 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | d633ec0c-3c8e-5228-bc2a-c35540b5b872 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 10d4dfb1-e30c-59c7-967d-d47ed0cecda9 |  | textbox | RE = (D/C) * A
text | 74caafe9-3fe3-528d-af9b-ce6710bc058a |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 0f82d48e-e9cb-5c81-a8c1-71c9b31fce48 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 2547492c-143b-5840-adcc-cc719f6820fa |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 3
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | b5d20a41-ed35-54f2-a745-b746b38552be |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | d15ad5e4-0b4e-5aad-86c2-22d6d7588e66 |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | 36d51440-ed4a-59f8-b349-794af7979aa5 |  | textbox | Rating in (A)
text | c77d20e4-4b93-5e67-8b31-2b06d6b30940 |  | textbox | (A) Active CSA mm2
text | 983bf74b-59fb-5a87-822e-de13b41983fd |  | textbox | (B) Earth CSA mm2
text | b5bad88d-9596-5576-81c3-69be48b4f684 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 03a58f10-d356-578b-8660-6ae54edc972c |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | e5637de0-f42e-55ef-99a5-2408678abee4 |  | textbox | RE = (D/C) * A
text | f15630a3-cf0b-5fa6-98d0-085d8f433139 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 629a2ca3-59e6-5263-9c6d-0b2accff16f4 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | bf8f3a7c-1e8c-5e90-9165-456d8b0f5dec |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 4
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | b24f600e-55b1-512b-a0fe-410df2f06841 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 0edf3e5a-6bf2-5706-8fe1-aa0777d24528 |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | 28509b76-9e75-5aea-8714-f3e4fe034bdb |  | textbox | Rating in (A)
text | 6318779a-2215-567e-99c3-d9eb7be51084 |  | textbox | (A) Active CSA mm2
text | 655e4392-5894-508e-815b-718c6ed94617 |  | textbox | (B) Earth CSA mm2
text | 6349d6e9-2412-5808-bc4d-0ca472cd69ec |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 79801b05-9e97-504f-9080-7458211e68a1 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | bac3b337-bb45-50a5-93d6-0a348d7632fc |  | textbox | RE = (D/C) * A
text | 7f126772-f3e6-5b98-8f22-03bb8de5f4ce |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 10cd1581-8394-528e-a67d-19bf3ce482d5 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 40f09f15-d44e-5f66-94ad-1b96c4ccf5ae |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 5
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | b85b4483-e79d-5988-ba6a-19c149024caa |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | d4f53a81-0557-5523-b682-a38800610f08 |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | 53688452-0cf9-5b92-b694-7174877c29d2 |  | textbox | Rating in (A)
text | eda89c4f-769a-500d-8f6d-a39ee6aed451 |  | textbox | (A) Active CSA mm2
text | 96488c9e-42bd-5f8c-b350-53c14cec91db |  | textbox | (B) Earth CSA mm2
text | cd8324cd-0021-515f-aefb-4caca366b43f |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | af1c06d4-2e1c-519d-b823-04d286954800 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | e18fdbf3-96c1-56b6-aaa5-18a18dbbd868 |  | textbox | RE = (D/C) * A
text | c0901d9a-478f-5989-abee-24ae2f17b5c0 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | bf021fb2-0c53-52ce-95e5-f88218f2f0ba |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 77eee0bb-36a2-5003-bc02-1ec034c099c0 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 6
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 01477949-e01a-5e02-a611-b98b1fa4f808 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 53d938c4-4485-5bbc-9e7c-9a8fc43c9ee2 |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | 0b9e7871-0391-5bcc-8ca3-1214a86ee5c0 |  | textbox | Rating in (A)
text | 46fb5311-654b-58ca-83cb-25cfd9505bb1 |  | textbox | (A) Active CSA mm2
text | f55a4fc4-a8f2-50f0-9df5-3b0eedad8644 |  | textbox | (B) Earth CSA mm2
text | 137113b9-4dd8-5003-96af-59fa29482a5b |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 3c2ea4a5-5656-5fbf-b35a-395547763a4c |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 48e6c1b7-9054-5e85-8197-6b5e3c282549 |  | textbox | RE = (D/C) * A
text | 22366daa-9035-5afe-9e91-74731ecd9da3 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 75772400-4429-5e7b-8a19-f6d2efb54f1c |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 0a6a7cc2-5eca-53e3-a423-50d27d887767 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 7
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 05c14a34-16fe-50ee-9917-4c5a6d103941 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | f5007929-54cb-50d2-a2ab-40c854a411aa |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | 88f05681-b7ff-536d-987e-cac39a80cc87 |  | textbox | Rating in (A)
text | 3cff4173-80a1-5952-b5cd-ce0480c2c8c1 |  | textbox | (A) Active CSA mm2
text | dcd8a0dc-ddaf-58c1-80eb-e78fc9b61f60 |  | textbox | (B) Earth CSA mm2
text | 9c9b8327-436b-5774-8c98-c7076a3a9c32 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 48472c2c-c55c-5316-8af2-0a914cf44e57 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 4070c461-15b6-53cc-8ef7-99b3b1ea251c |  | textbox | RE = (D/C) * A
text | 3434cfc0-cbea-5426-a0bb-0385ac42d891 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | b086891e-c234-5cae-8503-e262a5da3709 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | efec1a29-a0c7-5cf8-9278-3e879e268397 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 8
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 3ed5f450-e10c-5535-8b37-4c04dc2c67c0 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 76e98b4d-fc2d-581a-9cdc-df66ade6c373 |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | f542fc84-00e1-5759-b0e9-3e224eb4b1df |  | textbox | Rating in (A)
text | 7c645989-8a25-5115-ab8b-2442d3d7b713 |  | textbox | (A) Active CSA mm2
text | ff65fa57-a1b0-5c1a-a555-c66031d2a7dd |  | textbox | (B) Earth CSA mm2
text | 156192c3-0e46-5745-a07c-cb2c3bd943b9 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 9b8ff8bf-4062-59fd-88e0-486ba9bb1ffe |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 222d6c92-1e67-5d75-aa81-61ad263bddad |  | textbox | RE = (D/C) * A
text | 94f03e8c-0840-5b7b-ad54-784de1ae9d04 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 38dc81b7-ac79-5014-ae47-53b260b4ee27 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | e757da96-656b-551e-9de5-0189dd09db90 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 9
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 069e99d7-90f1-5a54-94a3-c3570ebd6196 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | f85ccd45-5877-5b59-8806-bb7405a69cad |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | a4479498-012d-5fb6-ad6e-f7996fc12c1e |  | textbox | Rating in (A)
text | 2d8c6d2f-a168-5fe4-9dc0-5e731af1ac0e |  | textbox | (A) Active CSA mm2
text | 83d65d1c-e904-59f9-a848-0abc22ff0f08 |  | textbox | (B) Earth CSA mm2
text | 9386ddbb-e439-5f93-aa60-14d2dd7c1d12 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 394f7936-f22b-5f32-ac63-6785321595b0 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 5fc459d6-e5a3-5951-992f-a74ed487f176 |  | textbox | RE = (D/C) * A
text | 29f22b9a-024b-58de-8cae-495a4f012602 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | d11c588e-9806-5704-82e2-24516ce6bb0e |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 5e71b9c1-0ef7-5467-aa7b-116e8f9d9425 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 10
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 8ddf684b-c02b-594d-a0bf-0013e203a3ab |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 5e1a5cd3-88de-55e7-8740-96c0aabf5d64 |  | textbox | Type B, C, D, TM Electronic
checkpoint-status |  |  | checkpoint | Data Capture
text | 4cfc4446-73dd-50ed-b36a-df9720805bd2 |  | textbox | Rating in (A)
text | 0e2c4461-eca9-555f-b69a-b7e1137ce7f7 |  | textbox | (A) Active CSA mm2
text | d040e91e-0007-5de8-8bb1-915ca091acc4 |  | textbox | (B) Earth CSA mm2
text | 553b8d15-8368-58f0-bfbf-21a17fe4b9be |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | e7987ece-65e3-5eb5-8dd9-06da9cea9149 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | cb2e1811-3f18-5a13-be1a-a09fffb845fb |  | textbox | RE = (D/C) * A
text | 0cd4274e-be5d-5a77-87da-5fa3ed5cdf20 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 44d8b00f-beeb-514b-85a3-1d63ca9079d1 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 853733a8-32c5-5fa1-bcfa-00ec9c1d9bc1 |  | textbox | Difference (F) - Calc'd ZS
checklist-flat |  |  | checklist | AE-ITCX-036 - Cable pit installation |  |  |  |  | Yes | AE-ITCX-036 - Cable pit installation | 57b01fb8-c17b-4b6a-a452-a372bf2c8394
checkpoint-status |  |  | checkpoint | Pit installed in correct documented location
label | 0c8a7224-a6b3-5fbf-b000-5eaa8f990ef8 |  | note | * Mandatory Image - (Drawing Title Block)
checkpoint-status |  |  | checkpoint | Pit installed to the correct RL (Reference Level)
label | 7ca81d04-def4-55e2-945c-479eb69e741a |  | note | * Mandatory Image - (Drawing Title Block or Surveyor Details)
checkpoint-status |  |  | checkpoint | General Checks
button | 2ccee882-f4b9-5d75-be1a-25b68fa824e0 |  | button | Bellmouth conduit sealant is installed where conduits enter pit. | Yes,N/A
button | c7a73896-57e5-52b6-b8de-57646c654c15 |  | button | Is drainage connected to pit | Yes,N/A
button | 8005a0a8-bf1d-52c4-bf44-f0057fed5268 |  | button | Pit lid is squared and leveled | Yes,N/A
button | c8eae67b-cff5-5b35-b297-2da793f64f0d |  | button | Pit has been caulked between lid and riser. | Yes,N/A
button | 066ef4a7-8b1b-5bc1-b7e1-4f1c49ef4366 |  | button | Pit is cleaned and clear of debris. | Yes,N/A
label | 7c937baa-056b-5be0-97c1-bf58066d7cef |  | note | *Mandatory Images Pit Installed (lid on finsished)
label | 023bf531-b9bf-55b0-82bc-347f8f55791d |  | note | *Mandatory Image Pit Open visual of conduit entrys (Multiple images if required).
checklist-flat |  |  | checklist | AE-ITCX-028 - Lead-Ins Checklist (Rev 1 +Names) |  |  |  |  | Yes | AE-ITCX-028 - Lead-Ins Checklist (Rev 1 +Names) | 5838fde0-8db3-4e03-94f1-fc4f2060ec0e
checkpoint-status |  |  | checkpoint | Lead In Cables been roughed in to final locations as listed below completed?
button | a2ce0375-788b-5fa8-8ed0-ca73326179dc |  | button | Submains installed to the documented location in the field/riser, grouped together 3 or less and labelled correctly? | Yes,N/A
label | d1386db9-94f9-5101-82a0-37b5b24232d8 |  | note | *Mandatory Image - Marked Drawing Including Title Block Revision
button | 47caf0df-30e0-5dc1-965e-7ccbd2982b99 |  | button | MATV cables installed to the documented location in the field/riser and labelled as per shop drawings? | Yes,N/A
label | c7ac0947-ca35-5326-a0a0-f73a2eab108d |  | note | Is Cat6/6A Intercom Cabling Appselec scope and installed to correct location? - (If sub contract N/A)
button | 0bbb8f85-a992-5390-b987-b2dd784b1ad3 |  | button | Confirm Cat6/Cat6A leadins installed as documented. (This may include House Area CCTV/WAP outlets on drawings also) | Yes,N/A
label | be465f63-d5f1-53d8-917f-98032952e8f4 |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
checkpoint-status |  |  | checkpoint | NBN and Private Network conduits been completed?
button | fd82821f-7389-5f47-840b-9095ed909393 |  | button | P23 White Comms Conduit installed to the documented location as per Appselec Shop Drawing | Yes,N/A
button | f592e8e3-efd3-51ad-8ed8-357b58ea0508 |  | button | Draw string installed with the correct “stopper” tied off and labelled correctly? | Yes,N/A
label | 0671f322-8181-565a-a281-6f455e1420e0 |  | note | *Mandatory Image - Pathway Drawings Drawing Including Title Block Revision
checkpoint-status |  |  | checkpoint | General Checks
button | adc4d628-75ec-5755-a50e-39f5d5158d99 |  | button | Apartment Recessed DB installed prior to plaster, in the correct location and height? | Yes,N/A
button | 29745acf-1ebb-5acd-8daa-741ea07c25a0 |  | button | Leadin cables & conduits have been installed ready for fire rating systems and are in correct locations. | Yes,N/A
checkpoint-status |  |  | checkpoint | Lead-Ins completed to specification/drawings - Area left clean & tidy
label | 52357544-8e60-5bc3-bfa1-653c9e4f1157 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 1933a4ab-7ae9-5d2b-8f7f-429f0c467038 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 37816b4c-8ab3-5135-b5d0-f77a00c8b504 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622, ADAM STRONG - AGrade: A38815 - Employee#: 2002, ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794, ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684, ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863, ALAN BIRCHALL - Agrade: A18981 - Employee#: 379, ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111, ALI HASAN - Agrade: A48087 - Employee#: 1654, ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015, ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972, ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309, BEN DARBY - Agrade: A53332 - Employee#: 1702, BEN FINDLAY - Agrade: A41429 - Employee#: 2006, BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933, BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733, BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801, BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850, BRENTON HILL - Agrade: A47213 - Employee#: 1729, BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887, BROCK DOWNIE - Agrade: A53290 - Employee#: 1849, BROCK LLOYD - Agrade: A44808 - Employee#: 1680, CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193, DANIEL BENDINELLI - Agrade: A67728 - Employee# 2097, DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937, DAVID OLSEN - Agrade: A42915 - Employee#: 1685, DEAN NGUYEN - Agrade: A48514 - Employee#: 1515, DEREK JACOBS - Agrade: A67318 - Employee#: 2078, DWAYNE KLOET - Agrade: A48278 - Employee#: 1239, ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782, EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895, FERGUS COATES - Agrade: A59054 - Employee#: 1774, FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679, HUY DO - Agrade: A40954 - Employee#: 873, IMMANUEL KAWITI - Agrade: - Employee#: 2023, JACKSON SHARPE - Agrade: A53801 - Employee#: 1540, JAMES MARASCO - Agrade: A55184 - Employee#: 1758, JAMES PLEASANT - Agrade: A62956 - Employee#: 1976, JAMES SPOKES - Agrade: A48756 - Employee#: 1770, JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756, JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719, JASON PERL - Agrade: A36692 - Employee#: 1868, JASON SALE - Agrade: A28662 - Employee#: 1615, JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029, JESS ZAHRA - Agrade: A52969 - Employee#: 1403, JOEL BASSETT - Agrade: A39498 - Employee#: 1958, JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908, JOHN GREEN - Agrade: A55589 - Employee#: 1734, JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682, JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720, KALE BLACKLER - Agrade: A39293 - Employee#: 1751, KAYNE WALKER - Agrade: A38805 - Employee#: 1718, KEVIN MURPHY - Agrade: A63544 - Employee#: 2022, KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698, LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834, MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308, MARK D_ANGELO - Agrade: A40610 - Employee#: 1832, MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352, MATTHEW COX - Agrade: A42092 - Employee#: 1704, MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894, MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915, MICHAEL BRASHER - Agrade: A29237 - Employee#: 954, NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748, PAT DOUBLE - Agrade: A46604 - Employee#: 1118, PAUL HARMAN - Agrade: A26306 - Employee#: 1728, PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190, PETER LEWIS - Agrade: A53556 - Employee#: 1749, PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612, ROB POLLARD - Agrade: A56906 - Employee#: 1754, ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132, RYAN DEPRADA - Agrade: A41361 - Employee#: 1848, SCOTT RYAN - Agrade: A59062 - Employee#: 2017, SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034, SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771, SIMON COLLARD - Agrade: A32749 - Employee#: 883, STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829, TOM HAMILTON - Agrade: A48254 - Employee#: 1434, VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218, WILLIAM FISHER - Agrade: A20679 - Employee#: 859, Other (Specify below)
text | edc8ecc8-1b5c-5cc1-94e4-61ae3ad08a60 |  | textbox | Other (Specify here)
label | 276028ab-efe2-513e-a950-3d47fdce5c07 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | Cage Installation checklist |  |  |  |  | Yes | Cage Installation checklist | 5f3e00f1-0a28-4482-a481-740a74fed884
checkpoint-status |  |  | checkpoint | Cage Installed - N/A if no, PASS and add photo if yes
checklist-flat |  |  | checklist | Concrete poured into cage checklist |  |  |  |  | Yes | Concrete poured into cage checklist | 5f4e3e63-ce45-41cb-a488-0dfff6913c52
checkpoint-status |  |  | checkpoint | Concrete poured into cage - N/A if no, PASS and add photo if yes
checklist-sectioned |  |  | checklist | AE-ITCX-009 - Mains Cabling Reticulation Test Sheet (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-009 - Mains Cabling Reticulation Test Sheet (Rev 0 +Names) | 61aae376-75d2-4265-91bc-11eb17dacff5
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 253bd109-1bce-5063-bf3b-10de581ff2d1 |  | textbox | Drawing & Revision #
checkpoint-group |  |  | section | Test No.1
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 0bb91c65-3114-5e65-ac35-81527cdf06df |  | textbox | Cable No
text | fad1edb7-a6f9-5240-b5ba-79c2acca450a |  | textbox | Cable Origin
text | 4a5136e3-317f-5cd6-9ac0-95496b9208d6 |  | textbox | Cable Destination
text | 67a271c0-62f3-521e-8211-3e9b725dc03e |  | textbox | Upstream Circuit Breaker Size
select | 98077863-5279-5e06-9e08-26e3677f3da1 |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 860943fd-c31a-52c6-8e46-e80e5ac4ac3b |  | button | Fire Rated | Yes, No
text | 8fc0560f-427f-5c20-b70c-1abc6036558b |  | textbox | Cable Size (mm²)
text | 4e17dd45-62c6-5fb7-8c8b-2f0165e17e70 |  | textbox | Earth Conduit Size (mm²)
text | 7cf84ea8-9892-5dcc-918f-c4ef83b3a82e |  | textbox | Earth Conduit Size (mm²)
select | de85cf7f-ccad-542c-922f-85f0f5283bec |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 9e0230e3-610e-50cd-b46d-835549be795a |  | textbox | Other (Specify here)
button | f086dcce-4ac3-585b-8d8a-abe524e70e39 |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | bf7da1b6-bd60-562e-9a0f-90a4bcd00bca |  | dropdown | Cable Spacing | Trefoil, Flat
text | bbabb905-bdaa-576a-aa98-dcff9d1a1925 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | f47b3c14-ecf7-5762-9710-674380dc7c37 |  | textbox | Red / White
text | a2d40899-ceeb-560d-a1a9-49a90429d73d |  | textbox | Red / Blue
text | 1d05f9ef-34ef-5cca-b370-eebceb9f248e |  | textbox | Red / Earth
text | 06c66f25-4986-5658-aea1-8256b2268654 |  | textbox | Blue / White
text | c261f60f-b4a7-5248-adeb-23a613dba47c |  | textbox | Blue / Earth
text | ddf9a9ea-c1dd-522f-9c21-a9215eac931c |  | textbox | White / Earth
text | 3bb97c54-28f7-5cd9-9ff5-0ee97aa2a417 |  | textbox | White / Neutral
text | 3ff4997e-7b56-5c3a-951b-76b2777318d2 |  | textbox | Red / Neutral
text | 20c3e91a-4f49-5072-8f57-051de658e232 |  | textbox | Blue / Neutral
text | f66d27fb-3ca4-5909-95ac-f8deee0ed4e1 |  | textbox | Neutral / Earth (MEN Disconnected)
text | 30c04906-513b-53de-aba8-cd42b044108f |  | textbox | Earth Loop Impedance
text | 427fa668-570c-5d50-9e4c-fe55cbd58a1e |  | textbox | Name
label | dae411a3-9a97-52d8-8bfb-d8d44e6edf3a |  | note | Signature added below
checkpoint-group |  |  | section | Test No.2
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 4802c89b-77dc-5479-b922-9c96d67a407e |  | textbox | Cable No
text | b6a11c78-b27f-5a92-b0cc-19fe4bfbed90 |  | textbox | Cable Origin
text | 4104c07a-e68b-5376-8ab1-15519122483c |  | textbox | Cable Destination
text | 8f84780a-f334-500a-97c5-cb6cf7c3cc9f |  | textbox | Upstream Circuit Breaker Size
select | de8542da-74ae-5796-a802-5c7bec169e0e |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 19831c7f-2fa2-5e0c-98d5-dd15c7c98f2e |  | button | Fire Rated | Yes, No
text | 114e75b1-7226-59a4-9671-915443f780bc |  | textbox | Cable Size (mm²)
text | d7e134fc-56df-5fee-8580-14c1a5db4a83 |  | textbox | Earth Conduit Size (mm²)
text | 2064d9b6-fcc8-5e6c-8562-ecd18892f440 |  | textbox | Earth Conduit Size (mm²)
select | 6fc7f5ae-5673-528e-a45a-8f604ff3a60e |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 394bb46d-8b68-5a74-97cf-5869d906f030 |  | textbox | Other (Specify here)
button | 644240f7-8f29-5993-b905-c05d2c50f735 |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | 1ca4e044-1ab1-5a35-ae48-f0a292a9d298 |  | dropdown | Cable Spacing | Trefoil, Flat
text | f15c60ee-f4cc-5143-9a0e-65cd9543b749 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | 859e8a90-06a4-5316-8e2f-31d1145565b1 |  | textbox | Red / White
text | df27a160-a9d0-58c0-a8c4-4fa14fd95b14 |  | textbox | Red / Blue
text | bbd82b35-b157-5a68-838e-dc4034cf075a |  | textbox | Red / Earth
text | 332a902c-760e-5718-b85d-99f8a16c9724 |  | textbox | Blue / White
text | 74ab95bd-aa80-584a-ab8c-68c1d647c90f |  | textbox | Blue / Earth
text | 72ad8a20-35da-5eaf-adc4-32b7a0c3cf7a |  | textbox | White / Earth
text | 328651b2-386d-5946-b3bf-9b98e6801052 |  | textbox | White / Neutral
text | 022bb06d-9ac2-5af7-9124-2335fdee7ba8 |  | textbox | Red / Neutral
text | d1e64c80-7dd8-57aa-8c9b-220bb3f80685 |  | textbox | Blue / Neutral
text | a2c5762c-fc5b-55ae-84a1-20b6e07fb065 |  | textbox | Neutral / Earth (MEN Disconnected)
text | a95b57f8-f245-5651-b2f8-88d943c07fb7 |  | textbox | Earth Loop Impedance
text | 402c6a8e-b50b-5698-a81d-34d25cef661e |  | textbox | Name
label | fc46b986-9929-51cc-aa75-3dd4aba5180a |  | note | Signature added below
checkpoint-group |  |  | section | Test No.3
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 87da01d2-8221-502b-becb-9ad4243169f6 |  | textbox | Cable No
text | 5f813b77-1135-5540-866f-150d7599b2e2 |  | textbox | Cable Origin
text | c2a8944b-86b9-54e4-bb38-f2452af67d3e |  | textbox | Cable Destination
text | 34e0afd7-cdbf-568a-ba94-2badb9efaa86 |  | textbox | Upstream Circuit Breaker Size
select | 083e3ffa-a684-5d6d-8d2d-5058f0b13f8d |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 1dca478a-b180-5407-9222-a092416ff323 |  | button | Fire Rated | Yes, No
text | 1dd04e18-4f9a-57da-a2ca-86ce090e820c |  | textbox | Cable Size (mm²)
text | a1d56932-247c-5a54-bfdf-1fc52bda2649 |  | textbox | Earth Conduit Size (mm²)
text | c270c306-e127-5615-ba33-4021a0a615ea |  | textbox | Earth Conduit Size (mm²)
select | 050d628c-b498-5182-8385-45e475b92de9 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 02e93ba9-550e-5c27-b82f-54b2ea921c9d |  | textbox | Other (Specify here)
button | a77a60aa-d84c-5257-963e-3a32ed37fd00 |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | 88a8497a-9671-55c5-b739-df235b9ce0b6 |  | dropdown | Cable Spacing | Trefoil, Flat
text | 637c826b-0f9d-5fd0-9626-ace2844594f4 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | d44dcd90-9c0c-5cdc-9478-f3535f07330c |  | textbox | Red / White
text | 8dc94102-8496-531f-8642-4f03f817aef4 |  | textbox | Red / Blue
text | e5f90528-f018-599a-9acb-6425bca9226e |  | textbox | Red / Earth
text | 27bce003-c5cc-5d48-82f0-67c81274cc0a |  | textbox | Blue / White
text | bffdeac7-1697-568c-87ea-2701bd49f3d9 |  | textbox | Blue / Earth
text | 18bd5c75-fbbc-5433-98a3-f2788dd45bb3 |  | textbox | White / Earth
text | 647f0499-2069-5c9f-a133-fc4e84fe347f |  | textbox | White / Neutral
text | bd1a9f9b-cc9a-5786-86a8-6a7ca336799a |  | textbox | Red / Neutral
text | 9789ed76-82b6-5183-ac2f-19cf924f2d60 |  | textbox | Blue / Neutral
text | 21fd1b6d-45fe-587d-b6eb-674f1377d03f |  | textbox | Neutral / Earth (MEN Disconnected)
text | 25d3a90a-bf1e-5d64-9160-d1705a0e192c |  | textbox | Earth Loop Impedance
text | 3041f52d-79fb-5ef9-8928-5710e41f5dff |  | textbox | Name
label | ab838b04-b2df-59b3-923e-027ebb1a3c34 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.4
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 468a6180-c0b3-5425-9c4b-dd7b7cda500b |  | textbox | Cable No
text | 2743e60d-33a1-545b-957f-9b75a226a2e5 |  | textbox | Cable Origin
text | 8d4d3131-33fd-56c1-bbff-87c9b917c426 |  | textbox | Cable Destination
text | a7c6fb8d-763b-5234-a322-563b0e688d70 |  | textbox | Upstream Circuit Breaker Size
select | ccd9a706-539f-518c-9264-b12fe074506d |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 0307f2e0-5e18-5107-a08d-a052a7ac7188 |  | button | Fire Rated | Yes, No
text | 22b9dd1f-61ed-5d83-93f3-079bcfe84128 |  | textbox | Cable Size (mm²)
text | 8bc0134a-dbdb-5428-a646-bfccc4c89827 |  | textbox | Earth Conduit Size (mm²)
text | 6b326d20-957a-5d36-a6f8-cae979197652 |  | textbox | Earth Conduit Size (mm²)
select | b92361ad-3b09-5f88-9c0a-4d059f6684b0 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | ab6644a8-ce93-5262-95e3-14c14d2fef77 |  | textbox | Other (Specify here)
button | 9d0ccfb5-ddb7-522f-9a4e-2c4c6614cbb9 |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | 1fda6c62-aefc-53f1-92ac-1c7e68a9d767 |  | dropdown | Cable Spacing | Trefoil, Flat
text | 7335e3a3-2306-5aca-85f2-f2b347f90a60 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | 4b3c49ac-5850-556c-ac95-38c3345784d5 |  | textbox | Red / White
text | 3f06dcb8-ffc7-5d55-8b27-496c92f0af80 |  | textbox | Red / Blue
text | 279641b8-fbf2-5f1c-9f03-01de8a40e204 |  | textbox | Red / Earth
text | 7e07ba38-8490-5ea8-a899-b10bc0b38af7 |  | textbox | Blue / White
text | dfad191f-8717-5d8b-9da9-263a9b888f8c |  | textbox | Blue / Earth
text | f0cf98bf-8de8-5fb0-a425-98391d825f5c |  | textbox | White / Earth
text | 6b101fa9-db65-57b7-8c03-f4d41e1ab205 |  | textbox | White / Neutral
text | 543f262c-17f7-5cb9-bf6e-dbeeff870813 |  | textbox | Red / Neutral
text | c03c4ff8-970f-5703-b534-ed7053196ceb |  | textbox | Blue / Neutral
text | aca8db1b-e55b-5289-921f-4872cf13341b |  | textbox | Neutral / Earth (MEN Disconnected)
text | 973e7a25-4e1a-5f31-bb7e-488c592f49bd |  | textbox | Earth Loop Impedance
text | e2184cb8-5b67-5f2f-b039-39c13f2d06eb |  | textbox | Name
label | 18f623c5-7ec8-5ac9-b8cf-ef81cad34343 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.5
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 72c17ef4-ccb7-5ca4-8d33-a5a3f1fc5737 |  | textbox | Cable No
text | b17d0077-a6cf-539e-a9b1-3936adf3bf4f |  | textbox | Cable Origin
text | bc69cee1-36c4-59bd-9ffb-c77f34f97eb3 |  | textbox | Cable Destination
text | 7a6c1793-c9fc-5f48-82c1-0bba60321a0b |  | textbox | Upstream Circuit Breaker Size
select | 357cf3b7-d939-5113-84f5-45a684ee130d |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 522de937-93a1-56fb-9793-479b69e6cabc |  | button | Fire Rated | Yes, No
text | 537ab00c-d80b-5a52-9a84-97fe2450ddd3 |  | textbox | Cable Size (mm²)
text | dbf19db7-4286-564d-b524-6fa1dd211f8d |  | textbox | Earth Conduit Size (mm²)
text | 6ccca8f5-a988-58d4-8c60-6cb078d244d9 |  | textbox | Earth Conduit Size (mm²)
select | 5bfbd726-45dc-57a1-8a66-f97b99740a02 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 3aeb5687-c564-5b83-abc4-41e4c1c42f9c |  | textbox | Other (Specify here)
button | cd1eb237-b4ac-5767-9c73-c24b3a55d8ab |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | 6d1d8124-eb00-5930-8b1a-1f2a2efc04f8 |  | dropdown | Cable Spacing | Trefoil, Flat
text | e4792260-27d8-5216-be6e-dda080d7cd60 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | 6b3c4931-9c28-56fb-ad46-4c5a17eed02d |  | textbox | Red / White
text | 10be134c-72e5-5421-8df7-5e6987f55217 |  | textbox | Red / Blue
text | e6f0117c-36d2-55ac-b760-6003a97437a4 |  | textbox | Red / Earth
text | 4eafbdf8-e476-5ea3-beed-3f89dc2dfee7 |  | textbox | Blue / White
text | 0c75f59e-270f-5ab0-b7c9-958387498bd2 |  | textbox | Blue / Earth
text | 35891e66-5e0e-59ad-8cda-bc8d4609d036 |  | textbox | White / Earth
text | 4af8347b-2bd5-559c-b9e0-26f53f9e2524 |  | textbox | White / Neutral
text | a5852b9a-b640-5ddb-bdd5-0ac51b502aa0 |  | textbox | Red / Neutral
text | f6b23d6f-e0f0-54d0-b7b8-73726fd596c8 |  | textbox | Blue / Neutral
text | e564c88d-b002-59d7-8909-4cec6b77f4db |  | textbox | Neutral / Earth (MEN Disconnected)
text | dfd20613-c074-52d7-b68f-3ba8e3833509 |  | textbox | Earth Loop Impedance
text | b8c13505-324b-5af4-8b9d-20fd2b62a1ce |  | textbox | Name
label | 3f893481-c9fa-546a-95c0-29338d66d43d |  | note | Signature added below
checkpoint-group |  |  | section | Test No.6
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | ae45767a-7b20-5d82-a393-f78d57aec82f |  | textbox | Cable No
text | fe43c142-e45d-5380-986a-c55fbbbd6ca2 |  | textbox | Cable Origin
text | 235706be-36e3-5d27-80b5-5d717a91ce1b |  | textbox | Cable Destination
text | 8264869d-b22f-585f-97e6-c0cf7614a95f |  | textbox | Upstream Circuit Breaker Size
select | fa3d3f79-a7ff-532a-8a99-841ab814bb94 |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | cb24f0dd-9929-578a-84e7-07a1e713f182 |  | button | Fire Rated | Yes, No
text | d6e18a82-8267-519e-9b54-b680fa88e609 |  | textbox | Cable Size (mm²)
text | c75f0103-e449-5c96-aad8-6b1ffe8f231b |  | textbox | Earth Conduit Size (mm²)
text | 5f918cd8-1126-53a9-b1d2-68d9cc921a08 |  | textbox | Earth Conduit Size (mm²)
select | 30e7109e-251a-55f9-93d3-af683ca020d6 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 9da90b5d-0c9a-50cb-bfdd-30644c9778ed |  | textbox | Other (Specify here)
button | 256098cf-b95e-5118-adbb-fb2d072a9a0b |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | a0ab71ff-a528-5d5b-bf4c-22a4b083b1d1 |  | dropdown | Cable Spacing | Trefoil, Flat
text | 674aba70-26e1-5398-9162-5645e308f157 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | 05181046-18a9-5cdb-8158-c7ee28c431af |  | textbox | Red / White
text | 494568df-1efb-5b64-9825-dcd42e3d4f8f |  | textbox | Red / Blue
text | 4b492ba8-83d9-59c8-80bb-d7fdddd2ccf6 |  | textbox | Red / Earth
text | aa64e8f4-c398-5311-98de-0bed101cd39d |  | textbox | Blue / White
text | 6bd4b793-ef5f-58c7-a8bd-45e11d87f2d7 |  | textbox | Blue / Earth
text | 5626898d-0097-5a2f-9c1c-9f2e3ed84339 |  | textbox | White / Earth
text | 1328938f-7a5e-54ef-abe8-055dfdfba670 |  | textbox | White / Neutral
text | 8e5e62b2-8c76-5026-9496-8bc5a6bbfabc |  | textbox | Red / Neutral
text | 5fce86c7-0a9e-5273-b848-cabd603d61d8 |  | textbox | Blue / Neutral
text | fc283402-0518-560a-bf28-0872948d1032 |  | textbox | Neutral / Earth (MEN Disconnected)
text | 9d28fc31-9ffa-5d37-9d0f-cde1a82e64b3 |  | textbox | Earth Loop Impedance
text | 52f797c9-6321-5c71-9d25-e2bf1a657ee0 |  | textbox | Name
label | 75d7e967-caf6-5bcf-8e51-1bc8413c35ce |  | note | Signature added below
checkpoint-group |  |  | section | Test No.7
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 6bf65af4-6842-54f1-9095-423faf803f32 |  | textbox | Cable No
text | f53f851a-afca-59a6-9981-d50e61977ef1 |  | textbox | Cable Origin
text | de3c1533-ccdd-5769-a264-885bef33667a |  | textbox | Cable Destination
text | 776ab786-8ea6-5ba9-b7e3-e6334808cde9 |  | textbox | Upstream Circuit Breaker Size
select | 563fd177-e5f7-5102-ae56-0c9596e0cad8 |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 97771b78-4725-52c0-88af-3e2f822e91a0 |  | button | Fire Rated | Yes, No
text | 46d2c15c-0d40-5387-b332-b93d35807fd2 |  | textbox | Cable Size (mm²)
text | 0abb7e47-eb17-5fed-a226-ab222cb03a41 |  | textbox | Earth Conduit Size (mm²)
text | e4d7ba27-0615-50eb-a27a-9d4226fa6b31 |  | textbox | Earth Conduit Size (mm²)
select | 5cb5e90c-20a3-54f4-830c-db0c53f88540 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 659f6b80-e2af-51bd-b94a-1b1cdf33ca26 |  | textbox | Other (Specify here)
button | 532e3b86-e64d-533e-ae4e-acd92b8d3f3d |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | 20d7ccb9-b9e4-5189-91c6-37615bd39afd |  | dropdown | Cable Spacing | Trefoil, Flat
text | c82708e5-3570-5aa3-b0ec-5d31f0f16c86 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | a20a9a52-0817-51d1-9c5b-ed6add559d4a |  | textbox | Red / White
text | a8ca0722-b5ac-5c2d-99d4-d033a77f1182 |  | textbox | Red / Blue
text | 6aa8f3ce-e5ef-5777-b619-832a645da27e |  | textbox | Red / Earth
text | 567687cb-6250-5742-b00b-5bc144719cf9 |  | textbox | Blue / White
text | 282f83a5-a0d5-5d71-8615-5d544ffd9eaa |  | textbox | Blue / Earth
text | 46e8eafe-ddc8-550d-ac57-c5d773ed21c1 |  | textbox | White / Earth
text | b588dafb-03ae-53e2-8280-7bd6e393ea21 |  | textbox | White / Neutral
text | 10eeb616-7625-5642-9942-43c96f713b64 |  | textbox | Red / Neutral
text | c480e360-bf53-534c-ad25-e65f0deebab8 |  | textbox | Blue / Neutral
text | 9f2b8a72-2baa-59d0-bf59-11f597106b4d |  | textbox | Neutral / Earth (MEN Disconnected)
text | f97de7dd-2b8b-5ba0-a2c3-d1db441dc37c |  | textbox | Earth Loop Impedance
text | 863fff34-8e9d-5e48-9373-82cc5baabf59 |  | textbox | Name
label | ea9be0d7-df19-5440-9a4b-a2b5415f7c21 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.8
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 610fb846-8102-538e-9aab-965883f8dee6 |  | textbox | Cable No
text | d87ebd11-062f-54ad-a844-b654864f13ed |  | textbox | Cable Origin
text | 944176b1-9125-51e5-8a21-3bdfcbea18f3 |  | textbox | Cable Destination
text | 3d805d23-dd7a-55bd-bb50-414f4f9e60ba |  | textbox | Upstream Circuit Breaker Size
select | bdde5410-c457-5a5a-ad88-8e083d94ec2f |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 60d803ae-f185-5e2d-9c21-19eb512beff3 |  | button | Fire Rated | Yes, No
text | 5e44e36c-dfde-5883-b7c1-c30b438b5515 |  | textbox | Cable Size (mm²)
text | 495a2f55-aad2-50e9-abac-b8427ac50249 |  | textbox | Earth Conduit Size (mm²)
text | bae0cc58-7566-51d4-ad88-b7e2c9d3b82a |  | textbox | Earth Conduit Size (mm²)
select | 551ab6c8-7f06-52f9-b70d-c83d2d82e9a6 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | a7c65303-1502-552e-b0a0-cc61eb5becc9 |  | textbox | Other (Specify here)
button | 7e8acb40-053e-5f3b-a0f0-48e10fbac065 |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | dc8cd83c-b3fb-55f1-aed2-0f7bd11b551d |  | dropdown | Cable Spacing | Trefoil, Flat
text | e42b7707-2ea8-50ab-a7da-1085be9ba6e5 |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | 6434df0f-28c1-5873-9dd4-b284fdcc747e |  | textbox | Red / White
text | 6a17ab14-2acb-5aca-a37a-7b3cddd5ac0f |  | textbox | Red / Blue
text | 0905a2f2-a96b-54c3-ae3d-0c33a6eab44c |  | textbox | Red / Earth
text | d00030b3-6f3d-5c71-aff9-9c337aafc6bf |  | textbox | Blue / White
text | 94520cc2-d2cf-52ac-b0c8-d38a2cb579fe |  | textbox | Blue / Earth
text | 17843967-7652-5162-afdc-e393ebc33cd8 |  | textbox | White / Earth
text | e9a3f33e-565d-5339-b681-2696ee025bc6 |  | textbox | White / Neutral
text | 3fc9d7cb-ff63-5391-8eef-0e6518b68e55 |  | textbox | Red / Neutral
text | d4e8863d-17bc-5efa-8620-9cbbce228997 |  | textbox | Blue / Neutral
text | c3a96cea-2a85-5a69-a48e-a5ca51625aec |  | textbox | Neutral / Earth (MEN Disconnected)
text | c8553474-b58e-52b9-943a-23f3b4f10ea3 |  | textbox | Earth Loop Impedance
text | b50dc1e2-22a5-5b76-b4df-40650802f2aa |  | textbox | Name
label | 47467dce-ec40-5ffa-b4d3-5be1fc79de47 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.9
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 9d16d361-5864-54a0-a0dd-cbfb700210cf |  | textbox | Cable No
text | 16d436e4-537f-5421-bdf4-c1765c073e22 |  | textbox | Cable Origin
text | a6400e8f-6432-59e0-ab6b-5ad3a0a709df |  | textbox | Cable Destination
text | 593f0f05-9436-569b-bc10-3a0e6c7298ed |  | textbox | Upstream Circuit Breaker Size
select | 46ba44a1-5ec2-5db6-9060-ea4b7c771663 |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | f249e1d2-d37f-5323-80e1-415e13dccfc2 |  | button | Fire Rated | Yes, No
text | c054cee1-9b5b-58e4-a150-beb566f11c7e |  | textbox | Cable Size (mm²)
text | 785b00b0-5a75-5b43-8983-9c6f243c601c |  | textbox | Earth Conduit Size (mm²)
text | e4766dde-701a-5870-a528-d283aacb988d |  | textbox | Earth Conduit Size (mm²)
select | df10a936-d97a-5664-b8d9-886f93d70a30 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | 0be2fc80-02cd-52bc-8f06-5fb88c64ca43 |  | textbox | Other (Specify here)
button | fa9ea6b1-5346-5fd5-8b2c-e6965be19f74 |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | bd2ce0b3-1fe8-53e5-9ca9-d373fdfb2ffd |  | dropdown | Cable Spacing | Trefoil, Flat
text | d6c70c36-38f9-5151-bcc0-773f4913ea6b |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | ad4547e8-de9d-59d0-8aeb-40c877c1fc2b |  | textbox | Red / White
text | 364b2a9f-e7ab-5374-af1d-9791500db0a4 |  | textbox | Red / Blue
text | d13583bf-19e0-58df-94f6-95ed3726cfb6 |  | textbox | Red / Earth
text | 6f279d0c-cd97-5f8d-87d6-bb0cbf6bbd7c |  | textbox | Blue / White
text | 352495e8-8a46-5e27-8e8a-36bef4e691ff |  | textbox | Blue / Earth
text | f25ad2ec-635e-502e-956a-97f21e2831e6 |  | textbox | White / Earth
text | 14243ac2-2434-5a85-92c6-39db40473110 |  | textbox | White / Neutral
text | be08cabb-388e-50fd-99d7-88e1c9c59e3a |  | textbox | Red / Neutral
text | d3fcecfd-892c-5858-8209-d331edfc905f |  | textbox | Blue / Neutral
text | a19bcce2-de20-5d40-97f5-b031bc7b9caa |  | textbox | Neutral / Earth (MEN Disconnected)
text | 3f5795d5-a1b6-5744-a2fd-758ea0ee7240 |  | textbox | Earth Loop Impedance
text | 8a9d3d2e-9d72-530d-805e-6e6535b03f65 |  | textbox | Name
label | fdab32a6-40f7-5e75-ab93-5549f7bf6ee4 |  | note | Signature added below
checkpoint-group |  |  | section | Test No.10
checkpoint-status |  |  | checkpoint | Pass Once below details are completed
text | 3ad3925a-b39f-5ad0-b3f1-c1254736a905 |  | textbox | Cable No
text | 4d3b0c03-4775-5f71-9e01-aec91ec19cac |  | textbox | Cable Origin
text | d05b628e-8681-5e00-9648-a65e04694cbe |  | textbox | Cable Destination
text | d7836741-0d7f-5f07-b07e-b064266dd9dd |  | textbox | Upstream Circuit Breaker Size
select | 1426432b-396e-5f3d-944e-704a18089a39 |  | dropdown | Type of Cable | X = XLPE, O = Orange Circ, M = MIMS
button | 91b9f83f-db3b-5f20-a348-20d49e7eedf6 |  | button | Fire Rated | Yes, No
text | 2d6b4cba-de03-5f39-addd-5c797a62035a |  | textbox | Cable Size (mm²)
text | 2f5e6e6a-f297-553c-b064-f59cdb3cc653 |  | textbox | Earth Conduit Size (mm²)
text | f9e8a5ad-4d3a-5ec8-8044-995106c33045 |  | textbox | Earth Conduit Size (mm²)
select | 96c657c6-196f-5cf8-aea9-f01751d41f05 |  | dropdown | Support Method | Tray, Catenary, Duct, Other (Specify Below)
text | a8c9024d-5462-5fdf-be7a-b11c48517c8d |  | textbox | Other (Specify here)
button | 5c10a3ee-5226-5b6c-9d7b-9e802a251dce |  | button | Line & Load Side Termination Checked & torque (AF128-2) | Yes, No
select | 417bd4a8-02f2-50c0-baa5-890ffbccbf5e |  | dropdown | Cable Spacing | Trefoil, Flat
text | e597e7b5-7eb8-5099-9b72-59ec8ce67a0c |  | textbox | Cable Earth Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance - Pass Once below details are completed
text | ca6522df-a884-5847-8e69-c62952058d7c |  | textbox | Red / White
text | ac240649-9561-5b4f-928d-07737f2a893e |  | textbox | Red / Blue
text | 309f6a1b-09b3-54ef-aec8-90d0ecaf7457 |  | textbox | Red / Earth
text | b1296b15-64c9-538c-8a4b-97920bf2f80b |  | textbox | Blue / White
text | 2528255c-97dd-59c2-bd7d-bc19f814411c |  | textbox | Blue / Earth
text | 4076115c-18d3-52af-a945-de20b6dc5c56 |  | textbox | White / Earth
text | 5b391c33-1973-5a11-9929-145b786bedee |  | textbox | White / Neutral
text | 8b8377b5-a14f-5d4d-968f-70624027b501 |  | textbox | Red / Neutral
text | e89cede7-9c19-5bf9-b969-83abda599206 |  | textbox | Blue / Neutral
text | 80a14a01-7fe8-54b2-9bcb-b83f66f2718d |  | textbox | Neutral / Earth (MEN Disconnected)
text | e671c9d3-9725-57bb-8a1c-ac4d1cfa6935 |  | textbox | Earth Loop Impedance
text | 01564b69-67e1-5e40-bd8b-a8151082386d |  | textbox | Name
label | 9fb3c577-a869-5aca-beac-a8c3d6275f34 |  | note | Signature added below
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Testing completed to specification/drawings - Area left clean & tidy
label | 3eb81112-d57d-564d-859f-fd04539ca5f5 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 9f0db275-d2e9-52e4-8b0e-b2b5b891bc1a |  | note | Any Corrective Actions to be Photographed & Commented below
select | ebb40d22-14d7-5376-8c61-038e2cce7fbb |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 3c8a8a90-1681-5777-b7f8-598fc8d5c535 |  | textbox | Other (Specify here)
select | fdc9e5da-339f-5c1d-897f-524d23709c5f |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 248896ca-a7c0-5870-aba2-aff37012f30a |  | textbox | Other (Specify here)
text | bc0d0156-e6f2-5733-a482-0e48bd31d717 |  | textbox | Witnessed by (Builder/QAM)
label | 5c31251c-cc53-54ae-9479-8c550845f3fb |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AE-ITCX-005 - Construction Wiring 6-Monthly Re-Test Results (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-005 - Construction Wiring 6-Monthly Re-Test Results (Rev 0 +Names) | 6276c7d3-c9e1-437e-8443-f8028ab49cb9
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 93cfdcf1-10e5-57ed-b83d-6f0a7e2d293b |  | textbox | Level
text | dc185d1f-3f93-52af-851c-a233f4182b5c |  | textbox | DB No.
text | e3dc14b8-9ee0-5250-9736-dd1bb7cf45dd |  | textbox | Drawing # & Revision (Or photograph below)
select | cc350eaa-3d26-50ec-a9b2-915001a7db15 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 9b5ab61a-bdd3-52ec-a644-3e57522aa967 |  | textbox | Other (Specify here)
boolean | bcf074ec-6fc9-5877-a7a8-c1b29b7b7ae6 |  | tickbox | Signature added below
label | 65178869-a52c-50ed-b3e9-3b59069ff176 |  | note | .. ..
label | 4de64d70-f646-5e45-9b42-c50a2372017f |  | note | Test Equipment
text | 93bc1a75-9bd7-5553-baf2-255e0e0c28e1 |  | textbox | Tester Type
text | e8d90a15-db1f-5a01-bca5-c7426df9e99b |  | textbox | Serial No.
text | 0eb24fbd-1381-5044-be1d-33b144370faa |  | textbox | Calibration Certification Date
checkpoint-group |  |  | section | Test No.1
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | affa2bf6-50ea-5521-b5d0-7a4ce6b3e966 |  | textbox | Sub Main cable No.
text | 6d468dc9-308d-534a-80f5-58ca34b57c17 |  | textbox | Cable Size
text | 98a69ce7-4fe6-5b8a-888b-dafdbdaaae37 |  | textbox | Phase Qty
text | 75f76db5-7e41-51af-bc8a-88f88e7d6838 |  | textbox | Insulation Resistance - A+N/E
button | 5a9d89ec-acac-5f38-a419-56ae60f1123b |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 38696c71-f31f-5f94-973c-a13e0ed801b2 |  | note | .. ..
text | 0429d477-7e8a-5e49-ab75-b796d3ec3aac |  | textbox | Earth Continuity
button | cc2f7e7f-c539-58ce-bca3-6c905bd7ec37 |  | button | Result | Pass, Fail
label | fd718d2f-a4c3-5dc9-9994-e2b851f5431d |  | note | .. ..
text | 26fb2f81-e16d-599c-a467-03e1cb5ed7c5 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | c37019f9-bb67-59f8-a963-4d2a0f1b5314 |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.2
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | e806aa9d-4bef-52d7-b94b-65add372d849 |  | textbox | Sub Main cable No.
text | 8354e300-f756-5436-85ee-a9a2a99b67a4 |  | textbox | Cable Size
text | 625689b6-187a-5740-9ad8-0c7c08d7c317 |  | textbox | Phase Qty
text | 4cdab134-0b90-581a-9dcf-22fb2e99f0c4 |  | textbox | Insulation Resistance - A+N/E
button | 614d0484-a960-53b8-bfcc-19a7cb653fc8 |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 438d0816-bc2e-52dc-aea6-0b30427c82c6 |  | note | .. ..
text | 70e7f6b6-fb08-5eea-a099-d31397513cbd |  | textbox | Earth Continuity
button | 9b2a6141-51d0-5e06-8490-faef834b2965 |  | button | Result | Pass, Fail
label | df69568f-bb49-5678-9770-7b050724e513 |  | note | .. ..
text | 91d32ca1-e9df-5634-aec5-eefe57be8168 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 3a41addb-b426-5f70-bbb8-d20723899890 |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.3
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | 589b1595-513b-5537-84ee-4999e3724045 |  | textbox | Sub Main cable No.
text | 045651de-7b86-534d-90e6-21fd6e68c55a |  | textbox | Cable Size
text | 4546482d-105a-56b6-ad15-ddddcbb2f9ab |  | textbox | Phase Qty
text | d62556a3-5f55-55ec-81c8-db74a5623ffd |  | textbox | Insulation Resistance - A+N/E
button | e91be7fb-e7eb-5bfc-be60-d909b3c77ce8 |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 99157533-61fa-5b91-9e19-bcff5ffaa26d |  | note | .. ..
text | 63f81dd3-7e38-526c-9bfd-fdf5cafd9ec9 |  | textbox | Earth Continuity
button | cce4127a-076e-5420-ad96-5815601b4b48 |  | button | Result | Pass, Fail
label | f1556029-13b8-593e-a23e-8624b288eef3 |  | note | .. ..
text | beb0e7c9-c3d0-588e-ba0d-a5022ce416c1 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 237908e1-c7bc-57b5-b543-74e3996ac06b |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.4
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | a8debbe6-a5e7-513d-a4c0-778f782039b9 |  | textbox | Sub Main cable No.
text | 8d7c8aef-f1dd-5682-bd6a-fc684f73f398 |  | textbox | Cable Size
text | 0dd98ba4-388f-5fb1-8a0b-dc88d7fa188e |  | textbox | Phase Qty
text | 9be29784-01e1-5b82-b258-e9c1a26d7d9b |  | textbox | Insulation Resistance - A+N/E
button | 0aaad6e6-5429-5eb5-ae68-0a7423a61af5 |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | ff3f27e0-b371-5917-9dc9-676f907afd3f |  | note | .. ..
text | 4fff1724-e7c7-5f25-87e5-01a0a6efa968 |  | textbox | Earth Continuity
button | c7ce2b44-0529-5cab-a134-8e07593ee605 |  | button | Result | Pass, Fail
label | ad7701c5-5ff8-50ba-9c8f-8ae1e4e24310 |  | note | .. ..
text | 485f935f-306f-51a3-a0e1-060ac01bdcc9 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 07348693-e6dc-5e13-8955-d770e72d6252 |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.5
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | a04cf596-906a-5aca-8b45-381cb6005edf |  | textbox | Sub Main cable No.
text | 23f4dcd6-baa1-5e31-983e-6d577084f51d |  | textbox | Cable Size
text | 5a825f37-33fd-52e1-b18a-bf18ff46a80e |  | textbox | Phase Qty
text | 0a046dad-828f-529f-81e7-a80f5ed74dce |  | textbox | Insulation Resistance - A+N/E
button | 9222e4fb-ae85-57dd-b51b-66f367b3ee4e |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | ecdee21b-00aa-5d39-b6ec-57e01e94492a |  | note | .. ..
text | 2afd0ff4-967c-5296-89f5-ca83bc8fcf7e |  | textbox | Earth Continuity
button | 98c3c8d3-6566-56fc-8d47-9a279e9ec3fa |  | button | Result | Pass, Fail
label | 4f8af3be-c48b-53fe-bae9-a78f8322baeb |  | note | .. ..
text | aa5dd065-46ec-57f7-bb6f-ee0a616c08a4 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 9cb434e5-1099-568c-adbe-e4cd3f31738b |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.6
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | 18a59298-99ab-5f94-baf6-378db9e759a4 |  | textbox | Sub Main cable No.
text | 2f145e1c-e972-5e5f-a524-bfd2b5bdce6c |  | textbox | Cable Size
text | f3b24262-1437-534d-9350-cf12cd9862fd |  | textbox | Phase Qty
text | 11014f25-4a27-559d-9fd9-e7fbfdef4194 |  | textbox | Insulation Resistance - A+N/E
button | 03ed4c22-374a-5138-b14a-44960e8a6828 |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 54340c16-d445-5fcf-afc3-1559430dc3d5 |  | note | .. ..
text | f828b0ed-f9ae-5eb3-9df9-55e5cdab6c86 |  | textbox | Earth Continuity
button | c1747fa9-ad7b-5f11-8f3f-80b0cddcc252 |  | button | Result | Pass, Fail
label | 06d97f4c-2aaf-5bc1-ba0d-759d0b182dd5 |  | note | .. ..
text | 8baec752-b88c-50ab-921c-14092e802e55 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 1b606a24-6a8a-5ea2-a847-4bbeccd47391 |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.7
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | a41ac1d5-e7a9-5783-9ea8-98ac5caa0247 |  | textbox | Sub Main cable No.
text | 29203728-f7c4-5298-9630-6a1a1c1f6bcc |  | textbox | Cable Size
text | a5981367-7470-5db2-89ed-b48b47c704bd |  | textbox | Phase Qty
text | 87e7fb8e-49fa-57e2-b24c-2733c2a5e26d |  | textbox | Insulation Resistance - A+N/E
button | f289d3a2-7b31-5ac8-a02c-afbd396e1ece |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 8f5cd570-c6e9-523e-994c-26d70c5616ff |  | note | .. ..
text | ca2c82dd-d7f4-5b24-b3d5-ecdf1f55195f |  | textbox | Earth Continuity
button | 6242192e-c71c-51f7-888b-fb7f6cc23ea4 |  | button | Result | Pass, Fail
label | be625787-237d-5a2f-a73b-54aac8f67ce6 |  | note | .. ..
text | 655eba4c-b45b-599a-81be-46308a5e342c |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 3ddb7ced-f666-5fb0-bf52-618d72c5477b |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.8
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | f25fb408-ca18-535b-bf5c-d9c502a79f0a |  | textbox | Sub Main cable No.
text | 95d448ff-018e-5ca8-8e16-59554a7dfdbc |  | textbox | Cable Size
text | 6d2c0bff-c335-51a3-93ac-bb17639b18c7 |  | textbox | Phase Qty
text | 0035f203-e9f1-5224-83e2-083325ed2e8d |  | textbox | Insulation Resistance - A+N/E
button | c0b8474a-609b-52b8-9c28-f9b0dd81e8db |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 092c9234-25c9-539f-a1c3-795aa021abc5 |  | note | .. ..
text | 5e95694d-955e-5751-98c1-bd2d79853a1a |  | textbox | Earth Continuity
button | cc4d55dc-911e-5f86-95b7-e0af877c3f01 |  | button | Result | Pass, Fail
label | 889f2c27-b892-58b2-aba8-67eff9407a2b |  | note | .. ..
text | 459089ee-850d-56ec-b1f7-2d938d24ea31 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 2f21f320-ee28-5795-8bf2-2d744f58f87d |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.9
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | 752d2dfb-5b95-5a6e-bb03-72ff3f9dde85 |  | textbox | Sub Main cable No.
text | 5557d9e4-22b9-57ce-8940-982e54cbf1f2 |  | textbox | Cable Size
text | 8fd3882e-35ff-528f-9250-fcfdb12d1f4b |  | textbox | Phase Qty
text | 4e047773-48ac-526a-9ae7-dbc68408f47f |  | textbox | Insulation Resistance - A+N/E
button | 4293e050-f2df-5457-bd01-8da339633ea3 |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 4d078242-48ad-5b49-b3ec-23227f3800e0 |  | note | .. ..
text | cebefc3a-1f15-5b85-ad1a-8c12ebc154a0 |  | textbox | Earth Continuity
button | 0383e0e5-138b-5477-9eba-9688a3683b93 |  | button | Result | Pass, Fail
label | e12c1d10-3423-5ff3-9065-034ba7440c79 |  | note | .. ..
text | 51d95b76-1249-5851-922e-68bbe1c09e69 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | a0da0644-aa0e-5bdb-b2b7-ca92d1bd460a |  | button | Result | Pass, Fail
checkpoint-group |  |  | section | Test No.10
checkpoint-status |  |  | checkpoint | Test Details - Pass once entered
text | 45780107-a6be-5b6d-aa98-5802630f5ff2 |  | textbox | Sub Main cable No.
text | c44ba942-cb6d-5397-a6f1-3d26ecec6975 |  | textbox | Cable Size
text | 504448e9-8bb4-5f49-a279-61146b858aa2 |  | textbox | Phase Qty
text | 2bade566-15f8-5a21-9179-e203468851ed |  | textbox | Insulation Resistance - A+N/E
button | dac31dc0-0083-560d-a9d7-c312ce2c9533 |  | button | Pass/Fail (>1MOhm) | Pass, Fail
label | 8c4103e0-02da-50bc-95e9-1de3b44f57ec |  | note | .. ..
text | 5052b17a-ab10-5f19-af38-de6939642d0b |  | textbox | Earth Continuity
button | 489a4ef1-1ce4-5319-8ad5-fa5eb6c1a507 |  | button | Result | Pass, Fail
label | db4a8637-a4af-5d1e-af91-485f78bee7f6 |  | note | .. ..
text | 171b2a2c-6756-58ed-84d9-f5e5ffbc74c7 |  | textbox | Earth Loop Impedance (to furthest point) Result
button | 64a2674b-c3bc-510d-8c36-fc48a089ab57 |  | button | Result | Pass, Fail
checklist-flat |  |  | checklist | AE-ITCX-029 - Rough-In Checklist (Rev 1 +Names) |  |  |  |  | Yes | AE-ITCX-029 - Rough-In Checklist (Rev 1 +Names) | 66b0e7e7-302a-49f1-9b53-8c216e83a46f
checkpoint-status |  |  | checkpoint | Power
button | d16c64e5-5824-5135-93be-81fcdaf76790 |  | button | Power circuits roughed in to the documented location and cable sizes in the field/riser/DB and labelled correctly? | Yes,No
button | 4dc637f9-085b-56bc-90ee-463f8798c663 |  | button | Outlets within joinery/feature ceilings and walls have been coordinated so cables can be found later. | Yes,No
button | 942e90f8-7f37-5c08-a855-595ec50431e6 |  | button | Has steel framework been earthed appropriately? | Yes,No
label | 4b1a3126-0698-54dd-a0cb-8bc3ddde3035 |  | note | *Mandatory Image -Marked Drawing Including Title Block Revision
checkpoint-status |  |  | checkpoint | Lighting
button | d429539c-e7d8-50f3-8f9e-760ce6942931 |  | button | All cabling installed to the documented location in the field/riser/DB location and labelled correctly, including 2 way/int switching, smoke detector interlink & LED ELV cabling? Cables sizes have been checked, External Lighting and PE Cells | Yes,No
button | 36ff7e8c-b34e-50c9-8419-556b1a93ef4b |  | button | Plugbases/Quick connects fit off at rough in stage? | Yes,No
label | 4869938f-4de7-59b6-a043-dfa29d528c70 |  | note | *Mandatory Image -Marked Drawing Including Title Block Revision
button | 83d7ba8b-f92e-593d-b584-ed36660f0614 |  | button | Lighting control cabling installed to the documented location and zones and correct cable type used? Check cable is 240v rated or segregate? | Yes,No
button | 813d68b8-04bb-5f61-8be7-f1da97ce46f1 |  | button | Confirm the maximum allowable of 55 dali addresses has not been exceeded? | Yes,No
label | 5cb62bcc-957e-5a2e-8d69-c917c2d75097 |  | note | *Mandatory Image -Marked Drawing Including Title Block Revision add driver and puk locations is changed.
button | 3dc313aa-a159-50c5-be4e-55017900a67d |  | button | Timber noggins installed for large pendant lights? | Yes,No
label | 7e9c9a8e-002b-5f5b-97c3-d7dd57c945e3 |  | note | Optional - Additional Photos
checkpoint-status |  |  | checkpoint | MATV and Cat6/6A
button | bc9f54cc-72dd-5947-84c8-d837f2dd6eb1 |  | button | MATV cabling been installed to the documented location and labels reference shop drawing? | Yes,No
button | 17d754a7-a041-5868-85f0-1fdfea72fa14 |  | button | MATV Splitter is fit off in ceiling inlcuding 2.5mm earth roughed and labelled to Distribution Board | Yes,No
button | b61a6a36-ecbe-5ae6-a946-67bbfce0e338 |  | button | Cat6/6A cabling installed to the documented location, including correct cable type and labeled as per shop drawing? Cables are spaced 50mm or segregated from 240V rough in. (In some cases this may include Intercom and CCTV Cat6/6A cables also) | Yes,No
label | 0ca1cb68-6901-5174-92c6-2489768cb924 |  | note | Mandatory Photo - Accurate as wired drawings upon completion of fit off including variations, site changes?
label | e9539617-d11c-595b-8c09-e6ec2439ea41 |  | note | Optional - Additional Photos
checkpoint-status |  |  | checkpoint | UPS
button | ad42e742-ca47-598f-85d4-d8f652be454a |  | button | UPS circuits installed to the correct locations, and labelled correctly at the DB? | Yes,No
button | a2d0f1b2-31e1-539c-94de-5d52e72d61f6 |  | button | Mandatory Photo - Accurate as wired drawings upon completion of fit off? | Yes,No
label | f70df70f-9dbb-5857-824c-a9daed8b1d0f |  | note | Optional - Additional Photos
checkpoint-status |  |  | checkpoint | Rough In completed to specification/drawings - Area left clean & tidy
label | 1f7a409b-dfc5-50cf-b542-32df5d0f5e94 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 8910b6cf-e965-5523-b05a-0434229badf8 |  | note | Any Corrective Actions to be Photographed & Commented below
select | b73da6fb-a6f0-5f0f-a105-061798ee0b31 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622, ADAM STRONG - AGrade: A38815 - Employee#: 2002, ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794, ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684, ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863, ALAN BIRCHALL - Agrade: A18981 - Employee#: 379, ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111, ALI HASAN - Agrade: A48087 - Employee#: 1654, ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015, ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972, ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309, BEN DARBY - Agrade: A53332 - Employee#: 1702, BEN FINDLAY - Agrade: A41429 - Employee#: 2006, BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933, BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733, BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801, BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850, BRENTON HILL - Agrade: A47213 - Employee#: 1729, BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887, BROCK DOWNIE - Agrade: A53290 - Employee#: 1849, BROCK LLOYD - Agrade: A44808 - Employee#: 1680, CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193, DANIEL BENDINELLI - Agrade: A67728 - Employee# 2097, DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937, DAVID OLSEN - Agrade: A42915 - Employee#: 1685, DEAN NGUYEN - Agrade: A48514 - Employee#: 1515, DEREK JACOBS - Agrade: A67318 - Employee#: 2078, DWAYNE KLOET - Agrade: A48278 - Employee#: 1239, ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782, EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895, FERGUS COATES - Agrade: A59054 - Employee#: 1774, FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679, HUY DO - Agrade: A40954 - Employee#: 873, IMMANUEL KAWITI - Agrade: - Employee#: 2023, JACKSON SHARPE - Agrade: A53801 - Employee#: 1540, JAMES MARASCO - Agrade: A55184 - Employee#: 1758, JAMES PLEASANT - Agrade: A62956 - Employee#: 1976, JAMES SPOKES - Agrade: A48756 - Employee#: 1770, JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756, JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719, JASON PERL - Agrade: A36692 - Employee#: 1868, JASON SALE - Agrade: A28662 - Employee#: 1615, JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029, JESS ZAHRA - Agrade: A52969 - Employee#: 1403, JOEL BASSETT - Agrade: A39498 - Employee#: 1958, JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908, JOHN GREEN - Agrade: A55589 - Employee#: 1734, JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682, JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720, KALE BLACKLER - Agrade: A39293 - Employee#: 1751, KAYNE WALKER - Agrade: A38805 - Employee#: 1718, KEVIN MURPHY - Agrade: A63544 - Employee#: 2022, KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698, LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834, MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308, MARK D_ANGELO - Agrade: A40610 - Employee#: 1832, MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352, MATTHEW COX - Agrade: A42092 - Employee#: 1704, MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894, MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915, MICHAEL BRASHER - Agrade: A29237 - Employee#: 954, NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748, PAT DOUBLE - Agrade: A46604 - Employee#: 1118, PAUL HARMAN - Agrade: A26306 - Employee#: 1728, PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190, PETER LEWIS - Agrade: A53556 - Employee#: 1749, PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612, ROB POLLARD - Agrade: A56906 - Employee#: 1754, ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132, RYAN DEPRADA - Agrade: A41361 - Employee#: 1848, SCOTT RYAN - Agrade: A59062 - Employee#: 2017, SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034, SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771, SIMON COLLARD - Agrade: A32749 - Employee#: 883, STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829, TOM HAMILTON - Agrade: A48254 - Employee#: 1434, VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218, WILLIAM FISHER - Agrade: A20679 - Employee#: 859, Other (Specify below)
text | 27a4f26b-2d9a-5288-b576-e825fdd89cb5 |  | textbox | Other (Specify here)
label | 49d3488a-8615-558d-abd1-f25c61e7868a |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-032 - Electrical Commissioning Checklist (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-032 - Electrical Commissioning Checklist (Rev 0 +Names) | 69e6771e-f78f-446e-a43e-1220c92dc491
checkpoint-status |  |  | checkpoint | Documentation to proceed with commissioning
button | f59e3eef-9405-5311-a4a8-e3c72daa5443 |  | button | AE-FORM-006 - Builders Works Completion Notice, AE-FORM-011 - Notice of Intent to Energise Electrical Installation, AE-FORM-009 - Start card been filled out by all workers within the commissioning crew? | Yes,No
button | 11e23bc8-9abe-534e-9924-96cf8bc74155 |  | button | All Rough In and Fit Off and DB Fit Off QA has been closed out and As-Installed drawings are available to commissioning team confirming area is ready for commissioning to begin. | Yes,No
button | bcfd74b0-9dbb-5c44-b80c-46bdbdd61d4d |  | button | Have you checked if are there variations within zone/ area that may not be on shop drawings? (Check with Site Manager before continuing). Commissioning team to add to asbuilt immediately! | Yes,No
label | c7fc53c6-025e-5fbe-a4b6-35478dde3c15 |  | note | Commissioning Team have been provided copies of As-Builts, DB Schedules and AE-Form-038 to begin commissioning process.
checkpoint-status |  |  | checkpoint | General - Final Visual Checks in addition to AE-FORM-038
button | 09dd83cb-0310-56e7-8572-902d6c3e16fe |  | button | Outlets, switches and other equipment installed straight, level, in the correct location and mounting height? | Yes,No
button | 32e142ab-d9e1-58ac-8e0b-4478a01bd3d1 |  | button | Are any items left incomplete and made safe for energising (e.g missing splashback) If so please photo document here. | Yes,No
button | d4d7a5af-ef46-5f90-8879-5741370adae7 |  | button | If Yes add image of item made safe. | Yes,No
button | 7a9c6bf3-e505-5cb3-9ba7-720aea4b2ace |  | button | All switching devices are operating documented items? As per drawings documents. | Yes,No
button | c21dc8eb-5681-51cd-9752-6f8f55cb640e |  | button | Smoke Detector is tested, has back up power supply activated and is in permanent operation. | Yes,No
button | 12c2ba8d-e6cd-5414-935d-53453ef9c65d |  | button | Electric cooktop has a visible isolation switch in accordance with AS3000? | Yes,No
button | 660cc536-a157-523b-915d-676a616f3e04 |  | button | Exhaust fans function correctly? Where a fan is switched from multiple locations, double pole mechs are installed to prevent the “back feeding” of lights in the other spaces? | Yes,No
button | 858c1877-6d70-5936-b895-53055ec14768 |  | button | All outlets labelled correctly and all cover plates are installed. | Yes,No
button | 12142144-e8a6-5b01-a423-5e7f8fef2742 |  | button | All power is now available and Lighting Control System (if any) is ready for intergrator/specialist commissioning | Yes,No
button | 058f3a85-f9a9-5f5b-b269-c2b2538a3966 |  | button | Is the Exit and Emergency /circuits now powered and ready for Emergency discharge test and Commissioning to be performed. | Yes,No
button | 75a1067f-c438-5e63-aa67-4544125377f3 |  | button | All circuits locked/tagged out been entered into the AE-FORM-010 - Isolation Tag Register? | Yes,No
button | 343de46b-1c50-5a1f-bd76-e364f2ac0328 |  | button | Distribution Board is now energised and officially put into service. | Yes,No
label | 603b21d5-1dc6-573a-85a0-9e503e0d772a |  | note | Mandatory photo - Accurate as built drawings upon completion of commissioning including variations, site changes, driver and puk locations?
label | 7a0114d0-f648-5bf0-9960-b0fe4548c494 |  | note | Mandatory photo - Internal DB escutcheon off image documenting condition left at energisation.
label | df2373e8-7127-5587-9407-0afd562f0392 |  | note | Mandatory photo - Isolation tag register?
label | 4070ba3f-9252-5660-ac59-8a31a326fac3 |  | note | Mandatory photo - Commissioning Test Sheet FORM- 038 (obtained from Appselec way) including all test results.
label | 54dc960d-1a5b-5c60-b2d1-741c46a8a452 |  | note | Mandatory photo - Certificate of Electrical Safety (screenshot for electronic forms)
checkpoint-status |  |  | checkpoint | Electrical Commissioning completed to specification/drawings - Area left clean & tidy
label | 6057d42d-c384-545c-b7f9-5f3b9a903d76 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 1269485f-b827-52bc-8111-3a8a941dee2c |  | note | Any Corrective Actions to be Photographed & Commented below
select | 41944ab7-31c6-56d7-a2e2-33f88c7680ec |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622, ADAM STRONG - AGrade: A38815 - Employee#: 2002, ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794, ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684, ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863, ALAN BIRCHALL - Agrade: A18981 - Employee#: 379, ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111, ALI HASAN - Agrade: A48087 - Employee#: 1654, ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015, ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972, ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309, BEN DARBY - Agrade: A53332 - Employee#: 1702, BEN FINDLAY - Agrade: A41429 - Employee#: 2006, BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933, BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733, BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801, BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850, BRENTON HILL - Agrade: A47213 - Employee#: 1729, BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887, BROCK DOWNIE - Agrade: A53290 - Employee#: 1849, BROCK LLOYD - Agrade: A44808 - Employee#: 1680, CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193, DANIEL BENDINELLI - Agrade: A67728 - Employee# 2097, DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937, DAVID OLSEN - Agrade: A42915 - Employee#: 1685, DEAN NGUYEN - Agrade: A48514 - Employee#: 1515, DEREK JACOBS - Agrade: A67318 - Employee#: 2078, DWAYNE KLOET - Agrade: A48278 - Employee#: 1239, ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782, EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895, FERGUS COATES - Agrade: A59054 - Employee#: 1774, FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679, HUY DO - Agrade: A40954 - Employee#: 873, IMMANUEL KAWITI - Agrade: - Employee#: 2023, JACKSON SHARPE - Agrade: A53801 - Employee#: 1540, JAMES MARASCO - Agrade: A55184 - Employee#: 1758, JAMES PLEASANT - Agrade: A62956 - Employee#: 1976, JAMES SPOKES - Agrade: A48756 - Employee#: 1770, JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756, JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719, JASON PERL - Agrade: A36692 - Employee#: 1868, JASON SALE - Agrade: A28662 - Employee#: 1615, JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029, JESS ZAHRA - Agrade: A52969 - Employee#: 1403, JOEL BASSETT - Agrade: A39498 - Employee#: 1958, JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908, JOHN GREEN - Agrade: A55589 - Employee#: 1734, JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682, JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720, KALE BLACKLER - Agrade: A39293 - Employee#: 1751, KAYNE WALKER - Agrade: A38805 - Employee#: 1718, KEVIN MURPHY - Agrade: A63544 - Employee#: 2022, KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698, LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834, MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308, MARK D_ANGELO - Agrade: A40610 - Employee#: 1832, MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352, MATTHEW COX - Agrade: A42092 - Employee#: 1704, MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894, MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915, MICHAEL BRASHER - Agrade: A29237 - Employee#: 954, NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748, PAT DOUBLE - Agrade: A46604 - Employee#: 1118, PAUL HARMAN - Agrade: A26306 - Employee#: 1728, PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190, PETER LEWIS - Agrade: A53556 - Employee#: 1749, PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612, ROB POLLARD - Agrade: A56906 - Employee#: 1754, ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132, RYAN DEPRADA - Agrade: A41361 - Employee#: 1848, SCOTT RYAN - Agrade: A59062 - Employee#: 2017, SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034, SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771, SIMON COLLARD - Agrade: A32749 - Employee#: 883, STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829, TOM HAMILTON - Agrade: A48254 - Employee#: 1434, VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218, WILLIAM FISHER - Agrade: A20679 - Employee#: 859, Other (Specify below)
text | 3b8cfac2-bddf-513d-9a66-0c8043ccf5ce |  | textbox | Other (Specify here)
label | d475ccd4-cfe9-5377-b236-1d98d1bdd920 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-006 - Distribution Board Visual Inspection (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-006 - Distribution Board Visual Inspection (Rev 0 +Names) | 780f9e73-54de-4b24-81e6-c83c57948099
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 0dc7eb94-134a-5fdf-8738-df192b04541f |  | textbox | Switchboard No.
text | 3e46b827-92db-58b3-9c52-1b631fa0a8b2 |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | Appselec typed legend, schematic and labels all in place
checkpoint-status |  |  | checkpoint | Manufacturer's QA checklist provided - Attached as applicable
checkpoint-status |  |  | checkpoint | All connections tight with no copper visible out of terminals
checkpoint-status |  |  | checkpoint | Contactors labelled
checkpoint-status |  |  | checkpoint | Wiring neatly loomed (Internally and Externally)
checkpoint-status |  |  | checkpoint | Surge arrestors installed
checkpoint-status |  |  | checkpoint | Cable entries appropriately insulated and fire rated
checkpoint-status |  |  | checkpoint | Bottom entry cables have mechanical protection (if applicable)
checkpoint-status |  |  | checkpoint | Panel, escutcheon, cover plate, door, operable lock and pole fillers in place
checkpoint-status |  |  | checkpoint | Lighting control cabling and emergency cabling labelled
checkpoint-status |  |  | checkpoint | Emergency power sensing installed (if applicable)
checkpoint-status |  |  | checkpoint | Switchboard cupboard cleaned
checkpoint-status |  |  | checkpoint | Distribution Board Visual inspection completed to specification/drawings - Area left clean & tidy
label | 74fc345f-2587-56ac-97fa-1c7d225193d7 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | c607e37d-3f53-516d-a9fb-734c6125df78 |  | note | Any Corrective Actions to be Photographed & Commented below
select | fb678715-8b7e-5fe6-8012-12a862f7193e |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 33524e68-16d1-58de-a508-5fd6a2cebfe2 |  | textbox | Other (Specify here)
select | e039a56c-7fc4-5233-b52a-74fa958c02d4 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | b6eadc71-1b3b-55ca-a3df-a361d7d2a638 |  | textbox | Other (Specify here)
label | 40b53c1e-5439-5ef2-ac97-d2d5a2ae9b16 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-035 - Lead In Fit Off |  |  |  |  | Yes | AE-ITCX-035 - Lead In Fit Off | 7b204134-f681-44db-9347-999dda3d3882
checkpoint-status |  |  | checkpoint | Fit off Leadin cables
button | c6bb4620-9f1a-5750-8b8c-31dfa889d4c9 |  | button | Submain cables is terminated at field/Distribution Board End? | Yes,No
button | 00f7e3ab-0d03-54e2-b105-abe2ca6b88d9 |  | button | Apartment Db is fit off, backing plate installed (where applicable) and fire sealed? | Yes,No
label | 565affe2-8175-5d77-b931-903d7ba8bf96 |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
button | 18bf0870-0698-5efc-808a-44e633db6110 |  | button | CAt6/Cat6A Outlets are all fit off (this may include House CCTV/WAP or Intercom!) | Yes,No
label | 611afb87-294a-596d-9b87-a77d690f1eef |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
button | 8b6e8fc0-a66b-5cdb-b25f-5dcfaaf33017 |  | button | NBN conduit and string labelled and accessible at correct location within enclosure or cupboard? | Yes,No
label | d87fd309-82aa-500a-aa87-4103f7c7dd7f |  | note | *Mandatory Image -Marked Up Drawing Including Title Block Revision
checkpoint-status |  |  | checkpoint | Lead In Fit Off completed to specification/drawings - Area left clean & tidy
label | d050cb5a-8eb0-558e-9997-8282ac0876ef |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | af9a61d6-cba4-5d58-8011-817834c92851 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 09399d0d-2469-53f1-8a50-05678fdf4ffa |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622, ADAM STRONG - AGrade: A38815 - Employee#: 2002, ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794, ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684, ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863, ALAN BIRCHALL - Agrade: A18981 - Employee#: 379, ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111, ALI HASAN - Agrade: A48087 - Employee#: 1654, ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015, ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972, ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309, BEN DARBY - Agrade: A53332 - Employee#: 1702, BEN FINDLAY - Agrade: A41429 - Employee#: 2006, BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933, BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733, BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801, BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850, BRENTON HILL - Agrade: A47213 - Employee#: 1729, BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887, BROCK DOWNIE - Agrade: A53290 - Employee#: 1849, BROCK LLOYD - Agrade: A44808 - Employee#: 1680, CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193, DANIEL BENDINELLI - Agrade: A67728 - Employee# 2097, DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937, DAVID OLSEN - Agrade: A42915 - Employee#: 1685, DEAN NGUYEN - Agrade: A48514 - Employee#: 1515, DEREK JACOBS - Agrade: A67318 - Employee#: 2078, DWAYNE KLOET - Agrade: A48278 - Employee#: 1239, ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782, EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895, FERGUS COATES - Agrade: A59054 - Employee#: 1774, FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679, HUY DO - Agrade: A40954 - Employee#: 873, IMMANUEL KAWITI - Agrade: - Employee#: 2023, JACKSON SHARPE - Agrade: A53801 - Employee#: 1540, JAMES MARASCO - Agrade: A55184 - Employee#: 1758, JAMES PLEASANT - Agrade: A62956 - Employee#: 1976, JAMES SPOKES - Agrade: A48756 - Employee#: 1770, JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756, JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719, JASON PERL - Agrade: A36692 - Employee#: 1868, JASON SALE - Agrade: A28662 - Employee#: 1615, JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029, JESS ZAHRA - Agrade: A52969 - Employee#: 1403, JOEL BASSETT - Agrade: A39498 - Employee#: 1958, JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908, JOHN GREEN - Agrade: A55589 - Employee#: 1734, JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682, JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720, KALE BLACKLER - Agrade: A39293 - Employee#: 1751, KAYNE WALKER - Agrade: A38805 - Employee#: 1718, KEVIN MURPHY - Agrade: A63544 - Employee#: 2022, KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698, LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834, MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308, MARK D_ANGELO - Agrade: A40610 - Employee#: 1832, MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352, MATTHEW COX - Agrade: A42092 - Employee#: 1704, MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894, MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915, MICHAEL BRASHER - Agrade: A29237 - Employee#: 954, NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748, PAT DOUBLE - Agrade: A46604 - Employee#: 1118, PAUL HARMAN - Agrade: A26306 - Employee#: 1728, PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190, PETER LEWIS - Agrade: A53556 - Employee#: 1749, PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612, ROB POLLARD - Agrade: A56906 - Employee#: 1754, ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132, RYAN DEPRADA - Agrade: A41361 - Employee#: 1848, SCOTT RYAN - Agrade: A59062 - Employee#: 2017, SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034, SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771, SIMON COLLARD - Agrade: A32749 - Employee#: 883, STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829, TOM HAMILTON - Agrade: A48254 - Employee#: 1434, VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218, WILLIAM FISHER - Agrade: A20679 - Employee#: 859, Other (Specify below)
text | 578dc0af-c4d4-5cc4-8a7b-12abef052b21 |  | textbox | Other (Specify here)
label | 844cf00a-4cbb-54a0-9c18-592f12efea73 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-007 - Conduit Checklist (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-007 - Conduit Checklist (Rev 0 +Names) | 7f37a5a6-927f-43f7-908d-cfeab45386ec
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 39f429ca-3331-5406-b5d5-3f673c36f70d |  | textbox | Drawing & Revision #
text | 4ddbc334-caa1-5aae-9a34-dfbfbbb2e512 |  | textbox | Location
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | bed42fbd-7dcd-5026-b5f1-e44e02071b37 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint-status |  |  | checkpoint | Conduit layout plan prepared
label | c8d41cfa-5786-565b-ad06-d120950cd082 |  | note | Plan addresses minimum distance from other services, as per AS/NZS 3000 Table 3.7 (Minimum Separation of Underground Services
checkpoint-status |  |  | checkpoint | Required cover identified as per AS/NZS 3000 – Table 3.6 (Underground Wiring Systems – Minimum Depth of Cover)
checkpoint-status |  |  | checkpoint | Conduit installation. Check all joints
checkpoint-status |  |  | checkpoint | Accessories installation. Check all joints
checkpoint-status |  |  | checkpoint | Check conduits are securely anchored
checkpoint-status |  |  | checkpoint | Check accessories are securely anchored
checkpoint-status |  |  | checkpoint | Warning tape installed (not required for cast-in concrete conduits) as per AS/NZS 3000 – 3.11.4.5.
checkpoint-status |  |  | checkpoint | Conduits installed as per plan (inspect prior to pour)
label | 321a917c-bba6-5604-b17a-cef4166291cb |  | note | Photos taken showing all conduits - Attach below
checkpoint-status |  |  | checkpoint | Required cover in place
checkpoint-status |  |  | checkpoint | Conduit locations marked on As built drawing - Attached below as applicable
checkpoint-status |  |  | checkpoint | Conduit works completed to specification/drawings - Area left clean & tidy
label | 2043a4ea-5d6c-5efb-9760-063e414718d0 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
select | cac2c4e5-872a-5a1b-9fec-179a42f2a356 |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 5ea4a55f-dd58-5c0b-a919-4e284f6b1c5b |  | textbox | Other (Specify here)
select | 803babb0-91a8-5884-88d4-b398178f0457 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 2f554358-bfde-5460-bfee-2687db5dc04c |  | textbox | Other (Specify here)
text | cfcc67d3-683b-5fc6-9a01-0b334eeee67f |  | textbox | Witnessed by (Builder/QAM)
label | 3c480a54-0bc5-5572-85d9-bdaff764eee2 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | Bends into cage and conduit capped checklist |  |  |  |  | Yes | Bends into cage and conduit capped checklist | 819540d9-9abd-4603-9db0-d70245c635fa
checkpoint-status |  |  | checkpoint | Bends into cage and conduit capped - N/A if no, PASS and add photo if yes
checklist-flat |  |  | checklist | AE-ITCX-011 - Main Switchboard Inspection Sheet (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-011 - Main Switchboard Inspection Sheet (Rev 0 +Names) | 85d09d91-2928-4e15-8ef8-2b96fed00aca
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 01fe9a04-c25c-5c06-bd9f-88a5640c9025 |  | textbox | Switchboard No.
text | a5d823cf-69dc-5db8-90c2-fc38829ab333 |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | MEN and MSB Meter Panel Checklist (AF019) complete
checkpoint-status |  |  | checkpoint | Main switchboard location and clearances as per AS/NZS 3000
checkpoint-status |  |  | checkpoint | Perform insulation resistance test on main switchboard
checkpoint-status |  |  | checkpoint | Service protection device set and labelled
checkpoint-status |  |  | checkpoint | Consumer mains entry point fire rated
checkpoint-status |  |  | checkpoint | Emergency and exit lighting complete
checkpoint-status |  |  | checkpoint | Access/egress doors installed and labelled
checkpoint-status |  |  | checkpoint | Switchboard room fire rating confirmed
checkpoint-status |  |  | checkpoint | Verification of Switchboard Integrity by Supplier (e.g. Aline Final Inspection & Testing Checklist)
checkpoint-status |  |  | checkpoint | Electrical inspection – Prescribed Works Certificate signed
checkpoint-status |  |  | checkpoint | Power Supply Authority energisation sign off
checkpoint-status |  |  | checkpoint | Main Switchboard works completed to specification/drawings - Area left clean & tidy
label | 69672848-0224-5c07-a4f8-0e9dd79f7bca |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | bf32f4bd-f7c4-57c3-abe2-42b2b4aa5306 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 038076f3-348c-5bb2-82b2-bca97e8968a3 |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | e3aa5b88-e761-50e9-95c8-be6195b9360e |  | textbox | Other (Specify here)
select | f9e85e3b-eb6d-5038-85b8-be6b4733b259 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | edb307fd-110c-54a1-9aaf-f97aa5e5ca59 |  | textbox | Other (Specify here)
label | 43df0ba7-e7a3-5689-853a-d54e4bbf3fcb |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AE-ITCX-34 - Communications/Security Rack Installation QA (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-34 - Communications/Security Rack Installation QA (Rev 0 +Names) | 87bbb332-5010-4577-8c73-db929ada2b33
checkpoint-group |  |  | section | Communications Rack
checkpoint-status |  |  | checkpoint | Is the communications riser ready for communications rack installation
label | 6ae0849d-ec69-5849-8804-34ac378a30be |  | note | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
label | ca7dcd25-bc4b-529f-9f61-4a4e10635ab8 |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Does the communications rack match the approved technical data
checkpoint-status |  |  | checkpoint | Has the communications rack been installed in position as per the Appselec communications riser elevation shop drawings and floor plan layout
text | 588c8f8b-e4c1-597f-b36f-0a9b096639d6 |  | textbox | Drawing & Revision # (or Attach photo below)
checkpoint-status |  |  | checkpoint | Has the communications rack been fixed to the floor using appropriate fixings
checkpoint-status |  |  | checkpoint | Are the doors and side panels installed and free from damage
checkpoint-status |  |  | checkpoint | Does the communications rack comply with all the relevant clearances
label | 69e9bdcf-7a2f-5194-8a27-a8558fe94704 |  | note | Are door swings and access to the communications rack unobstructed
checkpoint-status |  |  | checkpoint | Has the communications rack been permanently labelled with a traffolyte label or similar on the door
label | 12aa7628-4307-5c74-a663-7f977d0145b9 |  | note | Check that the label matches the communications rack layouts
checkpoint-status |  |  | checkpoint | Has the Appselec label/logo been fixed to the front of the communications rack
label | ed9320ab-97da-52bb-aa20-fa3126d78506 |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-group |  |  | section | Communications Earthing Terminal (CET)
checkpoint-status |  |  | checkpoint | Has a CET been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth cable been terminated to the CET
label | 076dff2d-021c-5534-ad7e-bcd66a440658 |  | note | Refer to Communications SLD for earth cabling schematic
label | 5c390725-9eb5-5b88-be10-a5467fd1a739 |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Has an earth bar been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth been terminated to the earth bar from the CET
checkpoint-status |  |  | checkpoint | Has the 6 mm2 green/yellow earth been identified and labelled with “Communications Earth” at the originating electrical distribution board
checkpoint-group |  |  | section | FOBOTS (Fibre Optical Breakout Trays)
checkpoint-status |  |  | checkpoint | Does the FOBOT match the approved technical data
checkpoint-status |  |  | checkpoint | Has the FOBOT been installed in the correct rack RU position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Has the FOBOT been labelled permanently with traffolyte label or similar
checkpoint-status |  |  | checkpoint | Has a service loop been provided in the optical fibre cable
checkpoint-status |  |  | checkpoint | Has the fibre port arrangement on the FOBOT been detailed and labelled
label | 01bf6b98-73ec-5067-bcc7-c6d3fcfbfd67 |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Do the fibre adapters on the FOBOT match the type of fibre being used
label | ed116ca3-7c18-554f-9ca1-f1ffff8e0672 |  | note | e.g. aqua = multimode, green = singlemode
label | 034f6f79-36c7-566e-a145-669bd1a1b842 |  | note | Adapters, pigtail connector colours must match, fibre cable type must match
checkpoint-status |  |  | checkpoint | Have fibre protective caps been installed on all fibre adapter ports
checkpoint-group |  |  | section | Cat 6/6A Patch Panels
checkpoint-status |  |  | checkpoint | Does the Cat 6/6A patch panels match the approved technical data
checkpoint-status |  |  | checkpoint | Have the Cat 6/6A patch panels been installed in correct rack RU position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Have the Cat 6/6A patch panel ports been labelled permanently with traffolyte label or similar
label | 39e8b24b-b7e7-56ae-ab15-5e79385fac2a |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Have cable wrap-around labels been attached to each individual Cat 6/6A cable behind the patch panels
label | 75359b1b-5eef-5ffb-8855-cd5a585f127b |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Have the Cat 6/6A patch panels been earthed with 2.5 mm2 green/yellow earth cable from the earth bar within the communications rack? (Shielded patch panels only)
checkpoint-group |  |  | section | Cable Management
checkpoint-status |  |  | checkpoint | Have horizontal cable managers been installed in the correct rack RU position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Have vertical cable managers been installed in the correct rack RU position as per the communications rack layout
checkpoint-group |  |  | section | Power
checkpoint-status |  |  | checkpoint | Has the correct power been provided for the communications racks
label | fc88d5df-5662-5b16-87f4-66f909dc50d4 |  | note | Check for captive outlets? Are there 2x or 1x? Are they 10A, 15A or 20A? Check the Appselec power floor layouts against the communications specification
checkpoint-status |  |  | checkpoint | Do the PDU’s match the approved technical data
checkpoint-status |  |  | checkpoint | Have the PDU’s been installed in position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Have the PDU’s been plugged into the captive outlets/rack mounted UPS as detailed on the communications rack layouts
checkpoint-status |  |  | checkpoint | Have the PDU’s been labelled appropriately detailing the power source
label | 28a3309c-0c43-5542-9edf-93e302e338c4 |  | note | For example UPS supply (Generator backed) DB-XX
checkpoint-group |  |  | section | Rackmount UPS
checkpoint-status |  |  | checkpoint | Is the communications rack/riser ready for UPS installation
label | 72a32ace-157d-523c-9c1d-411c6273e0a2 |  | note | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint-status |  |  | checkpoint | Does the UPS match the approved technical data
checkpoint-status |  |  | checkpoint | Has the UPS been installed in position as per the communications rack layouts
checkpoint-status |  |  | checkpoint | Has the UPS been labelled appropriately detailing the power source
label | 48c0271a-3e4f-5777-89d2-2f022305f3a8 |  | note | For example UPS supply (Generator backed) DB-XX
label | 42981cf2-5312-55a7-9e63-f6fb570e04ed |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Has any associated Battery Backup for the UPS been installed as per the communications rack layouts and is it connected
checkpoint-status |  |  | checkpoint | Has the UPS been commissioned? Refer to UPS ITP for commissioning details
checkpoint-group |  |  | section | Active Equipment
checkpoint-status |  |  | checkpoint | Is the communications rack/riser ready for Active Equipment installation
label | 246a944b-3d8b-58ff-9546-4c30b4571b08 |  | note | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint-status |  |  | checkpoint | Does the Active Equipment need to be configured prior to installation within the communications rack
checkpoint-status |  |  | checkpoint | Does the Active Equipment match the approved technical data
checkpoint-status |  |  | checkpoint | Has the Active Equipment been installed in the correct rack RU position as per the communications rack layouts
label | cf9cb955-ac45-56fb-b2de-bc38a74ad40a |  | note | MANDATORY PHOTO - Photo attached below
checkpoint-status |  |  | checkpoint | Do you have a network diagram detailing the connection and labelling of all Active Equipment
checkpoint-status |  |  | checkpoint | Has the Active Equipment been labelled appropriately as per the vendor requirements
label | 5de2ee05-be40-5c65-b6d6-5c98d28facab |  | note | All switches are to be labelled with the correct vendor labelling convention
checkpoint-status |  |  | checkpoint | Have SFPs been provided and installed
label | c8e22cea-4a8c-5ec5-9d81-77602ef5f094 |  | note | Check that they are the correct SFP for the optical fibre cable installed
label | 7016b022-5f15-583f-bbb9-0ab1f41b1b34 |  | note | Check they are installed into the correct port
label | 3ddd9d95-83a1-5a76-a7e4-8c044f50c883 |  | note | (SFP is a small form-factor pluggable transceiver)
checkpoint-status |  |  | checkpoint | Have stacker cables been provided to stack switches together
label | f4f5255c-b57f-59f0-b701-df52874abb49 |  | note | Are they connected as per the integrator/vendor requirements
checkpoint-status |  |  | checkpoint | Have the switches been connected to the PDUs
label | d8afbaed-b777-5ddb-a727-151e8798f864 |  | note | Check if switches require one supply or two supplies (dual power redundancy)
label | 9755bde0-b7c0-5548-8d1e-d8f9a5a08b30 |  | note | Check if switches require UPS supply/UPS + generator supply
checkpoint-group |  |  | section | Patching
checkpoint-status |  |  | checkpoint | Do you have the correct length, colour, type (Cat6/6A) and quantity of patch leads
checkpoint-status |  |  | checkpoint | Do you have a patching schedule detailing which switch port patches to which patch panel port
checkpoint-status |  |  | checkpoint | Do you have the appropriate cable management capacity installed to patch cables as per the patching schedule
checkpoint-group |  |  | section | Mandatory Photos
checkpoint-status |  |  | checkpoint | MANDATORY Photo 1: Front of rack, door closed - Photo attached below
checkpoint-status |  |  | checkpoint | MANDATORY Photo 2: Front of rack, door open - Photo attached below
checkpoint-status |  |  | checkpoint | MANDATORY Photo 3: Front of rack, door closed - Photo attached below
checkpoint-status |  |  | checkpoint | MANDATORY Photo 4: Rear of rack, doors open - Photo attached below
label | be8fb38f-ecbc-56f0-a49c-718fff2b5c63 |  | note | Additional Photos attached below as applicable
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Communications/Security Rack Installation completed to specification/drawings - Area left clean & tidy
label | 94f22460-3ff3-5e87-9811-7a70ba9989fa |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | f509536b-88d3-5115-ad81-380c599267b2 |  | note | Any Corrective Actions to be Photographed & Commented below
select | c2915d11-849c-547b-b6be-3542c67654ad |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | f777bdf8-d7fb-51d3-b623-1bf531f807e0 |  | textbox | Other (Specify here)
label | a4193f6d-5458-563c-afb3-3224e78d19b7 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | Security Conduit to cage checklist |  |  |  |  | Yes | Security Conduit to cage checklist | 8c6231d8-7026-4bd6-b2b8-97242bddf6da
checkpoint-status |  |  | checkpoint | Security Conduit to cage - N/A if no, PASS and add photo if yes
checklist-sectioned |  |  | checklist | AE-ITCX-027 AS:3003-Table B1 Patient Area CL (Rev 0) |  |  |  |  | Yes | AE-ITCX-027 AS:3003-Table B1 Patient Area CL (Rev 0) | a741f5bc-7d3f-4939-b4a0-06c58b9bbb2d
checkpoint-group |  |  | section | Preface
checkpoint-status |  |  | checkpoint | Appendix B: Summary of Information - Pass once confirmed
label | eb2dca06-54b9-5526-8925-2e83ae9c5af1 |  | note | Commissioning Inspection Checklist
label | 4489b6cf-9ed6-5db1-af47-683d7fc9aa01 |  | note | .. ..
label | 52b3a6fc-a469-5c15-a759-0ebacca17b8a |  | note | B1: General
label | 4135ee3f-d76e-5ee0-a8dc-40eeca4c0077 |  | note | This Appendix sets out a checklist for electrical area installations in accordance with this standard
label | d9885bd4-0ea7-5ff6-9704-be6fada8a8bb |  | note | All body-protected and cardiac-protected electrical areas shall be in accordance with this Standard by the use of a commissioning checklist
label | c5fdfe55-8f75-5aac-a12e-2bc9e0400496 |  | note | The commissioning results may be recorded electronically, on paper, or other similar medium. The commissioning checklist shall be retained by the person conducting the tests and a copy provided to the responsible organisation/entity. NOTE:This checklist can also be used for special patient areas as specified in Section 5
label | 07a49a49-4690-5f45-bc32-c42d2077ac59 |  | note
label | ec0db698-1b81-5317-9e9a-fb924721f11c |  | note | .. ..
label | bde85cef-554d-58c0-b79b-21c2308da4db |  | note | B2: Commissioning Inspection Checklist for Patient Areas
label | 4b971663-fddd-52ae-ae75-b97f8a914683 |  | note | A checklist shall be developed to record the results for each patient area commissioned, in accordance with each of the required clauses of this Standard
label | eca8293f-1a11-5883-bcaf-638ac994c145 |  | note | The checklist shall be in English, and shall clearly record the result for each item. NOTE: Checked boxes with a 'Pass' or 'Fail' or 'N/A' would satisfy this requirement
label | 9597e51c-f8b9-5090-b8d9-2fb3713bc2d2 |  | note | .. ..
label | d21a3ae6-9e2f-5ca9-98b6-377564daf75d |  | note | B3: Commissioning Checklist
label | b6893b7e-7095-524e-8cd1-902ceabed98a |  | note | The information in Table B1 shall be included in the commissioning checklist and have a result recorded against each item
checkpoint-group |  |  | section | 2.1: General Requirements for Body-Protected and Cardiac-Protected Electrical Areas
checkpoint-status |  |  | checkpoint | 2.1 - All locations that form part of the current works and which it is intended that low-voltage medical electrical equipment will be used in contact with patients and can be operated while connected to the electrical supply mains (except in emergencies) are checked to confirm that they are signposted as body-protected or cardiac-protected electrical areas
label | d10e0d60-b703-54c0-b797-b99541b778e9 |  | note | Where there is doubt about the intended use of a particular location, formal clarification should be sought from the responsible organisation
label | 4983cf95-d025-5812-937a-d5469caaabab |  | note | If an area is not required to be wired as a patient area a letter stating that mains operated medical electrical equipment will not be used within that area should be provided by the responsible organisation
checkpoint-status |  |  | checkpoint | 2.1 - Cardiac-protected and body-protected electrical areas not in the same room
checkpoint-group |  |  | section | Classification of Patient Areas
checkpoint-status |  |  | checkpoint | 2.2.3 - Only those specified areas are wired as cardiac-protected
checkpoint-status |  |  | checkpoint | If others nominated, then confirm documentation outlining specific requirements is provided by responsible organisation
checkpoint-status |  |  | checkpoint | 2.2.4 - Patient areas not wired as cardiac-protected electrical areas are wires as body-protected electrical areas
checkpoint-status |  |  | checkpoint | All patient ensuites, bathrooms, shower rooms and toilets wired a body-protected electrical areas
checkpoint-group |  |  | section | Low-Voltage A.C. Supplies
checkpoint-status |  |  | checkpoint | 2.4.1.1 - Confirm that electrical final sub-circuits are unique to respective rooms in body-protected electrical areas
checkpoint-status |  |  | checkpoint | Ensuite in adjoining room may share final sub-circuit
checkpoint-status |  |  | checkpoint | Confirm that cleaning outlets are on a separate electrical sub-circuit to other socket-outlets in the room
checkpoint-status |  |  | checkpoint | 2.4.1.2 - Confirm that electrical final sub-circuits are unique to respective rooms in cardiac-protected electrical areas
checkpoint-status |  |  | checkpoint | 2.4.1.3 - Final sub-circuit for socket-outlets identified 'CLEANING PURPOSES ONLY' supplies no other socket-outlets
checkpoint-status |  |  | checkpoint | 2.4.2 - Confirm conformance with AS/NZS:3000 for protection against mechanical damage
checkpoint-status |  |  | checkpoint | 2.4.3.2.1 - Confirm by inspection and testing that al socket-outlets specified are protected by LPD (except those exempted)
checkpoint-status |  |  | checkpoint | 2.4.3.2.2(a) - Socket-outlets that are accessible in patient areas without using a key or tool
checkpoint-status |  |  | checkpoint | 2.4.3.2.2(b) - Excludes multi-phase outlets conforming with AS/NZS:3123
label | a6dc95bb-b00d-5241-be8a-adc3a9a9b5ab |  | note | Socket-outlets conforming with AS/NZS:3112 that are located within 2.0m of the entrance to a body-protected electrical area and are accessible without the use of a key or tool in any room, corridor, etc., opening directly off a patient area
checkpoint-status |  |  | checkpoint | Socket-outlets conforming with AS/NZS:3112 that are located within 5.0m of the entrance to a cardiac-protected patient area and are accessible without the use of a kay or tool in any room, corridor, etc., opening directly off a patient area
checkpoint-status |  |  | checkpoint | 2.4.3.2.2(c) - Socket-outlet(s) installed outside the patient area but used to supply medical electrical equipment used within the patient area
checkpoint-status |  |  | checkpoint | 2.4.3.2.3 - LPD protection not required for permanently installed pendant-type sockets that will not accept common 10 or 15A plugs conforming to AS/NZS:3112
checkpoint-status |  |  | checkpoint | LPD protection required for socket-outlets that are mounted on, and form part of, a permanently installed medical system provided that such socket-outlets are clearly intended to power specified component parts of the medical electrical system
checkpoint-status |  |  | checkpoint | LPD protection not required for socket-outlets specifically intended for clocks
checkpoint-status |  |  | checkpoint | 2.4.3.2.2(a) - LPD protection not required for socket-outlets that are mounted on the ceiling or above 2.3m on the wall, and are clearly intended for permanently mounted plug-in equipment other than medical electrical equipment
checkpoint-status |  |  | checkpoint | 2.4.3.3 - LPD protection provided for permanently wired medical electrical equipment with Type B applied parts, consisting
boolean | 5da5c7eb-5644-5f4e-b619-8424dc1aa527 |  | tickbox | Electrodes or transducers that contact patients
boolean | fc8c1987-2b5e-5c49-8ead-dc7ef38f82d4 |  | tickbox | Parts that enter patients
boolean | 66604d7a-5cc5-5b9a-8568-39b1d031c430 |  | tickbox | Parts that contact liquid in patients
button | 80b08ff2-2fc5-5da7-8ea3-a83787cef961 |  | button | Other permanently wired electrical equipment is protected as required by AS/NZS:3000 | Pass, Fail, N/A
checkpoint-status |  |  | checkpoint | 2.4.4.1 - Where the switchboard from which the UPS is to be supplied contains an essential supply of sufficient capacity the UPS is connected to that essential supply
checkpoint-status |  |  | checkpoint | 2.4.4.2 - Where the output circuit of the UPS is earth-free in every mode of operation, the UPS is treated as an isolation transformer and provided with a LIM
checkpoint-status |  |  | checkpoint | Where one output terminal of the UPS is connected to the neutral input terminal earthed within the UPS, the output is protected by RCD or isolated supply
checkpoint-status |  |  | checkpoint | 2.4.4.3 - A suitably located UPS status indicator is provided where socket-outlets or permanently wired equipment are connected to a UPS and there is continuous patient observation
checkpoint-status |  |  | checkpoint | Confirm that the alarm/indicator operates as intended
checkpoint-group |  |  | section | Low-voltage D.C. Supplies
checkpoint-status |  |  | checkpoint | 2.5 - Reticulated low-voltage D.C. - Confirm that they are earth-free and measure current
text | 0d32558a-c0ca-5882-8599-a1889d2a6c9b |  | textbox | Current
checkpoint-group |  |  | section | Access to Controls & Indicators
checkpoint-status |  |  | checkpoint | 2.6 - Confirm that Controls & Indicators are readily accessible
checkpoint-status |  |  | checkpoint | Confirm that Controls & Indicators, depending on the location of socket-outlets or permanently connected equipment requiring LPD protection, located in accordance with Table 2.1
checkpoint-status |  |  | checkpoint | Confirm that Controls & Indicators, Not mounted under benches, within cupboards or cabinets, or behind bulky equipment in such manner as to inhibit easy access to the controls and indicators
checkpoint-status |  |  | checkpoint | Confirm that Controls & Indicators, if mounted ne the entrance of a room, separated by at least 500mm from any wall-mounted light switch
checkpoint-status |  |  | checkpoint | The above checked requirements do not apply to RCDs protecting socket-outlets that are identified 'CLEANING PURPOSES ONLY' in accordance with Clause 2.7.3 or RCDs mounted in ensuite vanities
checkpoint-group |  |  | section | Socket-Outlets
checkpoint-status |  |  | checkpoint | 2.7.2 - Socket-outlets that are not readily accessible and are not protected by a dedicated LPD are provided with a separate readily accessible isolating double-pole switch
checkpoint-status |  |  | checkpoint | 2.7.3.1 - In body-protected electrical areas, confirm socket-outlet identified 'CLEANING PURPOSES ONLY' within 15.0m of any point in the patient area
checkpoint-status |  |  | checkpoint | In cardiac-protected electrical areas, confirm socket-outlet identified 'CLEANING PURPOSES ONLY' within the patient area
checkpoint-status |  |  | checkpoint | 2.7.3.2 - Socket-outlets that are identified 'CLEANING PURPOSES ONLY' are protected by LPDs that do not protect any other type of socket-outlet
checkpoint-status |  |  | checkpoint | 2.7.4 - Correct labelling is used
checkpoint-status |  |  | checkpoint | 2.7.4.1 - Socket-outlets protected by LPD are labelled 'From RCDX' or 'From LIMX', depending on whether the LPD is an RCD or isolated supply
checkpoint-status |  |  | checkpoint | 2.7.4.2 - Confirm 'ON' indication of socket-outlet switch
checkpoint-status |  |  | checkpoint | 2.7.4.3 - Confirm socket-outlets connected to a normal (mains) supply are colour-coded white
checkpoint-status |  |  | checkpoint | Confirm socket-outlets connected to an essential supply are colour-coded red
checkpoint-status |  |  | checkpoint | Confirm socket-outlets connected to an uninterruptible supply are colour-coded dark blue
checkpoint-status |  |  | checkpoint | Confirm socket-outlets identified 'CLEANING PURPOSES ONLY' are colour-coded beige
checkpoint-status |  |  | checkpoint | 2.7.4.4 - Confirm indicator colour and operation
checkpoint-status |  |  | checkpoint | 2.7.5 - Confirm each socket-outlet is individually switched
checkpoint-status |  |  | checkpoint | Confirm if socket-outlet supplied from isolated supply then it is double poled
checkpoint-group |  |  | section | Residual Current Devices (RCDs)
checkpoint-status |  |  | checkpoint | 2.8.1 - Confirm Type1 RCDs in use
checkpoint-status |  |  | checkpoint | Confirm RCD sensitivity using tests in this Standard (and record results)
text | 9cb754e9-672c-553a-9b8f-4ff57fc114a0 |  | textbox | RCD result
checkpoint-status |  |  | checkpoint | Confirm RCD maximum tripping time using tests in this Standard (and record results)
text | e1d17c3a-fe72-54d8-b112-fcd124da19d7 |  | textbox | RCD result
checkpoint-status |  |  | checkpoint | Check cClauses 8.2.3.2 and 8.2.3.3 for body-protected areas or Clauses 8.3.4.2 and 8.3.4.3 for cardiac-protected areas
checkpoint-status |  |  | checkpoint | 2.8.2 - Confirm by inspection and testing that there are no RCDs protecting other RCDs
checkpoint-status |  |  | checkpoint | 2.8.1 - Confirm by testing that all RCDs are double poled
checkpoint-status |  |  | checkpoint | 2.8.3 - Confirm that RCDs that are used as LPDs do not protect the supply to the below
boolean | 9593a767-60c4-5c4c-99ae-f1667592612b |  | tickbox | More than 12 electrical points, i.e. socket-outlets, items of permanently-wired equipment or combinations thereof
boolean | ed4cef8b-94a4-5135-b64d-b28ccf995790 |  | tickbox | Socket-outlets in different rooms
boolean | b20a12af-6c22-54d5-bde8-8c949a3d1626 |  | tickbox | Socket-outlets in a a patient area and socket-outlets in an area that is not a patient area except, if applicable, for socket-outlets mounted in the ceiling space of a patient area in accordance with Clause 2.4.3.2(iii)
checkpoint-status |  |  | checkpoint | 2.8.4 - Confirm indicator colour and operation of power available indicator of RCDs used as LPDs
checkpoint-status |  |  | checkpoint | 2.8.5 - Confirm by inspection that each RCD is labelled to identify distribution board and circuit breaker, and with unique identifier, e.g. RCD X
checkpoint-status |  |  | checkpoint | 2.8.7 - Confirm that separate test facility is provided for RCD used as LPD when connected to permanently wired equipment
checkpoint-group |  |  | section | Low Voltage Isolated Supplies
checkpoint-status |  |  | checkpoint | 2.9.1 - Confirm isolation transformer LIM and overload monitor are correctly labelled that they conform with AS/NZS:4510
label | 5c790e28-ddff-53b9-bb00-656ab32dc15c |  | note | 2.9.2 - Confirm by examining the location, housing and ventilation of the isolation transformer
checkpoint-status |  |  | checkpoint | In cardiac-protected electrical areas, confirm that isolation transformer only supplies one patient location
label | a140bb33-41c4-5bbe-896b-1cf99f9cfe2c |  | note | 2.9.3 - See to Clause 2.9.3
checkpoint-status |  |  | checkpoint | 2.9.4 - Confirm overload monitor by inspection and testing using tests in this Standard (and record results)
text | 103a9030-6aa6-589f-a50b-4b19ad227753 |  | textbox | RCD result
checkpoint-status |  |  | checkpoint | 2.9.5 - Confirm LIM prospective hazard current display and current alarm using tests in this Standard (and record results)
text | c79da12f-3884-57f2-a88b-53f4a3db37da |  | textbox | RCD result
checkpoint-status |  |  | checkpoint | Confirm by inspection that labelling is consistent and identifies circuit and LIM
label | 7cb7f4a7-e07f-5f6f-b4ab-3ba1e163f27b |  | note | See to Clause 2.9.3
checkpoint-status |  |  | checkpoint | 2.9.6 - Confirm prospective hazard current of each transformer-isolated supply does not exceed 2mA
checkpoint-status |  |  | checkpoint | For commissioning, the PHC under normal conditions of operation shall be confirmed by applying the following process to each transformer Line Isolation Overload Monitor (LIOM)
boolean | 7b0f725c-9629-58bd-8eaf-b78eb1721747 |  | tickbox | All electrical equipment are disconnected from the supply
boolean | 91a7c86b-1e72-5869-a80e-96cf7b73db14 |  | tickbox | The current flowing through a low impedance ammeter connected between one isolated supply conductor and earth is noted. The test is repeated for the other isolated supply conductor. The larger of the noted values is the prospective hazard current. It shall be less than 2mA
boolean | c7f161b7-56e0-5bc1-b978-49d960774498 |  | tickbox | The prospective hazard current of the supply is recorded in the commissioning checklist
checkpoint-status |  |  | checkpoint | 2.9.7 - In body-protected electrical areas, confirm that the number of socket-outlets protected by isolated supply does not exceed 12
checkpoint-status |  |  | checkpoint | In cardiac-protected electrical areas, confirm that the number of socket-outlets protected by isolated supply does not exceed 12
checkpoint-status |  |  | checkpoint | 2.9.8 - Confirm that a test facility is provided if permanently wired equipment is protected by an individual isolated supply
checkpoint-group |  |  | section | Isolation Switches
checkpoint-status |  |  | checkpoint | 2.10 - Confirm that a separate individual readily accessible switch(s) has been provided for the below
boolean | 8bc5b17e-c67b-5779-9f4e-f730a97915d2 |  | tickbox | For conductors that supply an inaccessible socket-outlet that is protected by an LPD
boolean | a040393f-2468-5ebe-bf22-da5739536f0b |  | tickbox | To permanently wired electrical equipment that is connected to an LPD that also protects socket-outlets
checkpoint-status |  |  | checkpoint | Confirm correct labelling of the switch
checkpoint-group |  |  | section | Identification
checkpoint-status |  |  | checkpoint | 2.12.1 - Confirm labelling is of the correct format and size and placed in correct location
checkpoint-status |  |  | checkpoint | 2.12.2 - Confirm patient area signage installed in correct location and appropriate labels attached and signed
checkpoint-group |  |  | section | Testing & Verification of Electrical Work
checkpoint-status |  |  | checkpoint | 2.13 - To confirm that requirements of this Standard have been met, after completion, but before being placed in service, the installation shall be as per below
boolean | 8d9a9aba-121b-5995-9b16-e5c044f4bdc4 |  | tickbox | Inspected as far as is practicable
boolean | f2ebda68-1cfa-5927-87aa-cc052f9534e9 |  | tickbox | Tested and confirmed in accordance with Appendix B of this Standard and AS/NZS:3000
checkpoint-group |  |  | section | Additional Documentation
checkpoint-status |  |  | checkpoint | 2.14 - Confirm commissioning checklist in accordance with Appendix B
checkpoint-status |  |  | checkpoint | 3.2 - Additional requirements for body-protected electrical areas - Earthing
label | 237a440a-8585-5027-8c87-b81bf2f9c573 |  | note | Confirm conformance with AS/NZS:3000
checkpoint-status |  |  | checkpoint | 4.2 - Additional requirements for cardiac-protected electrical areas - Earth-Free ELV
label | bbc5f4da-aa13-5eeb-8a40-36bf19b779d4 |  | note | Confirm that no more than 10mA can flow to earth
checkpoint-status |  |  | checkpoint | 4.3 - Disposition of electrical points controlled by LPDs
label | 2d679443-5c08-52e1-9a18-7269e9f8f16d |  | note | Confirm by tripping all RCDs in a particular patient location, to confirm that socket-outlets in any other patient location(s) are not protected
checkpoint-group |  |  | section | Earthing & Equipotential Bonding
checkpoint-status |  |  | checkpoint | 4.4.1 - Confirm earthing has been carried out in accordance with the requirements of this Clause and the requirements of AS/NZS:3000
checkpoint-status |  |  | checkpoint | The minimum size of any protective earthing system conductor shall be not less than that required by AS?NZS:3000
checkpoint-status |  |  | checkpoint | The minimum size of any EP bonding system conductor associated with the fixed wiring installed on site shall be 4mm2
checkpoint-status |  |  | checkpoint | 4.4.2.3 - Confirm by inspection that only one EP junction is in use
checkpoint-status |  |  | checkpoint | 4.4.2.4.1 - Confirm by inspection and testing that the resistance of the earthing conductor between each socket-outlet and EP junction or node is <=0.1 Ohm For the below
boolean | 50f168a0-f513-5ded-bd6f-503e0ccc2a9a |  | tickbox | Socket-outlets within cardiac-protected electrical area
boolean | fe8f674f-84bc-50d8-849c-b61dfeb27413 |  | tickbox | Socket-outlets within specified distance of entrance to cardiac-protected electrical area
boolean | 9e28b616-4626-5625-b645-78f5b91db574 |  | tickbox | Socket-outlets in another room/ceilings for medical electrical equipment with conductive parts accessible within cardiac-protected electrical area
checkpoint-status |  |  | checkpoint | Confirm protective earthing conductors are insulated and segregated from other conductive items
checkpoint-status |  |  | checkpoint | Confirm the below by inspecting and testing
boolean | c4533149-de7d-590e-9203-04fb81682460 |  | tickbox | Each node is individually connected to the EP junction by insulated conductors with a maximum resistance of 0.01 Ohms
boolean | 7efa2074-4af7-5e04-8e8a-5a5bd3762db3 |  | tickbox | Each node is accessible and its location identified by labelling
boolean | b83d69ab-961c-578f-933f-ba93569be547 |  | tickbox | Each node is fully insulated or isolated from contact with structural metal
boolean | 6f921e8e-12eb-5991-ac53-32f8006d70ba |  | tickbox | Each node is numbered and identified to identify the location of the EP junction
boolean | 51f9f7ba-a713-533b-aca3-25ab712a5e60 |  | tickbox | 4.4.1 - Confirm earthing has been carried out in accordance with the requirements of this Clause and the requirements of AS/NZS:3000
boolean | 9c4b61bf-d06e-5441-9a58-23f36cec5dab |  | tickbox | The EP junction is identified to identify the number of nodes connected
checkpoint-status |  |  | checkpoint | 4.4.2.4.1 - Confirm inspection and testing that the following socket-outlets conforming to Clause4.4.2.4.1 are connected to an EP junction or node
checkpoint-status |  |  | checkpoint | All socket-outlets that are accessible anywhere in the cardiac-protected electrical area without using a key or a tool, including those that are mounted on permanently installed electrical equipment and are available for general use
checkpoint-status |  |  | checkpoint | All socket-outlets that conform with AS/NZS:3112 or AS/NZS:60884.1, or both, and are located within 5.0m of the entrance to the cardiac-protected electrical area and accessible without the use of a key or tool in any room, corridor, etc,., opening directly off the cardiac-protected electrical area
checkpoint-status |  |  | checkpoint | Confirm that these outlets are only connected by one EP earthing system
checkpoint-status |  |  | checkpoint | Socket-outlets that are installed outside cardiac-protected electrical area but are used to supply medical electrical equipment
checkpoint-status |  |  | checkpoint | 4.4.2.4.1 - Confirm earthing in accordance with AS/NZS:3000
boolean | 80e73a03-dc37-520c-9373-5a06e099bdb7 |  | tickbox | Permanently installed cord extension sockets that are part of a medical electrical equipment system and will not accept common 10A plugs
boolean | f622eba3-0ca3-552c-be15-df55536b1cc3 |  | tickbox | Earth pin of socket-outlets for clocks
checkpoint-status |  |  | checkpoint | 4.4.2.4.2 - Confirm that the protective earthing conductors used to connect socket-outlets to the EP junction or node is insulated and segregated from contacting other conductive items except at the EP junction
checkpoint-status |  |  | checkpoint | Check the resistance between the earth pin of the socket-outlet and the EP junction or node is <+0.1 Ohms using a four-wire milliohm measuring device
checkpoint-status |  |  | checkpoint | 4.4.2.5 - Confirm by inspection and measurement that the following (if within patient environment) are directly earthed to the EP junction or node with a resistance of <+0.1 Ohms:
boolean | e9f3ab61-58b6-5d8b-80ee-e4a5c29c8960 |  | tickbox | The protective earthing terminal of permanently installed Class1 electrical equipment that is accessible within patient environment
boolean | 79a150da-cd8e-5b81-9799-59ee4f166fa9 |  | tickbox | Metal enclosure containing socket-outlets
checkpoint-status |  |  | checkpoint | 4.4.2.6 - Confirm by inspection and measurement that the following (if within patient environment) and measure <1 Mega Ohm with respect to the EP junction or node are directly earthed to the EP junction or node with a resistance of <=0.1 Ohms
checkpoint-status |  |  | checkpoint | Medical gas outlets and water taps contact reticulated metal services such as medical gas, water or drainpipes, the reticulated metal services etc
checkpoint-status |  |  | checkpoint | Accessible fittings such as hinged window frames or lift-out air-conditioning registers, etc
checkpoint-status |  |  | checkpoint | 4.4.2.7 - Confirm inspection (except for EP junctions) that all joints are as per below
boolean | e5bfad28-5264-52f5-8719-2cf7840f52e3 |  | tickbox | Fully insulated or isolated from contact with structural metal
boolean | 8c83dfd5-6b13-513c-b472-bb670af62a7b |  | tickbox | Effected so that conductors forming part of the equipotential earthing systems are not joined in tunnel connectors in which a single screw bears directly on the conductors
checkpoint-status |  |  | checkpoint | 4.4.2.8 - Confirm where EP junction is readily accessible within the cardiac area it is identified
boolean | f5ce1723-e3ac-5481-b5c8-e7777740401f |  | tickbox | EP Test Point
boolean | a4b3b273-67c6-5991-beac-9c41af85f08b |  | tickbox | 0.1 Ohm Ep Earthing System
boolean | c30dafe5-d56a-5d91-949d-5c419eb0ad17 |  | tickbox | EP Junction
checkpoint-status |  |  | checkpoint | 4.4.2.9 - Confirm where the EP junction is not readily accessible in the cardiac-protected electrical area, a test facility is provided as per below
boolean | 31e3b408-1bef-5a96-bfa0-59e68b8316d1 |  | tickbox | Isolated from structural steel
boolean | cfcb72d1-0754-5661-bb7b-8c1e8f3a9620 |  | tickbox | Identified 'EP Test Point'
boolean | dbbd9fae-9381-55a6-b999-6d970d354809 |  | tickbox | Identified '0.1 Ohms EP Earthing System'
boolean | c456eda7-6b94-5c8e-be17-d7b640fd65f2 |  | tickbox | Indicates the location of the EP junction
checkpoint-status |  |  | checkpoint | 4.4.2.10 - Confirm that the EP test terminal between EP junction or node has resistance of <+0.01 Ohms
checkpoint-status |  |  | checkpoint | Confirm that the EP test terminal is not used for any other purpose
checkpoint-status |  |  | checkpoint | Confirm that the EP test terminal has separate individual return earths
checkpoint-status |  |  | checkpoint | 4.4.3 - Confirm return to earth distribution board supplying the cardiac-protected electrical area
checkpoint-status |  |  | checkpoint | Confirm each return earth is labelled correctly at the EP junction and the distribution board
checkpoint-status |  |  | checkpoint | Confirm each EP junction has separate individual return earths
checkpoint-group |  |  | section | Alterations & Repairs to Electrical Installations in Patient Areas
checkpoint-status |  |  | checkpoint | 6.2.1 - Confirm that every alteration of the electrical installation in an existing patient area conforms with all relevant provisions of the Standard
checkpoint-status |  |  | checkpoint | 6.2.3 - Confirm inspection within the last 12 months before carrying out any alterations
checkpoint-status |  |  | checkpoint | Confirm in-service sticker is current
checkpoint-status |  |  | checkpoint | 6.2.4 - Check % increase in socket-outlets. If 10% or more increase, then verify all socket-outlets in patient area conform with colour requirements
checkpoint-status |  |  | checkpoint | 6.2.5.1 - Confirm EP wiring system as per below
boolean | 2b468683-a465-58e3-8971-1fbbda0129d8 |  | tickbox | EP junction accessible
boolean | afa9490c-5513-580f-a384-a61a398b2f28 |  | tickbox | EP test point labelled
checkpoint-status |  |  | checkpoint | Confirm the rating of the new fixed electrical equipment
checkpoint-status |  |  | checkpoint | 6.2.5.2 - Conformance is checked by confirming or actioning Items (a) to (c) of Clause 6.2.5.1
checkpoint-status |  |  | checkpoint | 6.2.5.3 - For the reclassification of a cardiac-protected electrical area to a body-protected electrical area, verify the below
boolean | a6468bc9-64da-55e4-adec-9a25d0661099 |  | tickbox | Conformance with Sections 2 & 3, except that, the requirement of Clause 2.4.1.3 for a claner's outlet to have a dedicated circuit need not apply
boolean | 0369a102-e4fd-5e87-9b4c-4c3d3ca9a31a |  | tickbox | All EP studs or EP receptacles removed
boolean | e44f5af5-78c6-5342-b3ee-f474723036f0 |  | tickbox | Re-certification as a body-protected electrical area in accordance with Clause 2.13
boolean | 5b5accc0-5d66-5dc0-a20f-80f3855589b2 |  | tickbox | Identification in accordance with Clause 2.12
checkpoint-group |  |  | section | Repairs
checkpoint-status |  |  | checkpoint | 6.3.1 - If the patient ares is not sign posted as a cardiac-protected electrical area or a body-protected electrical area, the repairs may only be completed when the patient area meets the requirements of this Standard
checkpoint-status |  |  | checkpoint | 6.3.2 - Confirm that the repair is only an equivalent fitting replacement and not the replacement for the fixed electrical equipment
checkpoint-group |  |  | section | 7.1, 7.2. 7.3 - Identification of Patient Areas
checkpoint-status |  |  | checkpoint | Confirm that sign is correct size, affixed in correct location, correctly completed, dated and sighted and the tester clearly identified
checkpoint-status |  |  | checkpoint | Where alterations have occurred, confirm addition of label stating this and indicating the date, name and organisation responsible
checklist-sectioned |  |  | checklist | AE-ITCX-026 AS:3003- Appendix F Cardiac Protected CL (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-026 AS:3003- Appendix F Cardiac Protected CL (Rev 0 +Names) | b2a01e2f-accc-4b72-b852-f36c3c1baee6
checkpoint-group |  |  | section | Preface
checkpoint-status |  |  | checkpoint | Appendix F: Summary of Information - Pass once confirmed
label | 87cfd4bd-291a-5252-846b-77e7e1b7ee12 |  | note | Routine inspection checklist for Cardiac-Protected electrical areas
label | 86cddc8c-0349-5b90-8a80-a300ec94a311 |  | note | .. ..
label | 7a789cd7-eb0b-594b-8b6c-bf9a0bb1fa77 |  | note | This checklist shall be used in accordance with Clause 8.3.7
label | ddc7a5a3-7b66-5aa6-b33b-85a0f47829cb |  | note | Note: The checklist may be in a different format and may be recorded electronically
checkpoint-group |  |  | section | Inspection & labelling
checkpoint-status |  |  | checkpoint | 8.3.1.1: Inspection - All electrical equipment and fittings in good condition
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Circuit identification visible and intact on each
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Relevant electrical points labelled to identify associated RCDs
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Circuit identification visible and intact on each LIM
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Relevant electrical points labelled to identify associated LIMs
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Overload monitors labelled with alarm setting
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Socket-outlets protected by RCD labelled 'RCD PROTECTED'
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Socket-outlets protected by isolating transformers labelled 'ISOLATING TRANSFORMER PROTECTED'
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Socket-outlets intended for cleaning purposes labelled 'CLEANING PURPOSES ONLY'
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Visible
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Labelled with current inspection date
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Labelled with identity of authorised person
checkpoint-status |  |  | checkpoint | 8.3.1.2: Labelling - Body-protected electrical area sign - Labelled with next test date
checkpoint-group |  |  | section | 8.3.1.3: Socket-Outlets
checkpoint-status |  |  | checkpoint | Socket-outlets coloured according to type of supply
checkpoint-status |  |  | checkpoint | If RCD protected, power-available indicator operational
checkpoint-status |  |  | checkpoint | Number of socket-outlets and permanently wired electrical equipment protected by RCD does not exceed 12
checkpoint-status |  |  | checkpoint | On indicator light operational, if present
checkpoint-status |  |  | checkpoint | Socket-outlets double-poled if protected by a transformer-isolated supply
checkpoint-status |  |  | checkpoint | All socket-outlets used for medical electrical equipment or installed below 2.3m protected by LPD
checkpoint-status |  |  | checkpoint | Confirm that when a fault is applied to each socket-outlet within patient area or within 5.0m of entrance of the patient area, the RCD trips
checkpoint-status |  |  | checkpoint | Confirm that when a fault is applied to each socket-outlet within patient area or within 5.0m of entrance of the patient area causes a response on LIM
checkpoint-status |  |  | checkpoint | Confirm that RCDs do not protect socket-outlets in another patient location
checkpoint-group |  |  | section | 8.3.2: Earthing
checkpoint-status |  |  | checkpoint | Confirm that the earth pins of all socket-outlets below 2.3m are earthed to less than 1.0-Ohm with respect to EP junction or node or other electrical equipment
checkpoint-status |  |  | checkpoint | Confirm that the earth pins of all socket-outlets within 5.0m of entrance to patient area are earthed to less than 1.0-Ohm with respect to EP junction or node or other electrical equipment
checkpoint-status |  |  | checkpoint | Confirm that all permanently wired electrical equipment with conductive parts below 2.3m are earthed to less than 1.0-Ohm with respect to EP junction or node or other electrical equipment
checkpoint-group |  |  | section | RCD
checkpoint-status |  |  | checkpoint | 8.3.3.2: RCD Sensitivity for Australia - Confirm that the RCD trips between 4.5-10.5 mA
checkpoint-status |  |  | checkpoint | 8.3.3.3: RCD Tripping times for Australia - Confirm this by carrying out at least two such tests
text | bbf3e667-a145-5cdf-b4aa-bf330e2d814a |  | textbox | Record the longest tripping time (ms)
checkpoint-status |  |  | checkpoint | 8.3.3.5: RCD Supply available indicators - Confirm that they are operational
checkpoint-status |  |  | checkpoint | 8.3.3.6: Audiovisual RCD Trip Indicators - If applicable, confirm that they are operational
checkpoint-group |  |  | section | 8.3.4.1: Prospective Hazard current
checkpoint-status |  |  | checkpoint | Ensure PHC is less than 2.00mA when no electrical equipment is plugged in
label | 3851291d-d10e-57f9-8b81-69d3fcd4e68c |  | note | For routine testing, the PHC under normal conditions of operation shall be verified by applying the following process to each transformer Line Isolation Overload Monitor (LIOM)
checkpoint-status |  |  | checkpoint | All electrical equipment are disconnected from the supply
checkpoint-status |  |  | checkpoint | The current flowing through a low impedance ammeter connected between one isolated supply conductor and earth is noted
label | b392f4c1-17d6-5b6b-ae49-8fa8a6d2f9c2 |  | note | The test is repeated for the other isolated supply conductor. The larger of the noted values is the prospective hazard current. It shall be less than 2mA
checkpoint-status |  |  | checkpoint | The prospective hazard current of the supply is recorded in the commissioning checklist
checkpoint-group |  |  | section | 8.3.4.2: LIM Prospective Hazard Current Alarm
checkpoint-status |  |  | checkpoint | Confirm that the LIM alarms between 4.5-10.5mA
text | 408c29f4-e2ec-5755-8186-c0e70af1f00e |  | textbox | Record alarm current (mA)
checkpoint-group |  |  | section | 8.3.5: Overload Monitors
checkpoint-status |  |  | checkpoint | Confirm that a load of 110-120% of transformer rated current causes the alarm to activate in 3-5 Seconds
checkpoint-group |  |  | section | 8.3.6: Uninterruptible Power Supplies (UPS)
checkpoint-status |  |  | checkpoint | Confirm that UPS status indicator performance is routinely verified
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Checks completed to specification/drawings - Area left clean & tidy
label | 84d306d1-e82c-5c43-a2d2-39cfa72afdb6 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | b2209c37-865a-50da-9edd-98d211718432 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 0fd5a48e-9ccc-5cf5-8bf8-5432c75df647 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 56a78440-f3d7-54fa-8223-86ea05b899a8 |  | textbox | Other (Specify here)
label | a355d481-3171-5fba-9dce-776485f4c357 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AE-ITCX-020 - MATV Backbone Rough in, Testing & Panel Fit Off (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-020 - MATV Backbone Rough in, Testing & Panel Fit Off (Rev 0 +Names) | b50b3654-388a-4ea2-95fa-288ac89015c1
checkpoint-group |  |  | section | No.1
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | 6be4bd86-5033-5f64-86dc-37093bbb1bde |  | textbox | MATV Backbone Cable Type
text | 8d856db1-736d-5360-a456-57cc6f2952c4 |  | textbox | From MATV Panel
text | d42be38e-524d-569d-ba44-4c2f32016356 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.2
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | 288aa08c-b884-597e-ad26-46021607c448 |  | textbox | MATV Backbone Cable Type
text | c8e71ea2-4ef7-5fab-b7b4-43419cc902a3 |  | textbox | From MATV Panel
text | c3ec1622-6b07-57dc-a6b2-578062d508d4 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.3
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | a057a6ef-3357-5ea9-bcc1-846a37184851 |  | textbox | MATV Backbone Cable Type
text | 4355adc2-4512-54cf-9363-707e5ae4f7e5 |  | textbox | From MATV Panel
text | ce224a72-93f9-5cb2-a45f-ff88542f6e2f |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.4
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | 71ed4b76-e0f6-5727-a380-79c876bdd398 |  | textbox | MATV Backbone Cable Type
text | b99eefe2-f0e2-5b5e-827e-a3e8fd04be29 |  | textbox | From MATV Panel
text | 100f9bb4-60f6-5795-a264-e4551c215ee0 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.5
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | ebf37003-989f-5e60-9e4f-5b6d7ba653c3 |  | textbox | MATV Backbone Cable Type
text | 376c56d4-464c-5107-8052-9d6cb7985989 |  | textbox | From MATV Panel
text | 521d5b8b-1eeb-5541-bd29-88a251ff4fd3 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.6
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | 8270ff62-7a89-5cd9-9470-4f126d79bc8f |  | textbox | MATV Backbone Cable Type
text | 0937c4be-0a84-513a-887a-434ad1d4185a |  | textbox | From MATV Panel
text | ef02e519-1d89-5807-884e-b87b69065344 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.7
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | 3635db71-ce78-5ca9-bd29-b7715e4c7ecf |  | textbox | MATV Backbone Cable Type
text | 6cdef5b6-6ec2-51d6-a189-15fbc4e21a7e |  | textbox | From MATV Panel
text | 329cdae7-9fdc-5f30-970a-2e9a33975eba |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.8
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | b5993ae4-d277-50d2-b6eb-1887ad8d65f5 |  | textbox | MATV Backbone Cable Type
text | 999187cf-f2a3-5712-a847-fd77d8c841a1 |  | textbox | From MATV Panel
text | 1108ec09-38e5-5cd3-870b-891e755af376 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.9
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | 1e41590c-b268-5367-a50f-920c0a940327 |  | textbox | MATV Backbone Cable Type
text | 2bf1ecd8-d2e0-554b-9d2d-33b0fa83ade5 |  | textbox | From MATV Panel
text | fa5d2cf0-d072-592e-98cc-9317041f06f8 |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | No.10
checkpoint-status |  |  | checkpoint | MATV Backbone Instalaltion completed
text | b5bc6574-5a65-516a-b4d4-5035740dfe55 |  | textbox | MATV Backbone Cable Type
text | b19cea66-3897-5324-88ed-b6cb64b3c4ec |  | textbox | From MATV Panel
text | 405c1bbe-df08-53bd-af88-4886d2bc3c7f |  | textbox | To MATV Panel
checkpoint-status |  |  | checkpoint | Tested and Labelled
checkpoint-status |  |  | checkpoint | MATV Panel Installed (Level)
checkpoint-status |  |  | checkpoint | MATV Panel Fit-Off Completed
checkpoint-status |  |  | checkpoint | MATV Panel Labelled
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Backbone Works completed to specification/drawings - Area left clean & tidy
label | f76592ef-4cfd-5579-a379-ed67251698ed |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
select | fa5cfcc3-535e-5e80-b31e-31a5c566afd8 |  | dropdown | Backbone by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 33f49746-0492-5ad8-ad12-cbd8c0a83345 |  | textbox | Other (Specify here)
text | 141cda00-8402-5a96-a527-9b4a97d02f27 |  | textbox | Witnessed by
label | 53b33678-6028-584a-96bd-cf8d7839071f |  | note | Signature Sign-Offs - Attach signature(s) below
label | 9a5bed5b-7d37-54fb-8222-8a9bf94334de |  | note | .. ..
select | cd616738-205b-52c4-8965-e341246a5a68 |  | dropdown | Panel Fit-Off by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 28305ba6-1cb4-538a-9029-b4302c4e2f84 |  | textbox | Other (Specify here)
text | ff24b970-ba28-5f4a-9fe3-cfb2ad1a7939 |  | textbox | Witnessed by
label | c078705c-45aa-59a7-9f18-2e03abf6f4a5 |  | note | Signature Sign-Offs - Attach signature(s) below
label | 61f6ebc4-d25c-5da6-99fd-258756de079c |  | note | .. ..
select | 61751f33-4d82-5f94-bc13-e60fefecaaf3 |  | dropdown | Testing by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | eea8dc22-ad70-55e1-aecd-4d1d558cc757 |  | textbox | Other (Specify here)
text | cf9dda02-8804-5373-a7ca-1884dcd56900 |  | textbox | Witnessed by
label | 79465711-8ebf-5ae0-99f7-8f49b32f9152 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | DETAILS & 10x - AF-502 - Electrical Services commissioning Sheet - Protective Device Details and RCD Results (Rev 0 +Names) |  |  |  |  | Yes | DETAILS & 10x - AF-502 - Electrical Services commissioning Sheet - Protective Device Details and RCD Results (Rev 0 +Names) | b6b39946-19e8-49b2-b11b-5b14b9f4272a
checkpoint-group |  |  | section | Electrician Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | f888b696-3799-5fff-a328-dd8aff05f778 |  | textbox | Test Date
select | 00251f40-4378-5598-a579-5463ac8a312e |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 1a28f1b9-19c8-51ac-83ef-3cb42a01bf67 |  | textbox | Other (Specify here)
boolean | cabe9ecf-9b51-5d9b-946b-0b203209b2fe |  | tickbox | Signature added below
checkpoint-group |  |  | section | Circuit Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | bd5aa1de-82a1-5ce1-81c3-f54b55376b8b |  | textbox | Designation of service
text | 2cc9eb0e-9643-5440-9045-4bccd6e5a65e |  | textbox | Location of Service
checkpoint-group |  |  | section | No. 1
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 816a3730-b4e7-524e-8493-c8f81858f26d |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | c735973f-c9c3-50aa-9787-7416367c54c7 |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 6482774d-3b96-513b-bc65-6e6e8cfc9581 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | c53a04b8-2ea1-517c-9728-2e3ce21f2f84 |  | textbox | 0.Deg (P/F)
text | 2d399485-5e97-55c2-b8ac-ab1722cda47f |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | ddfeb9f6-1748-5642-9221-afde63a9649f |  | textbox | 0.Deg
text | fa23d682-687d-5749-a219-4016949d4993 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | e03d4a4f-d30f-5e49-9cb1-6f41ef5879d4 |  | textbox | 0.Deg
text | 13ba15c5-5c77-5552-b43e-6ecfcdf343ed |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 64aecabf-da23-5f84-b8c1-cc034646e8b9 |  | textbox | 0.Deg
text | 5710dfce-e6ae-5269-9753-4a8218426dc7 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 78d9a2e1-ec24-5242-a0da-5372252c0e14 |  | textbox | Action taken
checkpoint-group |  |  | section | No. 2
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 04730a7f-44b8-535b-88ab-81da204142a6 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | 8fe48733-583a-5f4d-92a0-e93b41a3cd2b |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 08175834-7d29-51e5-8de3-20e9654d6c0c |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | d3282640-978e-5176-a280-1e33f8c33911 |  | textbox | 0.Deg (P/F)
text | 5090e529-0459-5da4-b99f-e49e10a7fff1 |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 52a1d7ae-80a7-556f-bb26-9f6c9d7ea9cb |  | textbox | 0.Deg
text | cf2f17a4-bf08-576a-8428-a98c1ff4ab98 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 885dff8a-2713-5673-80b5-855b7feee0a3 |  | textbox | 0.Deg
text | 39ad61bb-ad01-5b15-863e-5109476444c5 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 6a0ecd67-18fe-5d48-9730-2048137497b9 |  | textbox | 0.Deg
text | ca3e661d-3d75-5576-8a90-699983083bd7 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | a045572f-3fa9-53d6-a9ad-50d2e338ed59 |  | textbox | Action taken
checkpoint-group |  |  | section | No. 3
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 8abe8ae5-233a-558c-a46f-a99f303bdc83 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | c8fd0a3c-8c30-5013-a587-4ba731c3608b |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 5bc0bd6d-9211-5de9-a7df-46785306660d |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 74bf99b9-c17c-54e9-a2a8-d7d1b85472f5 |  | textbox | 0.Deg (P/F)
text | e87f5fc7-b8f4-5a7d-9a1f-3fe0566fdccb |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 10185f23-19af-5009-a282-9630ac156da7 |  | textbox | 0.Deg
text | 5e5c11ba-5b0f-5e31-a1a3-3698391f84e9 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 89dc3286-2952-56f4-bdd3-421d398236ca |  | textbox | 0.Deg
text | c22739bb-0c6f-5a76-bfc8-c7de31961960 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | f8978758-88ea-5cec-a813-ed020d4f109b |  | textbox | 0.Deg
text | b3c0c689-e4b5-5eb2-ba81-fcb84ad9d435 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | c9c25731-d61a-541f-84d7-1bb82e092522 |  | textbox | Action taken
checkpoint-group |  |  | section | No. 4
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | e9e3cdd9-877f-5969-8d9e-51bf491f1499 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | a5df6b65-280d-5c23-bfdd-d59e54c90b43 |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | e099fa23-09d6-5b1c-b670-7836fa0c8ac0 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 31a42e94-1c2e-5255-a07b-b53287602fcc |  | textbox | 0.Deg (P/F)
text | 1a1d224b-8104-5808-875e-a94eb7f8104d |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 9d0f1521-fbc8-5cab-abd7-4af15796cfef |  | textbox | 0.Deg
text | 5dc03d19-62db-5785-ad6d-b5d5dcc3631a |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | fbca82ea-75d3-5212-b321-5878b15f6ba6 |  | textbox | 0.Deg
text | 596c80cf-37b0-5de0-9595-adf85da176e0 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 6eabcacb-69aa-5552-854e-cc11f432c662 |  | textbox | 0.Deg
text | aec28595-2fd5-5f8f-a67e-eaaaeb6c2ddf |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | dc6917bd-48f9-5fac-9d12-cf7c1172bb45 |  | textbox | Action taken
checkpoint-group |  |  | section | No. 5
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 00ae6bef-f2e2-5747-a86e-1b36684babe6 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | 4c1546f4-cef7-5759-80d6-b1c5929c29ec |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 2421a6f8-2018-57a3-8a67-4b1116e94d50 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 3b56f5be-58dc-5eb2-a3bf-e2d40fed2c81 |  | textbox | 0.Deg (P/F)
text | 0a3d7cb3-b2ee-5dc9-9a6c-2d84c78e04f6 |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 8ca1b623-e767-5ede-871a-e67431b63dac |  | textbox | 0.Deg
text | e947e806-e912-54a1-a98d-083232d45a06 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | cf2794a4-3218-50d1-9ba6-04d8b4176650 |  | textbox | 0.Deg
text | 343e0aab-1950-5171-8ceb-db007be7fb88 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 877b1698-4402-5d0b-937f-5592aa2a3bbd |  | textbox | 0.Deg
text | 47e2760b-23d8-5fbd-8986-dc596a1c3640 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 61bac33d-934d-5659-a2de-19e476d0bba2 |  | textbox | Action taken
checkpoint-group |  |  | section | No. 6
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 6dba3d3d-fc34-52f1-b3ae-b6802321c60e |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | db0e07e1-da22-57c9-abf0-7937d42f6ea5 |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 948f98dd-9aa7-5be7-b647-d81886e49411 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 2eb0cd90-5d74-5cb1-b620-3804222704ed |  | textbox | 0.Deg (P/F)
text | b0306d17-a253-5155-bfd6-3c838169ecb0 |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | a863ddb3-1f43-510d-9d3c-53287ccfcebf |  | textbox | 0.Deg
text | 80954be3-bff8-50bc-a9c7-c12d5599604c |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 14e55238-37dd-5a7b-a5ee-ddb49c9e47d4 |  | textbox | 0.Deg
text | 7d41fcf1-bd9f-57a1-94cd-bcfca737a28c |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 820f6195-1d20-5f0f-8b86-7a74d51caf05 |  | textbox | 0.Deg
text | 8992a921-8049-55d5-b746-49d29d55d164 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | f369d1ba-3436-503b-b772-abb8fd77874e |  | textbox | Action taken
checkpoint-group |  |  | section | No. 7
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 2475a460-bea1-5ce1-9b2b-c462744d6e8e |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | d2c4007d-c283-50c5-a89d-ca95b8803cc8 |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 27f418a3-c4c7-5241-8150-cbff814a5c7b |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 8bb6be86-9c3f-5699-ae83-38fa3078de50 |  | textbox | 0.Deg (P/F)
text | 73f033ee-7de3-5e59-a24f-59e7a7959f9b |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | f5379b3b-a47a-5e80-9823-ac973bd19a40 |  | textbox | 0.Deg
text | 993d7811-3604-5ec3-8cf5-e6c3a0d43dba |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | c6ecbd2f-b5ee-5b09-8ee0-7cb4bf3ea96a |  | textbox | 0.Deg
text | 544a0fa3-9356-5a3a-8b08-a934e5839673 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 965c9d64-4fca-579d-9e8d-8d2780e67c25 |  | textbox | 0.Deg
text | aa01bd11-8fd6-52c3-9ea2-c59092568d48 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 09d6c03c-1bbd-5d32-8e5d-6423871f3c2d |  | textbox | Action taken
checkpoint-group |  |  | section | No. 8
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 8c9622f0-4e3f-51b8-bbdf-c2fd0a8b35a0 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | 87dbd672-5515-56fe-8ff1-ee7a3b3c6237 |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | f05dd67b-96c3-5615-98a4-efe4e2100b48 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 8b0b0066-8e0e-5d87-8911-2be3b556af3c |  | textbox | 0.Deg (P/F)
text | 2bce270e-6c88-5881-810c-3cf577e1d863 |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 7730344d-d11a-5752-bc79-e5f033b6ca13 |  | textbox | 0.Deg
text | 2df9b7b3-31e3-506f-b286-c60024640815 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 8e9203bb-ad23-5409-9918-373af6dd3d2d |  | textbox | 0.Deg
text | 67b647ee-19f8-527b-99f0-b1ad0e7ffae0 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 1d5d1600-a689-543d-ae17-136f9512fbe9 |  | textbox | 0.Deg
text | 67550c7a-eb02-50c6-8df2-c15e634c6889 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | ca774da4-d2fb-5b23-b3df-0ca444ab4c9a |  | textbox | Action taken
checkpoint-group |  |  | section | No. 9
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 3bf17656-3a22-5454-9948-7ba601eccb9c |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | 1866eadb-dd98-565c-9e48-508b293b9f1e |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | aea7eecc-0a35-52f8-b4a7-ba27298efeeb |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 1d169702-2bfc-5b7c-8e09-8266438ba77c |  | textbox | 0.Deg (P/F)
text | 51255aef-b7bc-5098-a768-0e5bc0b73f3c |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | c37f9fd7-4be2-53d1-9667-7e9582251af2 |  | textbox | 0.Deg
text | 4af8e808-0cd5-5fcf-9521-87e0a36e4b01 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 96da161f-c129-5837-bff4-4b488e284881 |  | textbox | 0.Deg
text | d5b357e4-7ee8-5412-926e-f1beb3cce950 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 8249b724-93c5-586c-974e-62248ac13f54 |  | textbox | 0.Deg
text | c3a34888-c389-58f9-b8fb-5bb0f05bec88 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | f53dccdc-60a1-5ba8-9a1a-ecf09d45b2e8 |  | textbox | Action taken
checkpoint-group |  |  | section | No. 10
checkpoint-status |  |  | checkpoint | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | a03198b6-29dd-5c8b-b05a-fe828032f650 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
select | 5dc4bfd5-80f1-56bc-9452-cd1ea7d6a0ad |  | dropdown | RCD Type - Where applicable | A, AC, B, F
text | 3dd65c1c-ffa5-5d9c-8d0c-71483cfdc2c7 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 95cbdeba-f074-5bda-9243-b8576ae556ac |  | textbox | 0.Deg (P/F)
text | 17d3b910-a472-5e5f-ae60-14c411c9eb4c |  | textbox | 180.Deg (P/F)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 2c2e44e9-51da-5b56-854e-e95b4e767546 |  | textbox | 0.Deg
text | 5529588c-6eff-57e2-bdbb-7e061622af5b |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <150ms - x2 Trip Time (ms)
text | 817aa8ec-e63d-58d0-b3d9-617d5e18bcec |  | textbox | 0.Deg
text | a9b6e034-85e4-5707-b92d-de0c0d1b3e97 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | c4d9b8ad-1a6c-54dd-a95d-bfbe63d0212d |  | textbox | 0.Deg
text | bbc959f5-be73-5477-a961-1dda36cf7871 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | ab1efd45-f839-5d45-b4d4-17bb96351218 |  | textbox | Action taken
checklist-sectioned |  |  | checklist | AE-ITCX-003 - Mandatory Test Results For Construction Wiring (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-003 - Mandatory Test Results For Construction Wiring (Rev 0 +Names) | c58492ed-2fab-440b-bc38-434873ad0d30
checkpoint-group |  |  | section | Electrician Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | c24c9c11-2d84-538d-9af0-74dfb88258a4 |  | textbox | Equipment being Energised
select | cb8fffb7-38d4-59cc-b167-153c90120089 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 5b335dba-110b-51e7-93f3-da3aa671e3cd |  | textbox | Other (Specify here)
boolean | 32049fb5-1a0b-5a89-89cf-6b18aac4f1e1 |  | tickbox | Signature added below
checkpoint-group |  |  | section | Temporary Board Visual Inspection
checkpoint-status |  |  | checkpoint | All cables secured and protected appropriately
checkpoint-status |  |  | checkpoint | All cables identified with Construction Wiring tape
checkpoint-status |  |  | checkpoint | Switchboard is structurally sound
checkpoint-status |  |  | checkpoint | Appropriate signage in place
checkpoint-status |  |  | checkpoint | All holes filled with stops
checkpoint-group |  |  | section | Temporary lighting visual inspection
checkpoint-status |  |  | checkpoint | All cables secured and protected appropriately
checkpoint-status |  |  | checkpoint | All cables identified with Construction Wiring tape
checkpoint-status |  |  | checkpoint | Appropriate number of emergency lights installed
checkpoint-status |  |  | checkpoint | All lighting plug bases terminated
checkpoint-status |  |  | checkpoint | Light fittings in serviceable condition with wire-guards or plastic diffusers
checkpoint-group |  |  | section | Test Results
checkpoint-status |  |  | checkpoint | Test Results - Pass once complete
text | 45e6b46a-16a1-5f99-957b-805abbab54ea |  | textbox | Insulation Resistance (Mega Ohms)
button | a86442c5-dd3b-5d2c-b361-c090f42fbabd |  | button | Result | Pass, Fail
label | c8fcdfd9-5201-507b-b906-a6f4c3f8c78d |  | note | .. ..
text | a3846f43-7a44-5247-b30b-f87c386ca782 |  | textbox | Earth Resistance & Continuity (Ohms)
button | 66bb1ce7-0d92-5d17-b9ff-a850736569ed |  | button | Result | Pass, Fail
label | 6f89cb6d-860d-56f6-9070-6a297a25f30c |  | note | .. ..
text | fd80879a-458d-52e1-8242-37dd5509ca23 |  | textbox | Polarity
text | 7a0fa3e3-ccc6-5b40-966b-c1e96aea24d2 |  | textbox | Earth loop impedance
button | 0aa92a90-8d5b-5638-86cd-0c451b9671ec |  | button | Result | Pass, Fail
checkpoint-status |  |  | checkpoint | RCD Time trip test completed
checkpoint-status |  |  | checkpoint | Correct circuit connection
checklist-sectioned |  |  | checklist | AE-ITCX-025 AS:3003 - Appendix E Body Protected CL (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-025 AS:3003 - Appendix E Body Protected CL (Rev 0 +Names) | c58b5772-d09c-40d7-aad7-fb1117abb311
checkpoint-group |  |  | section | Preface
checkpoint-status |  |  | checkpoint | Appendix E: Summary of Information - Pass once confirmed
label | 8b23527d-7cee-56e6-bbc8-78464d049891 |  | note | Routine inspection checklist for Body-Protected electrical areas
label | 3d768a1e-2f8c-5bc0-9806-ff8b697b8afe |  | note | .. ..
label | 0a02c7ca-d7bc-5b0e-a791-6954a34e288c |  | note | This checklist shall be used in accordance with Clause 8.2.7
label | de85b62b-6261-58ef-888f-a5d200ea7286 |  | note | Note: The checklist may be in a different format and may be recorded electronically
checkpoint-group |  |  | section | Inspection & labelling
checkpoint-status |  |  | checkpoint | 8.2.1.1: Inspection - All electrical equipment and fittings in good condition
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Circuit identification visible and intact on each
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Protected points labelled as to which RCD protects them
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Circuit identification visible and intact on each LIM
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Overload monitors labelled with alarm setting
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Socket-outlets protected by RCD labelled 'RCD PROTECTED'
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Socket-outlets protected by isolating transformers labelled 'ISOLATING TRANSFORMER PROTECTED'
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Socket-outlets intended for cleaning purposes labelled 'CLEANING PURPOSES ONLY'
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Still Visible
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Labelled with current inspection date
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Labelled with identity of authorised person
checkpoint-status |  |  | checkpoint | 8.2.1.2: Labelling - Body-protected electrical area sign - Labelled with next test date
checkpoint-group |  |  | section | Socket-Outlets
checkpoint-status |  |  | checkpoint | 8.2.1.3.1: Socket-outlets coloured according to type of supply
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: If RCD protected, power-available indicator operational
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: Number of socket-outlets and permanently wired electrical equipment protected by RCD does not exceed 12
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: On/Off luminous indicators operational, if applicable
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: Socket-outlets double-poled if protected by a transformer-isolated supply
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: All socket-outlets below 2.3m protected by LPD
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: Confirm that when a fault is applied to each socket-outlet within patient area or within 2.0m of entrance of the patient area, the RCD trips
checkpoint-status |  |  | checkpoint | 8.2.1.3.2: Confirm that when a fault is applied to each socket-outlet within patient area or within 2.0m of entrance of the patient area causes a response on LIM
checkpoint-group |  |  | section | 8.2.2: Earthing
checkpoint-status |  |  | checkpoint | Confirm that the earth pins of all socket-outlets below 2.3m are earthed to less than 1.0-Ohm
checkpoint-status |  |  | checkpoint | Confirm that the earth pins of all socket-outlets within 2.0m of entrance to patient area are earthed to less than 1.0-Ohm
checkpoint-status |  |  | checkpoint | Confirm that all socket-outlets used by medical electrical equipment accessible above 2.3m are earthed to less than 1.0-Ohm
checkpoint-status |  |  | checkpoint | Confirm that all permanently wired electrical equipment with conductive parts below 2.3m are earthed to less than 1.0-Ohm
checkpoint-group |  |  | section | RCD
checkpoint-status |  |  | checkpoint | 8.2.3.2: RCD Sensitivity for Australia - Confirm that the RCD trips between 4.5-10.5 mA
text | 881cb63c-0d37-58fa-9f5c-cd313eea9fb9 |  | textbox | Record the RCD sensitivity (may)
checkpoint-status |  |  | checkpoint | 8.2.3.3: RCD Tripping times for Australia - Confirm this by carrying out at least two such tests
text | 5deec8f9-a36c-5620-bea2-9d7b0a097783 |  | textbox | Record the worst case (ms)
checkpoint-status |  |  | checkpoint | 8.2.3.5: RCD Supply available indicator lights - If applicable, confirm that they are operational
checkpoint-status |  |  | checkpoint | 8.2.3.6: Audiovisual RCD Trip Indicators - If applicable, confirm that they are operational
checkpoint-group |  |  | section | 8.2.4.1: Prospective Hazard current
checkpoint-status |  |  | checkpoint | Confirm that the hazard current is below 2.00mA
text | b46dae46-41a2-59d0-bc7b-a4e87c74e739 |  | textbox | Record hazard current (may)
label | 6ffdfd5d-76cb-5f16-97a1-dd382508f5fb |  | note | For routine testing, the PHC under normal conditions of operation shall be verified by applying the following process to each transformer Line Isolation Overload Monitor (LIOM)
checkpoint-status |  |  | checkpoint | All electrical equipment are disconnected from the supply
checkpoint-status |  |  | checkpoint | The current flowing through a low impedance ammeter connected between one isolated supply conductor and earth is noted
label | d208f415-2311-5241-83fe-9e923609e0cf |  | note | The test is repeated for the other isolated supply conductor. The larger of the noted values is the prospective hazard current. It shall be less than 2mA
checkpoint-status |  |  | checkpoint | The prospective hazard current of the supply is recorded in the commissioning checklist
checkpoint-group |  |  | section | 8.2.5: Overload Monitors
checkpoint-status |  |  | checkpoint | Confirm that a load of 110-120% of transformer rated current causes the alarm to activate in 3-5 Seconds
checkpoint-group |  |  | section | 8.2.6: Uninterruptible Power Supplies (UPS)
checkpoint-status |  |  | checkpoint | Confirm that UPS status indicator performance is routinely verified
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Checks completed to specification/drawings - Area left clean & tidy
label | 200ff21a-241b-564e-9e0d-b8496f30765e |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 234e6f8e-7e84-5c2d-937e-92586a376037 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 9af89730-f5ec-5309-90dc-d83f0682fab1 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 1747212c-e073-500d-968f-79b838a3cd81 |  | textbox | Other (Specify here)
label | 05ed4d80-5875-51be-bcee-672cad2d6561 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AE-ITCX-021 - Temp Board Audit Form (Rev 0) |  |  |  |  | Yes | AE-ITCX-021 - Temp Board Audit Form (Rev 0) | c660196f-86e4-4c32-9892-d86b5101562f
checkpoint-group |  |  | section | Structural
checkpoint-status |  |  | checkpoint | Is insulated lead stand with board and in good condition
checkpoint-status |  |  | checkpoint | Is the insulation on the lead hook in good condition
checkpoint-status |  |  | checkpoint | Is the switchboard structurally sound
checkpoint-status |  |  | checkpoint | Does the main door close properly
checkpoint-status |  |  | checkpoint | Does the main door have the facility to be propped open
checkpoint-status |  |  | checkpoint | Is the chain to prevent the wind catching the door
checkpoint-status |  |  | checkpoint | Is the insulated bar in place
checkpoint-status |  |  | checkpoint | Do the flap-lock and door-lock work
checkpoint-status |  |  | checkpoint | Are all screws holding escutcheon covers in place
checkpoint-group |  |  | section | Signage
checkpoint-status |  |  | checkpoint | Is the main isolating switch identified
checkpoint-status |  |  | checkpoint | Are all C.B’s and R.C.D’s identified
checkpoint-status |  |  | checkpoint | Is 1.2m clearance signage in place
checkpoint-status |  |  | checkpoint | Is ‘Live Parts’ signage in place
checkpoint-status |  |  | checkpoint | Is KEEP CLOSED-RUN LEADS THROUGH BOTTOM sign on the door
checkpoint-status |  |  | checkpoint | Is the ID number of the board clearly visible
checkpoint-group |  |  | section | Electrical
checkpoint-status |  |  | checkpoint | Has all external wiring been removed?(not just cut off)
checkpoint-status |  |  | checkpoint | Do pole fillers cover all gaps
checkpoint-status |  |  | checkpoint | Are test points installed in the board
checkpoint-status |  |  | checkpoint | Is the 15amp GPO’s protected by a 25amp C/B
checkpoint-status |  |  | checkpoint | Are all holes in connection (J.Box) filled in/covered
checklist-sectioned |  |  | checklist | AE-ITCX-024 - Communications/Security Rack Installation QA (Rev 0) |  |  |  |  | Yes | AE-ITCX-024 - Communications/Security Rack Installation QA (Rev 0) | cc93efce-3a7f-4797-8ff9-cace2bf51436
checkpoint-group |  |  | section | QA ITEM 1 - Communications Rack
checkpoint-status |  |  | checkpoint | Is the communications riser ready for communications rack installation
label | f522d38d-7aa6-5ffa-ab34-2230dfb864e6 |  | note | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint-status |  |  | checkpoint | Does the communications rack match the approved technical data
checkpoint-status |  |  | checkpoint | Has the communications rack been installed in position as per the Appselec communications riser elevation shop drawings and floor plan layout
text | 7fa1ae94-9c58-514c-bfeb-4eda1421ae2e |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | Has the communications rack been fixed to the floor using appropriate fixings
checkpoint-status |  |  | checkpoint | Are the doors and side panels installed and free from damage
checkpoint-status |  |  | checkpoint | Does the communications rack comply with all the relevant clearances
label | 3e69dc1c-e4b1-5354-8d38-5603ab1eab36 |  | note | Are door swings and access to the communications rack unobstructed
checkpoint-status |  |  | checkpoint | Has the communications rack been permanently labelled with a traffolyte label or similar on the door
label | 6dd738ef-3a5e-5c5a-b756-be0afc3693e8 |  | note | Check that the label matches the communications rack layouts
checkpoint-status |  |  | checkpoint | Has the Appselec label/logo been fixed to the front of the communications rack
checkpoint-group |  |  | section | QA ITEM 2 - Communications Earthing Terminal (CET)
checkpoint-status |  |  | checkpoint | Has a CET been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth cable been terminated to the CET
label | e40cb272-5229-5d11-a995-f5e935ca604b |  | note | Refer to Communications SLD for earth cabling schematic
checkpoint-status |  |  | checkpoint | Has an earth bar been installed adjacent to/or within the communications rack and has a 6 mm2 green/yellow earth been terminated to the earth bar from the CET
checkpoint-status |  |  | checkpoint | Has the 6 mm2 green/yellow earth been identified and labelled with “Communications Earth” at the originating electrical distribution board
checkpoint-group |  |  | section | QA ITEM 3 - FOBOTS (Fibre Optical Breakout Trays)
checkpoint-status |  |  | checkpoint | Does the FOBOT match the approved technical data
checkpoint-status |  |  | checkpoint | Has the FOBOT been installed in the correct rack RU position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Has the FOBOT been labelled permanently with traffolyte label or similar
checkpoint-status |  |  | checkpoint | Has a service loop been provided in the optical fibre cable
checkpoint-status |  |  | checkpoint | Has the fibre port arrangement on the FOBOT been detailed and labelled
checkpoint-status |  |  | checkpoint | Do the fibre adapters on the FOBOT match the type of fibre being used
label | 31526f63-3fce-54c2-8dee-520bb76e15a9 |  | note | For example: aqua = multimode, green = singlemode. Adapters, pigtail connector colours must match, fibre cable type must match
checkpoint-status |  |  | checkpoint | Have fibre protective caps been installed on all fibre adapter ports
checkpoint-group |  |  | section | QA ITEM 4 - Cat 6/6A Patch Panels
checkpoint-status |  |  | checkpoint | Does the Cat 6/6A patch panels match the approved technical data
checkpoint-status |  |  | checkpoint | Have the Cat 6/6A patch panels been installed in correct rack RU position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Have the Cat 6/6A patch panel ports been labelled permanently with traffolyte label or similar
checkpoint-status |  |  | checkpoint | Have cable wrap-around labels been attached to each individual Cat 6/6A cable behind the patch panels
checkpoint-status |  |  | checkpoint | Have the Cat 6/6A patch panels been earthed with 2.5 mm2 green/yellow earth cable from the earth bar within the communications rack
label | 65aa3c99-9479-5e10-ad0b-04edc89c1df2 |  | note | Shielded patch panels only
checkpoint-group |  |  | section | QA ITEM 5 - Cable Management
checkpoint-status |  |  | checkpoint | Have horizontal cable managers been installed in the correct rack RU position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Have vertical cable managers been installed in the correct rack RU position as per the communications rack layout
checkpoint-group |  |  | section | QA ITEM 6 - Power
checkpoint-status |  |  | checkpoint | Has the correct power been provided for the communications racks
label | fbcaf199-867b-5852-b13c-7eff531cf29d |  | note | Check for captive outlets? Are there 2x or 1x? Are they 10A, 15A or 20A? Check the Appselec power floor layouts against the communications specification
checkpoint-status |  |  | checkpoint | Do the PDU’s match the approved technical data
checkpoint-status |  |  | checkpoint | Have the PDU’s been installed in position as per the communications rack layout
checkpoint-status |  |  | checkpoint | Have the PDU’s been plugged into the captive outlets/rack mounted UPS as detailed on the communications rack layouts
checkpoint-status |  |  | checkpoint | Have the PDU’s been labelled appropriately detailing the power source
label | 7468b23a-d3a3-5c96-b5ce-ef7f2a44bc75 |  | note | For example UPS supply (Generator backed) DB-XX
checkpoint-group |  |  | section | QA ITEM 7 - Rackmount UPS
checkpoint-status |  |  | checkpoint | Is the communications rack/riser ready for UPS installation
label | 9991e07e-4985-50ca-a5dd-30cdf5f2b9ef |  | note | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint-status |  |  | checkpoint | Does the UPS match the approved technical data
checkpoint-status |  |  | checkpoint | Has the UPS been installed in position as per the communications rack layouts
checkpoint-status |  |  | checkpoint | Has the UPS been labelled appropriately detailing the power source
label | 2b23ebf4-13d5-5d43-8e31-c311667aa3e7 |  | note | For example UPS supply (Generator backed) DB-XX
checkpoint-status |  |  | checkpoint | Has any associated Battery Backup for the UPS been installed as per the communications rack layouts and is it connected
checkpoint-status |  |  | checkpoint | Has the UPS been commissioned? Refer to UPS ITP for commissioning details
checkpoint-group |  |  | section | QA ITEM 8 - Active Equipment
checkpoint-status |  |  | checkpoint | Is the communications rack/riser ready for Active Equipment installation
label | f9f9f4b6-31fe-5045-aabf-ebbfbf89bca1 |  | note | Riser must be in a finished dust-free state, finished floors, cable tray installed, clean and permanent doors installed
checkpoint-status |  |  | checkpoint | Does the Active Equipment need to be configured prior to installation within the communications rack
checkpoint-status |  |  | checkpoint | Does the Active Equipment match the approved technical data
checkpoint-status |  |  | checkpoint | Has the Active Equipment been installed in the correct rack RU position as per the communications rack layouts
checkpoint-status |  |  | checkpoint | Do you have a network diagram detailing the connection and labelling of all Active Equipment
checkpoint-status |  |  | checkpoint | Has the Active Equipment been labelled appropriately as per the vendor requirements
label | d077e7b1-2228-5fdb-9fa2-8dfbbeef6d33 |  | note | All switches are to be labelled with the correct vendor labelling convention
checkpoint-status |  |  | checkpoint | Have SFPs been provided and installed
label | d14b9dab-5659-576d-9f9b-f7640102a380 |  | note | Check that they are the correct SFP for the optical fibre cable installed. Check they are installed into the correct port. (SFP is a small form-factor pluggable transceiver)
checkpoint-status |  |  | checkpoint | Have stacker cables been provided to stack switches together Are they connected as per the integrator/vendor requirements
label | 63bdb5e3-c866-51b5-90ed-c782719a51a2 |  | note | Are they connected as per the integrator/vendor requirements
checkpoint-status |  |  | checkpoint | Have the switches been connected to the PDUs
label | 40094bee-378c-545e-b82f-8b46a3efa5bb |  | note | Check if switches require one supply or two supplies (dual power redundancy). Check if switches require UPS supply/UPS + generator supply
checkpoint-group |  |  | section | QA ITEM 9 - Patching
checkpoint-status |  |  | checkpoint | Do you have the correct length, colour, type (Cat6/6A) and quantity of patch leads
checkpoint-status |  |  | checkpoint | Do you have a patching schedule detailing which switch port patches to which patch panel port
checkpoint-status |  |  | checkpoint | Do you have the appropriate cable management capacity installed to patch cables as per the patching schedule
checkpoint-group |  |  | section | QA ITEM 10 - Photos
checkpoint-status |  |  | checkpoint | Photos must be taken of each communications rack when completed
label | 63547774-a157-5e24-9ab9-0fd4d64cb7ee |  | note | Attach photos below as applicable
boolean | 19953e90-8321-5306-b4d9-75bb623ebf91 |  | tickbox | Photo 1: Front of rack, door closed
boolean | b2436637-c1fd-5c0f-b81a-9574dbf9b305 |  | tickbox | Photo 2: Front of rack, door open
boolean | 640efbcf-7730-5f15-8348-b2f8f930bf79 |  | tickbox | Photo 3: Front of rack, door closed
boolean | c2dcc0f6-61a4-5586-8c7f-9c2e6b2825a5 |  | tickbox | Photo 4: Rear of rack, doors open
boolean | 137b2f77-b046-564f-a921-99c82e07d575 |  | tickbox | Photo 5: Any other relevant photos
checklist-flat |  |  | checklist | AE-ITCX-013 - T-Off Visual Inspection Test (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-013 - T-Off Visual Inspection Test (Rev 0 +Names) | d09c6ea8-937b-4e3a-ae93-49e81a132119
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | c1ec65c3-17e4-585b-9c03-968c90662f31 |  | textbox | Switchboard No.
text | 35837016-99fd-5c9e-948a-3c4b4052a6a1 |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | Earthing check
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | All terminations points tight
checkpoint-status |  |  | checkpoint | Labels
checkpoint-status |  |  | checkpoint | Insulation Test
checkpoint-status |  |  | checkpoint | Wiring neatly loomed
checkpoint-status |  |  | checkpoint | Check takeoff box fuse/breaker rating
checkpoint-status |  |  | checkpoint | Energisation procedure
checkpoint-status |  |  | checkpoint | Fire rating of penetrations
checkpoint-status |  |  | checkpoint | Cover plate secure
checkpoint-status |  |  | checkpoint | Switchboard and cupboard cleaned
checkpoint-status |  |  | checkpoint | T-Off Box Visual inspection completed to specification/drawings - Area left clean & tidy
label | c38ca900-ea7e-5c12-8f67-cfd941bd1de7 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 43eaa3d1-2082-5abd-ae56-911ed6162f80 |  | note | Any Corrective Actions to be Photographed & Commented below
select | c1abb70e-0cea-59fe-90d7-c4f642d655b2 |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 236110ea-f668-561d-acc9-70acc78ab71f |  | textbox | Other (Specify here)
select | 51070bcf-e83f-5831-9e1a-81ce23645032 |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 30272149-6d1d-56e3-9d34-83ee1462bc2c |  | textbox | Other (Specify here)
label | 4da8081b-cd6a-52a1-979a-f3c949a8b990 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-018 - DB Fit Off Sheet (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-018 - DB Fit Off Sheet (Rev 0 +Names) | d3c577d4-9148-4bb0-ba44-370f06ed1a84
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | a26e9bf0-cfbd-5562-b9de-4fd85577ad8f |  | textbox | Distribution Board No.
text | 352ce072-5542-5a9c-b30a-9b121edd6eac |  | textbox | Drawing & Revision #
checkpoint-status |  |  | checkpoint | All screw terminations tight
label | 1694725d-6293-5b2d-9c66-a273ca632ed7 |  | note | With copper not visibly out of terminal
checkpoint-status |  |  | checkpoint | Neutrals correspond with actives
checkpoint-status |  |  | checkpoint | Pole fillers installed
checkpoint-status |  |  | checkpoint | DB door and escutcheon scratch and defect free
checkpoint-status |  |  | checkpoint | Switchboard labelled and cleaned
checkpoint-status |  |  | checkpoint | Cable entry points fire sealed
checkpoint-status |  |  | checkpoint | BMU circuits protected by a 100mA RCD
checkpoint-status |  |  | checkpoint | Correct lighting control equipment installed
checkpoint-status |  |  | checkpoint | Appselec 'installed by' sticker installed
checkpoint-status |  |  | checkpoint | Warning: Interrupting power supply will discharge emergency lighting batteries' installed next to RCBO feeding emergency lighting
checkpoint-status |  |  | checkpoint | Energy Meter been installed with CT metering
checkpoint-status |  |  | checkpoint | Wiring goes through the correct CT,
label | 19f1c220-0ffc-5288-a6d4-58906cb6a4ce |  | note | Installed in the correct direction and terminated to the correct phase
checkpoint-status |  |  | checkpoint | Wiring neatly loomed internally and externally of the DB
checkpoint-status |  |  | checkpoint | MANDATORY PHOTO 1 - Accurate DB schedule (Taken and Attached below)
label | a2abbd0c-b2e7-5092-8a67-184926d37fe4 |  | note | Additional photos where required (Example - Lighting control schedule)
checkpoint-status |  |  | checkpoint | DB Fit-Off completed to specification/drawings - Area left clean & tidy
label | 67d5d750-f9bd-5d0e-8272-e8cbd5dcf4fe |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 81d119b5-60eb-598a-9e9f-2b1736dd4d36 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 333c30ad-04a9-563c-b1ed-fa8d4d927c82 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 66aaecb2-f94d-59b4-a158-6a4c29f3ad1c |  | textbox | Other (Specify here)
label | 33b7f835-c369-51eb-93f7-830f15ffee8e |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AE-ITCX-017 - RCD Test Sheet (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-017 - RCD Test Sheet (Rev 0 +Names) | dd655396-0b65-4e86-93d9-217689e4ae3a
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 0197efa0-707e-5380-9541-b57b4ec82b02 |  | textbox | Test Date
text | 420ea32f-1291-515e-a143-27ac1efec8d2 |  | textbox | Switchboard No.
select | ab7267c3-3803-5690-b51f-3241b71922d1 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 2d271cfa-69e2-568f-8fdf-4726129f9182 |  | textbox | Other (Specify here)
boolean | 5e9ccce0-f0df-578b-b269-6cc0224e990c |  | tickbox | Signature added below
checkpoint-group |  |  | section | RCD Test 1
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | a247bf80-a49a-5c80-8000-705028f3e174 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 721ca98d-4911-5e16-9279-5b25b93c83a7 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | fc85163a-871a-55a1-b454-dcd1bcab7d16 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | bfc550f7-3dd7-5bfc-839b-94f79bfb0279 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | e96b0628-5e6c-57a1-a6e4-a0a331b5c964 |  | textbox | 0.Deg
text | 8f6e882c-9c62-5090-b75c-8ace0de77481 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 2bdfc71b-9241-59b3-b49f-86bd41ff9643 |  | textbox | 0.Deg
text | bd65bb2d-10fa-5dfe-b47a-dabe6a923579 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 820c4fe4-5671-57ef-8e65-d7e6db96306e |  | textbox | 0.Deg
text | e20f59fa-0ce4-5b99-9582-e0a633e69485 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 6da142ee-e1d0-50e7-87ad-86eb056bd026 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 2
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 9c28b631-2231-5816-9c2a-043aedc50427 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | ea7375e1-4107-554a-924d-6f4e7551d686 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 6666746b-5965-531e-9cc6-e51d94703f2c |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | 30fab7ac-97e2-5ceb-aca7-33d05602b097 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 43b00e96-bf50-5732-aad5-1d99e80e7b90 |  | textbox | 0.Deg
text | c4d16f91-1d60-5417-833a-1aa6ae4c49bb |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | 4c8bbcf6-d8a8-5406-975d-0464aae2b7d4 |  | textbox | 0.Deg
text | 7eb502d6-9d8e-5baa-bb9a-f21533a65060 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 74683898-ee60-5639-82f3-b6a6da735303 |  | textbox | 0.Deg
text | 10fa55db-5b59-5fa0-9430-90c2ff5f4034 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | a7685153-c061-5e1e-8658-e2b487d9ac82 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 3
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | a73fc4c4-5531-50dd-bf87-cb5402da57b7 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | cd088b58-6869-5e00-b6be-7df7f5058704 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | c53ed222-29b7-5424-89ca-26db5611916c |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | c6020513-a592-5b92-8cc4-02fe328e6aa7 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 98f9a49c-4849-5719-b514-b8d790e8ec43 |  | textbox | 0.Deg
text | 301b05ed-4d42-50d5-8fac-c022172eae1f |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | a6bc65db-5c52-5ecb-be09-d0128110037e |  | textbox | 0.Deg
text | 6197b62c-1f16-5c30-86a3-599cf005e561 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 44e12e2e-0707-5eb8-a9de-04400539d6d0 |  | textbox | 0.Deg
text | 7290d280-a35e-5792-9d21-cb1913a3261c |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 48e989ae-3648-5095-9f8c-19d0c867a0cc |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 4
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | a4e29070-df8a-5caf-8e21-546a94dedb9f |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | c071b9f9-6a97-57ae-8d61-3bd806789aa1 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | dcf17294-e35f-55a6-b5cb-bb49a776f9fa |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | 5ef6c3d5-4838-52bd-a084-d56756155d9a |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 1e41c4ad-dbe6-5b8c-a427-dbed36e903d2 |  | textbox | 0.Deg
text | 7680d0a6-45bd-5bdb-9e08-90218457ea0b |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | de5f4bc3-33a5-5cec-b45a-3d01b88291eb |  | textbox | 0.Deg
text | b3fba134-51fc-5176-8169-14020ad9c772 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 97629b38-1c41-5179-bfe7-b3c6d2b5279f |  | textbox | 0.Deg
text | 224803dd-54cb-5667-89c9-fb386fc9142b |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | c451052a-1bc4-5b60-ba2e-5b52a31a9ff7 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 5
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | d8d9a086-34b3-51ca-addb-e37a8a2dab2f |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 52b6d4dd-406e-591a-afa0-d70826fc3b85 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | a41c2d74-df3a-5fe5-bb73-b8267606f1ad |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | 4778f75d-3a48-5780-a94e-719e4f377517 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 69fa1d70-3684-547c-981f-e229bc758821 |  | textbox | 0.Deg
text | 7842c983-da0e-562d-b34f-85e9ef87f2d1 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | ac764f15-d8d5-514e-a2a5-a328b79d716e |  | textbox | 0.Deg
text | 30795651-696c-5407-b130-cb484156278c |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 8789c246-081b-52e4-aa5c-434c5878da92 |  | textbox | 0.Deg
text | f8f91a27-a73f-5677-8027-e32fef58c1b0 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 20475fce-391e-5401-818b-26cc908da2d5 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 6
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | f408e09f-9297-57a9-9f9d-4e45e9758969 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | dc9245e4-f79c-5216-9a79-4bf401da1a27 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 46c588f7-8523-58f8-a894-ce1fe2a859df |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | f7a6f7cc-1f97-5a39-8ca8-4c9f8a4f2f5d |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | c4e4a5a4-a7bd-569a-b47e-d66c7e3db364 |  | textbox | 0.Deg
text | e17f2632-7594-5d41-9058-10e8ba4ed5e6 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | d8ed8173-1532-5d98-a6a4-7a0bc8f955ae |  | textbox | 0.Deg
text | 8dac8a71-b735-5b5d-af0f-8357feeec5e4 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 6db5685c-80d6-5983-bdff-2d6034186582 |  | textbox | 0.Deg
text | 7d551b89-0c31-5720-8f57-1c0bb1349edc |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 498cc494-d8be-5bfa-83de-21ea359271d3 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 7
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | d0f016af-d9b2-531c-8df1-3af2593e3e88 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | fb2e06d7-9b08-5c6b-b6a1-5c948dac341f |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | c38792da-2c19-511d-97ea-7965240abcc7 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | 8bd04493-7b98-5ad6-bfd1-8654d8860929 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 403da96e-712d-5122-8e21-95efb65431ca |  | textbox | 0.Deg
text | 3cc1193f-b773-5aa3-911c-98001d8fad2b |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | eaa34e09-5849-5305-a792-bb1be12ffbb5 |  | textbox | 0.Deg
text | 9133c34b-4c73-5d11-83d7-26bc6d6fc505 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 82f35288-4cc1-59d7-9d42-73d5d38ec080 |  | textbox | 0.Deg
text | 0be283a6-028a-5ba1-8227-95cfb413bc8f |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | d42924a5-2f3c-528a-9455-3297d4c17e01 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 8
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 7d438473-400c-5656-b2be-f275debc87db |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 0494f6f0-34e5-5c18-b1a6-0d1c945ff3ae |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 2ff62b90-416e-5562-b924-e5566863ac30 |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | aedd8730-639d-5418-87ec-561d431880b8 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 5a2a6cb5-894f-5d0f-821a-2fb942595d9a |  | textbox | 0.Deg
text | a616e58c-8a2a-5ba6-922c-6fdfa9ea4494 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | c70695f8-75ee-558a-a22c-aa12932a7a28 |  | textbox | 0.Deg
text | bdf44885-4aeb-5379-90f8-49599f89f5ea |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 65672206-aaa0-5dbb-9187-da26512d0e6c |  | textbox | 0.Deg
text | 2a245b42-cf73-5db6-8deb-588a5330f6df |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 9a232ffa-0be2-532a-8b1d-e4effea135d5 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 9
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 569acf17-1422-59c9-a77b-93010daa9d44 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 7cf49974-92eb-5b41-a08d-20c16fdc3526 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 9ad80c3f-ebe8-5771-a076-4270857c02ec |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | 004299ad-8f05-502f-8d4f-3bc32035df7b |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | 60951e22-54b0-5736-b943-9b432dcfc2ee |  | textbox | 0.Deg
text | c2f1e4b8-099b-52e4-9ec4-7c897f72a107 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | adf3a760-8a11-5b97-9993-7db88e4d115f |  | textbox | 0.Deg
text | 569a718e-b19a-50cd-b27a-883766b2131f |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | a03929cb-2e99-5f25-b5ba-f69f7d1bf9a4 |  | textbox | 0.Deg
text | 4cafd3e1-470c-5b96-bc88-774af371f465 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 6dfdc0d5-58de-5cac-b2b1-53fef33281a7 |  | textbox | Action taken
checkpoint-group |  |  | section | RCD Test 10
checkpoint-status |  |  | checkpoint | Tested tripping time of RCD’s (using RCD Tester)
label | 71bf87cc-cd2d-5cf0-9e17-d3969a7ec9a7 |  | note | FAST TRIP FOR TYPE 1,2 OR 3 MUST BE LESS THAN 40 MS
label | 71047a60-b96d-5b4e-9edb-dbef4126a100 |  | note | Test results to include both phase relationships readings in milliseconds (ms)
checkpoint-status |  |  | checkpoint | Protective Device type selected and details entered
select | 44ed2992-7c78-5db4-9ff6-cf307ce5f88a |  | dropdown | Device type | RCD, RCBO, CB, FUSE
text | 39ab8f5f-a8f2-56ed-8230-b8cbfc6b4300 |  | textbox | Nominal Trip Current (may)
checkpoint-status |  |  | checkpoint | Acceptance Criteria= No Trip - x1/2 No Trip Time
text | e308cdd7-b2df-5fb2-b118-703486bd3378 |  | textbox | 0.Deg
text | d3897a31-a106-5cae-bb37-dc7ab708e7c5 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <300ms - x1 Trip Time (ms)
text | a502f917-933b-51e8-99b7-de77eaa29352 |  | textbox | 0.Deg
text | dcab29f8-5f07-5ee1-b2be-3f732bf78d67 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Acceptance Criteria= <40ms - x5 Trip Time (ms)
text | 13c6e968-8366-5952-a9ec-f754a3f6b288 |  | textbox | 0.Deg
text | 32766f9c-b3e4-532a-bfee-2d681a91d181 |  | textbox | 180.Deg
checkpoint-status |  |  | checkpoint | Any action taken for unsatisfactory results - PASS=No / FAIL=Yes (noted below)
text | 0ea9949f-c8ca-565a-839c-ed525f8ef22c |  | textbox | Action taken
checklist-flat |  |  | checklist | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-008 - Cable Tray Checklist (Rev 0 +Names) | dd9ac9e3-a1e9-4b71-b072-673051aa34d8
checkpoint-status |  |  | checkpoint | Latest consented drawings checked & referenced
text | 4cf935b1-2e5e-59c5-9815-c41fe25074f6 |  | textbox | Drawing & Revision #
text | 923242ad-f959-56c4-bc79-f42b843ad913 |  | textbox | Position & Purpose of Cable Tray
checkpoint-status |  |  | checkpoint | Area clear, tidy and accessible
label | 96d94dbf-2624-57c2-90cc-349480e8162b |  | note | Attach Photos/Comments below if any issues & Send report to Builder
checkpoint-status |  |  | checkpoint | Plan & confirm cable tray route
checkpoint-status |  |  | checkpoint | Coordination of other services (Mechanical, Hydraulics Fire)
checkpoint-status |  |  | checkpoint | Correct spacing of brackets
checkpoint-status |  |  | checkpoint | Correct & suitable fixings for brackets
checkpoint-status |  |  | checkpoint | Joins of tray are secure
checkpoint-status |  |  | checkpoint | Tray is securely fixed to brackets
checkpoint-status |  |  | checkpoint | Check all hangers secure?
checkpoint-status |  |  | checkpoint | Check all lock nuts are tight?
checkpoint-status |  |  | checkpoint | Check the tray is level & straight?
checkpoint-status |  |  | checkpoint | Check no sharp edges or protrusions?
checkpoint-status |  |  | checkpoint | Update drawing for as built
checkpoint-status |  |  | checkpoint | Cable Tray works completed to specification/drawings - Area left clean & tidy
label | 5b1c0ee5-472b-5092-a373-b261c42a5b90 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
select | 3b52eb1c-573c-558f-9bcb-3176a2ae5cb2 |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | f1255d57-5aa6-5490-9e28-a765ee04a43f |  | textbox | Other (Specify here)
select | e1f49a79-2044-5c55-bb6b-5fa95162df9f |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 8971df00-a0c1-57e9-83c1-21d5ee9dd36c |  | textbox | Other (Specify here)
text | cbad0ce5-57ae-5d4d-863a-d9900ead2aa2 |  | textbox | Witnessed by (Builder/QAM)
label | 800215d3-c543-5c1a-9ad5-02e8745b0bb8 |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-flat |  |  | checklist | AE-ITCX-030 - Cut-Out Sheet (Rev 1 +Names) |  |  |  |  | Yes | AE-ITCX-030 - Cut-Out Sheet (Rev 1 +Names) | e0f187e6-0167-462d-afdf-a54496bca27a
checkpoint-status |  |  | checkpoint | Walls cutout
button | fcbe0948-9a75-5b65-9812-7d350c46daae |  | button | Wall Cut Out is complete and cables have been located and withdraw from wall cavity. | Yes,No
button | 0375f0ce-40c7-50e5-83a1-11e335bd00ef |  | button | Cut outs with obstructions have been resolved? (for example furring channel, main bar) | Yes,No
label | 294c5ca0-59ab-5869-8ab1-3b1414ab010c |  | note | Additional photos of Obstructions
checkpoint-status |  |  | checkpoint | Ceilings cutout
button | 7b93af5f-3b09-56f3-920a-f591d7a8af71 |  | button | Ceiling Cut Out is complete and cables have been located and withdraw from holes. | Yes,No
button | 45ae435f-4fe6-5146-bdd9-f60a4454fc8c |  | button | Cut outs with obstructions have been resolved? (for example furring channel, main bar) | Yes,No
label | f8255ff2-3daf-5bb7-a676-be725f69d87d |  | note | Additional photos of Obstructions
checkpoint-status |  |  | checkpoint | Fire Rating - (Note this is note the Fire Register!)
button | 6e7a160a-0e8d-5e9b-b038-ec7ecdda0193 |  | button | Fire boxes installed correctly on all fire rated walls with cables withdrawn from wall cavity. | Yes,No
button | 0554f30c-5856-595c-9b3a-275b4f12d747 |  | button | All wall penetrations, distribution boards and cables drops from top plates are appropriately sealed and labelled. | Yes,No
label | 73291279-1287-5043-85a9-9e0143e0861a |  | note | Mandatory photo of completed fire rated locations (Fire Register is recorded separately)
checkpoint-status |  |  | checkpoint | Cut-Out completed to specification/drawings - Area left clean & tidy
label | 2b0d8527-9eb1-5672-a9bb-c5bd9d1a3a51 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 70393baf-8572-5ad8-97de-1fdf03b9878e |  | note | Any Corrective Actions to be Photographed & Commented below
select | 4978fa90-dbc0-5800-a8b0-8a975e120efa |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622, ADAM STRONG - AGrade: A38815 - Employee#: 2002, ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794, ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684, ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863, ALAN BIRCHALL - Agrade: A18981 - Employee#: 379, ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111, ALI HASAN - Agrade: A48087 - Employee#: 1654, ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015, ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972, ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309, BEN DARBY - Agrade: A53332 - Employee#: 1702, BEN FINDLAY - Agrade: A41429 - Employee#: 2006, BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933, BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733, BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801, BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850, BRENTON HILL - Agrade: A47213 - Employee#: 1729, BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887, BROCK DOWNIE - Agrade: A53290 - Employee#: 1849, BROCK LLOYD - Agrade: A44808 - Employee#: 1680, CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193, DANIEL BENDINELLI - Agrade: A67728 - Employee# 2097, DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937, DAVID OLSEN - Agrade: A42915 - Employee#: 1685, DEAN NGUYEN - Agrade: A48514 - Employee#: 1515, DEREK JACOBS - Agrade: A67318 - Employee#: 2078, DWAYNE KLOET - Agrade: A48278 - Employee#: 1239, ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782, EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895, FERGUS COATES - Agrade: A59054 - Employee#: 1774, FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679, HUY DO - Agrade: A40954 - Employee#: 873, IMMANUEL KAWITI - Agrade: - Employee#: 2023, JACKSON SHARPE - Agrade: A53801 - Employee#: 1540, JAMES MARASCO - Agrade: A55184 - Employee#: 1758, JAMES PLEASANT - Agrade: A62956 - Employee#: 1976, JAMES SPOKES - Agrade: A48756 - Employee#: 1770, JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756, JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719, JASON PERL - Agrade: A36692 - Employee#: 1868, JASON SALE - Agrade: A28662 - Employee#: 1615, JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029, JESS ZAHRA - Agrade: A52969 - Employee#: 1403, JOEL BASSETT - Agrade: A39498 - Employee#: 1958, JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908, JOHN GREEN - Agrade: A55589 - Employee#: 1734, JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682, JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720, KALE BLACKLER - Agrade: A39293 - Employee#: 1751, KAYNE WALKER - Agrade: A38805 - Employee#: 1718, KEVIN MURPHY - Agrade: A63544 - Employee#: 2022, KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698, LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834, MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308, MARK D_ANGELO - Agrade: A40610 - Employee#: 1832, MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352, MATTHEW COX - Agrade: A42092 - Employee#: 1704, MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894, MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915, MICHAEL BRASHER - Agrade: A29237 - Employee#: 954, NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748, PAT DOUBLE - Agrade: A46604 - Employee#: 1118, PAUL HARMAN - Agrade: A26306 - Employee#: 1728, PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190, PETER LEWIS - Agrade: A53556 - Employee#: 1749, PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612, ROB POLLARD - Agrade: A56906 - Employee#: 1754, ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132, RYAN DEPRADA - Agrade: A41361 - Employee#: 1848, SCOTT RYAN - Agrade: A59062 - Employee#: 2017, SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034, SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771, SIMON COLLARD - Agrade: A32749 - Employee#: 883, STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829, TOM HAMILTON - Agrade: A48254 - Employee#: 1434, VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218, WILLIAM FISHER - Agrade: A20679 - Employee#: 859, Other (Specify below)
text | a7279f4a-ae0c-5f67-ad4c-e8ed76b182c8 |  | textbox | Other (Specify here)
label | fc96dcd2-aff9-5ac5-9c67-b3b578b0902d |  | note | Signature Sign-Offs - Attach signature(s) below
checklist-sectioned |  |  | checklist | AF-502 - Electrical Services commissioning Sheet - Details & 10x Circuit Resistance & Fault-Loop Impedance (Rev 0 +Names) |  |  |  |  | Yes | AF-502 - Electrical Services commissioning Sheet - Details & 10x Circuit Resistance & Fault-Loop Impedance (Rev 0 +Names) | e81b8036-123e-487c-b619-37ea55d83079
checkpoint-group |  |  | section | Electrician Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 5706bef8-05aa-583e-9d09-7f7868188885 |  | textbox | Test Date
select | e5f116e6-b597-588d-a46b-c55449f61691 |  | dropdown | Name of A-Grade Electrician | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | c675b8b7-b712-5a11-aa1a-7cdcea08bf13 |  | textbox | Other (Specify here)
boolean | a6b46fa1-c710-534f-8a99-9f0dd85ceb73 |  | tickbox | Signature added below
checkpoint-group |  |  | section | Circuit Details
checkpoint-status |  |  | checkpoint | Details - Pass once entered
text | 89d16a19-8bed-5c9e-8555-b6b4dc389d7d |  | textbox | Designation of service
text | 342b3d41-3d92-56e8-913a-ec7167a76893 |  | textbox | Location of Service
text | acc7b8f3-21cc-52b9-8d01-3e36a87462a6 |  | textbox | ZE
checkpoint-group |  |  | section | No. 1
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 7c64636d-5abc-5497-b1d2-9fa251ea2932 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 42e26360-76d7-5eca-b813-3ad13a94411e |  | textbox | Type B, C, D, TM Electronic
text | 6f25881f-9354-5af6-9cf5-394c4caaf972 |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | 72864834-6799-5fd7-9885-54c5d4c48326 |  | textbox | (A) Active CSA mm2
text | 2f9c9144-0780-596a-917d-0b2eee82a51c |  | textbox | (B) Earth CSA mm2
text | b7950f10-76a2-5ccb-a30c-7a560edd4d00 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 831df2a7-6759-5d78-9d2f-126523322c23 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 01978c1a-e79d-5ccb-b1e1-cd9c23f08bf3 |  | textbox | RE = (D/C) * A
text | 87cef09a-a420-5752-b16f-915e93d2975b |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | e12736e5-c9d6-5966-8d19-818541b016f8 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | fc32869f-f515-5b2f-867a-15679b440f78 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 2
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | e013e385-7490-51dd-87bb-3c52be2b56c8 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 2ffe2204-8ad1-571e-9236-653a30683e1f |  | textbox | Type B, C, D, TM Electronic
text | 774c0b5d-4931-5ae1-9ce2-8a7b86cc5f2e |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | 499daa92-4a28-58d0-991b-0943129a818b |  | textbox | (A) Active CSA mm2
text | 1c7c4fe7-9a80-56cc-9078-4ab2dd2b9328 |  | textbox | (B) Earth CSA mm2
text | a2e69f39-c0a7-50d6-8a23-23457805c837 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | dd2395a9-4f56-55ae-acb0-a60f5a1ca052 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 5e7c2ccf-d93f-597b-b810-7c5453cb8984 |  | textbox | RE = (D/C) * A
text | 6d5f05bb-af4c-56b5-a38f-09327776272b |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | e3a493ab-cff8-5304-ac04-eacdaeef28a2 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 12569d3c-b131-5f8e-9382-cf23c61dde60 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 3
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 62f83eda-9a48-58fb-b69d-d551c9a125e7 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 2fc6271a-6018-5cac-bd8b-e3cfd0ecf97e |  | textbox | Type B, C, D, TM Electronic
text | 7660d16d-6707-55f3-8a1a-93ca00223196 |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | 0734601b-51a1-56fe-a4a9-c54fcca54705 |  | textbox | (A) Active CSA mm2
text | 2cdc6391-46cd-556e-8abd-e6a0d39ee4a1 |  | textbox | (B) Earth CSA mm2
text | ea048e2c-1a8f-585d-81f0-dbd98ebb553f |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 91fffdd2-12d4-551c-96ed-a7b8fcea0b74 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 206ea067-ac54-5d60-a0f9-412d6db66995 |  | textbox | RE = (D/C) * A
text | d667acfd-6e44-58dd-b3cd-3d4a3aba52b5 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | ee795504-452f-5d80-84b2-0b5022acd223 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | d274be7a-2d2b-5f5f-97b2-f7cdce6682da |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 4
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 07ab793b-70fc-547f-9490-44d2fb1e25c1 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 5f84f168-5ea2-5a61-bab9-b258e446ea53 |  | textbox | Type B, C, D, TM Electronic
text | f1bc9811-a815-5387-8fbd-b8ce66d6242d |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | b9395dbb-7b16-5fe2-b4df-f701bb9d6e03 |  | textbox | (A) Active CSA mm2
text | a199f43e-2241-5b43-9cea-5b783d45d197 |  | textbox | (B) Earth CSA mm2
text | 1a204483-5d61-5b91-81a7-e40e4f69e963 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | eaba577c-4dd6-5145-ad74-1856ecac7cd8 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | c9eeba48-537b-5ed5-8502-41ddadfdc73e |  | textbox | RE = (D/C) * A
text | af6fa3ff-1c93-5759-817b-6f5672d04fdd |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 62331b0b-4d0c-5f3a-9595-bb11b9e0d2ca |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 04269d77-f523-56bd-b573-bd5abc1f1653 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 5
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 34d78c94-00f6-5f30-b610-497016b2fb5b |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 75f20b38-2682-549f-a04d-311d3d862926 |  | textbox | Type B, C, D, TM Electronic
text | 4915dea6-37ed-51ba-8061-3987393ad3e6 |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | d823faae-9d4b-5de1-81c5-e33805a31411 |  | textbox | (A) Active CSA mm2
text | 7f338e39-3246-59c6-a1cf-bafc557aced2 |  | textbox | (B) Earth CSA mm2
text | ab57cb93-f615-5cb3-a87f-f481d3ff769d |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 0173c956-0596-5730-9d8b-1fc686183462 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | d5469bab-d0fb-579a-ba31-081dcb98af6d |  | textbox | RE = (D/C) * A
text | 8bc4d602-d966-5895-bfb1-b4515917be3d |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 196b9fa4-887f-52d6-9427-ad3d9b5dbb27 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 083ed663-7b75-5166-9214-10867774b641 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 6
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 04da377f-a756-571b-b89b-054f09cbf053 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 63132af0-0cd6-5860-81b7-79776006cecd |  | textbox | Type B, C, D, TM Electronic
text | 129dde1e-61b0-58f9-b9ea-84d3a22c5d84 |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | 2b3bda58-c273-5886-b824-65b90adf2f66 |  | textbox | (A) Active CSA mm2
text | ec39c855-09cd-5d94-b61e-fdb9ceb18851 |  | textbox | (B) Earth CSA mm2
text | 8c13ca43-c28d-55db-8db3-d839f8db1631 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 95894bdd-2a22-5f00-b86b-0fc68cf55e1e |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 793475c3-2ae9-5baf-b7aa-23cf6314c4b6 |  | textbox | RE = (D/C) * A
text | 5f10969c-455e-5cc8-b3cd-f19dbf53a11c |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 5cc3341c-569d-5a31-8110-769ea97e2f3c |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 32d2a5d0-d1e8-5ad6-beea-c4e61f938b4c |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 7
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 2e531e31-9d6f-519a-b30d-f976a6c4c096 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | a1f76bf3-4e35-597b-9abb-59d23018ce93 |  | textbox | Type B, C, D, TM Electronic
text | 0f3b26fd-b452-5ae6-8868-00a65978acd1 |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | 0cecb24a-b936-586d-ac65-1577473acc88 |  | textbox | (A) Active CSA mm2
text | 83233c8e-0ff6-5f8c-99a9-57c0d47d1a8d |  | textbox | (B) Earth CSA mm2
text | 7baf6d5f-be37-5135-ad3e-7252285afeb5 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 68069766-de05-53b7-8593-00d8545b184c |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | a2dfc8c1-7c8a-56be-8735-25b2f33f4df6 |  | textbox | RE = (D/C) * A
text | c8992f6a-0f14-5680-ac2e-314f4170313f |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 60a0abb0-598e-5722-beae-653ac8685b5c |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 4f23c8b7-e37f-5c9d-b885-fae5cd8051c0 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 8
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | c0b5d927-b465-57e0-9758-2aed7f4dad86 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | a1195de6-686b-57fa-9a2e-a02c0e46a420 |  | textbox | Type B, C, D, TM Electronic
text | 21f97de3-fa2a-5c62-9a7b-87024a0a18b4 |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | a16dbfe9-3702-5dfd-ba1c-0d0ca7d213a0 |  | textbox | (A) Active CSA mm2
text | e06bc524-f15f-5e73-899e-20127c43c8bd |  | textbox | (B) Earth CSA mm2
text | 36b53d82-3ce8-5d25-86c8-9d27bfeb7d33 |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | 90e800b6-07fb-52c5-815e-597e71fdc205 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 00e3a8bb-3615-589b-b72d-775b22adc48f |  | textbox | RE = (D/C) * A
text | 26c1af4d-7e01-54e1-bd1a-53a5d45f2844 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 4e7e6478-17d7-5c68-88c4-f5e3279def5b |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | 8a564708-c9d0-5c14-a819-68c8a6924cf8 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 9
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | d2a1d6ac-9f49-56fb-bc79-9eff869dfaee |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | ef5c4acc-39f1-5d9a-a558-e508d76bbb93 |  | textbox | Type B, C, D, TM Electronic
text | f7bcc450-1a4e-5a6d-b16c-088e3829423f |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | e4213409-6b46-563b-8e61-e7f4832d27ab |  | textbox | (A) Active CSA mm2
text | 8f021296-d65c-5fdd-97d8-339604c89c13 |  | textbox | (B) Earth CSA mm2
text | 0f9bf134-3b93-5cb7-9c0b-fee88815802d |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | f8af9dbb-9edb-5cfd-92dd-da9ea08ad3f7 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | 9c4e9b19-08e6-5d7c-a6ba-1eb1c31d760f |  | textbox | RE = (D/C) * A
text | 6e94c1f0-b2fa-52b0-be81-afb8865d39d0 |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | 63edd1e5-49b8-5c45-ab52-08c372b3fcc7 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | e95e0859-fceb-5a58-8fe4-e02dfa63d0a0 |  | textbox | Difference (F) - Calc'd ZS
checkpoint-group |  |  | section | No. 10
checkpoint-status |  |  | checkpoint | Overcurrent Device - Pass once entered
text | 346d3444-231e-5fd3-b66d-6623922c2ed4 |  | textbox | Short Circuit Capacity (i.e. 6kA, 10kA)
text | 663004b0-ed72-5374-a51b-47c4f13efb5b |  | textbox | Type B, C, D, TM Electronic
text | cbc8c048-2d0f-5c73-9e4c-5088da4c017a |  | textbox | Rating in (A)
checkpoint-status |  |  | checkpoint | Data Capture
text | bf0bd68d-1f9a-598a-9820-c4c77226bb71 |  | textbox | (A) Active CSA mm2
text | 7fc8e076-2f20-5fd4-8e4c-56cb5f5c1b85 |  | textbox | (B) Earth CSA mm2
text | 5cecf3bd-51d4-52ba-a1be-9e8a9695d54d |  | textbox | (C) = A+B
checkpoint-status |  |  | checkpoint | Measure
text | b49e9f80-940c-5ef8-960c-c1e048ec4bc8 |  | textbox | (D) Rphe (Ohms)
checkpoint-status |  |  | checkpoint | Data Capture
text | eca31b7e-9703-5f6c-950f-5295cfdda9c3 |  | textbox | RE = (D/C) * A
text | 461f4956-b2ce-519f-b20c-01de9fc6ac8d |  | textbox | Calculated Loop impedance = D + ZE
checkpoint-status |  |  | checkpoint | Measure
text | aa06c745-7700-5912-b83b-448fcd0362b6 |  | textbox | (F) Tested ZS
checkpoint-status |  |  | checkpoint | Data Capture
text | c2face47-9ece-59ee-a1a3-9ddb52f9176a |  | textbox | Difference (F) - Calc'd ZS
checklist-sectioned |  |  | checklist | AE-ITCX-001 - Temp Board Checklist (Rev 0 +Names) |  |  |  |  | Yes | AE-ITCX-001 - Temp Board Checklist (Rev 0 +Names) | f2ec4ee1-4c83-4475-8038-4ba4873bfbe8
checkpoint-group |  |  | section | Defects
checkpoint-status |  |  | checkpoint | Major Defects (Send back to Aline)
label | 35a960b5-736a-5bff-b8fc-1f114eed9e51 |  | note | Add photos/comments & Send back to Aline
button | 0251fcc9-66ba-5619-9a5e-e02aa5fbf9ce |  | button | Is the switchboard structurally sound | Yes, No
button | 2e2e737b-6212-56da-baf0-09d9c4ae3bf9 |  | button | Does the main door close | Yes, No
checkpoint-status |  |  | checkpoint | Minor defects (Fix Onsite)
button | 80f21b8e-9235-5bc9-a0f4-ee27859ac5d7 |  | button | Is the main isolating switch identified | Yes, No
button | 898b990c-1076-5239-8014-37cdb5c6ad85 |  | button | Are all C.B’s and R.C.D’s identified | Yes, No
button | b5894af2-18e4-5651-be02-113af5bc6468 |  | button | Is 1.2m clearance signage in place | Yes, No
label | 0412946f-2c0a-5bbb-bcfe-d8019f5a70c2 |  | note | Add Photo below
button | 1bf726c5-ab78-59e6-81f4-303ce15fcf73 |  | button | Is ‘Live Parts’ signage in place | Yes, No
label | df2b9c7c-79d5-579a-b3a4-58a9eabe59e7 |  | note | Add Photo below
checkpoint-group |  |  | section | Electrical
checkpoint-status |  |  | checkpoint | Do pole fillers cover all gaps
checkpoint-status |  |  | checkpoint | Are test points installed in the board
checkpoint-status |  |  | checkpoint | Are all holes in connection (J.Box) filled with screwed stops
checkpoint-status |  |  | checkpoint | Are Perspex covers in place
checkpoint-status |  |  | checkpoint | Do escutcheon plates have all screws fitted
checkpoint-status |  |  | checkpoint | Is insulated lead stand attached and insulation intact
checkpoint-status |  |  | checkpoint | Do the flap-lock and door-lock work
checkpoint-group |  |  | section | Replacement Parts
checkpoint-status |  |  | checkpoint | Replacement parts list - Pass=Required, N/A if not Required
label | 4e63c799-bac3-599f-986b-c8eeb25d5800 |  | note | Complete this section and order from the office as required. Send report to office Top Right
label | 01099429-7b26-50ed-a21c-026508bbfa32 |  | note | ----Please do not strip other boards for parts.----
checkpoint-status |  |  | checkpoint | Galvanised Style - Pass=Required, N/A if not Required
label | 5ccb85f7-d0d2-5c41-8805-478925bcbb8c |  | note | Input quantities required below
text | c56eee73-14c8-5307-b726-4bd429025ec9 |  | textbox | 10 A DIN mounted GPO
text | e31b72c3-150f-52ff-bbbf-ec20435d4688 |  | textbox | 15 A DIN mounted GPO
text | a1581085-ceea-5052-b257-f84bc766a16e |  | textbox | Line taps
text | 94a68972-8d30-5cc9-aab3-145db77d72ef |  | textbox | Hinges
text | 5eabbcec-0fef-56f6-8ed7-a983584ae452 |  | textbox | Door
text | a8b427a0-5315-5fc3-85e0-f0334db8403a |  | textbox | Door handle and tongue
text | 508e7b4d-5c44-538b-b86e-cc0adbe0a2f1 |  | textbox | Bottom connection box
text | 54fad2e5-3af4-5544-882a-8ea40938259d |  | textbox | Bottom connection box cover
text | 6cf693ba-8926-577f-9807-58894521dd41 |  | textbox | RCD cover lock 001
text | 8e2b4baa-19b2-5d73-bf05-a0f1607094f7 |  | textbox | RCD cover
text | ad5e1de4-7785-5371-825e-f4754926e689 |  | textbox | Pole fillers
text | 039da2ee-789e-597f-8869-86326e078e2a |  | textbox | 63 A main switch
text | 469de711-902f-5312-ac3c-dd29e8be605b |  | textbox | 100 A main switch
text | 20bf03b0-8bdd-50b1-9216-c7a02134bf93 |  | textbox | 16 A RCBO 2 pole
text | 139b9c0b-2af9-586d-9db0-4a83498f140b |  | textbox | 20 A RCBO 2 pole
text | be6419cc-55b0-5990-a9d5-f1e7f7b6c1da |  | textbox | 32 A 4 pole CB
text | 5ab7fdac-c095-5202-81c9-ddb966e77fd5 |  | textbox | 40 A 4 pole CB
text | 5d08aa39-74ca-5a8f-9bc0-660ca842202f |  | textbox | Set of legs
text | d3f9478a-e3b7-57af-b8fa-22ce6432c94a |  | textbox | Set of feet
text | ceaec2fa-a0d4-565e-a0cf-8302e937e7ea |  | textbox | Perspex cover for line tap
text | f489805a-eacf-5077-97f1-1c52634bb8b7 |  | textbox | Lead stand
text | fa45a1cf-6cac-5dbc-ad71-45fe92a8fa9c |  | textbox | Escutcheon
text | c82b7737-3857-5b0d-9186-42aab7cd01ec |  | textbox | Connectors
text | bc448c25-d895-55ef-82b1-1f98728d7582 |  | textbox | RCD cover lock 001
checkpoint-status |  |  | checkpoint | New Green Style
label | 7c0bf02d-c291-5171-84a4-788557fc38cb |  | note | Input quantities required below
text | 9c156d1d-31d7-5f00-aee5-947eb398af52 |  | textbox | Door
text | a7169b63-662c-539f-8e1c-1016afca5fee |  | textbox | Hinges
text | 47b883f5-8b6e-55b4-855d-a265f9aaf448 |  | textbox | Legs
text | 0aaf9470-a7b7-521c-aefc-bad61f2143d6 |  | textbox | Lead stand
text | c3fcff9d-9554-5cff-899b-eeaad65cdc63 |  | textbox | Escutcheon
text | f9a0a26b-f8e4-5df6-b041-5483c4b5229a |  | textbox | Rcd cover
text | cae7558a-6122-5234-af35-dc0d3282f987 |  | textbox | Rcd cover lock 001
text | aa2b9843-cdea-5c06-b600-ef3433e18749 |  | textbox | Door handle and tongue
text | 18c64f7d-e68b-53c2-ab68-65afc6d12565 |  | textbox | 32 A 3 phase outlet
text | 479e9199-8a7c-545f-81f0-5fe5d431854b |  | textbox | Connectors
text | ff6d2932-19af-55b4-a2d4-4b61fe8da7dd |  | textbox | 15 A GPO
text | a6dced84-b05b-56d8-8d2f-4af279e6bbe3 |  | textbox | 10 A DGPO
text | db05f4ef-60e8-5ec9-ad54-3056f136fa30 |  | textbox | 63 A main switch
text | adf1f70b-bbe9-5cc0-8ec5-2d86dd9aae1b |  | textbox | 100 A main switch
text | 51dd584a-3caa-5dcf-985b-f6aaaecf5a07 |  | textbox | 40 A 4 pole CB
text | 519425a6-277e-550d-9559-ac190bdce48a |  | textbox | 32 A 4 pole CB
text | ef090719-38ca-5999-a6d2-291329f3ce77 |  | textbox | 16 A RCBO 1 pole
text | ee9c44ee-c047-5441-a2a6-f8e850d6d26a |  | textbox | 20 A RCBO 1 pole
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Temp Board completed to specification/drawings
label | ccaa0f5a-3e47-5a05-99dd-973712816ec6 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 1ea9ae56-4e98-5b14-ab9b-1ea9b7166891 |  | note | Any Corrective Actions to be Photographed & Commented below
select | 15e1729c-10f0-579b-9f81-631e33bce3fe |  | dropdown | Installed by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 649b8a69-8f6b-5e7f-a2e5-7ae870cc952c |  | textbox | Other (Specify here)
select | 99dcfdb6-7cd2-5e6f-9dd6-d9636e4092fd |  | dropdown | Checked by (Appselec) | ADAM KENT - AGrade: A56009 - Employee#: 1622 , ADAM STRONG - AGrade: A38815 - Employee#: 2002 , ADRIAN BROWNE - AGrade: A37356 - Employee#: 1794 , ADRIAN FANCELLU - AGrade: A58098 - Employee#: 1684 , ADRIAN IVANCIC- Agrade: A62060 - Employee#: 1863 , ALAN BIRCHALL - Agrade: A18981 - Employee#: 379 , ALBERT ISMAIL - Agrade: A42436 - Employee#: 1111 , ALI HASAN - Agrade: A48087 - Employee#: 1654 , ALLISTER DAVEY - Agrade: A43940 - Employee#: 1015 , ANDREW NANCARROW - Agrade: A36974 - Employee#: 1957, ANGELO MIHELAKOS - Agrade: A28568 - Employee#: 1972 , ARTHUR KAPLON - Agrade: A29972 - Employee#: 1309 , BEN DARBY - Agrade: A53332 - Employee#: 1702 , BEN FINDLAY - Agrade: A41429 - Employee#: 2006 , BENJAMIN ICELY - Agrade: A59057 - Employee#: 1933 , BENJAMIN OSMOND - Agrade: A59204 - Employee#: 1733 , BENJAMIN STEWART - Agrade: A50504 - Employee#: 1865, BRADLEY TRUSCOTT - Agrade: A35473 - Employee#: 1801 , BRANDON DUDLEY - Agrade: A45361 - Employee#: 1850 , BRENTON HILL - Agrade: A47213 - Employee#: 1729 , BRINSLEY TELLER - Agrade: A59986 - Employee#: 1887 , BROCK DOWNIE - Agrade: A53290 - Employee#: 1849 , BROCK LLOYD - Agrade: A44808 - Employee#: 1680 , CHRISTOPHER HUTCHESON - Agrade: A55937 - Employee#: 1644, DAMIEN CASEY - Agrade: A39744 - Employee#: 1193 , DANIEL MILLER - Agrade: A42685 - Employee#: 1909 , DANIEL SETTE - Agrade: A50502 - Employee#: 1812 , DARREN STACE-SMITH - Agrade: A48737 - Employee#: 1194 , DARRYL ROWLEY - Agrade: A35492 - Employee#: 1937 , DAVID OLSEN - Agrade: A42915 - Employee#: 1685 , DEAN NGUYEN - Agrade: A48514 - Employee#: 1515 , DWAYNE KLOET - Agrade: A48278 - Employee#: 1239 , ESMIR GOLETIC - Agrade: A60319 - Employee#: 1782 , EVAN CAMPBELL - Agrade: A35710 - Employee#: 1895 , FERGUS COATES - Agrade: A59054 - Employee#: 1774 , FRANC AUFFRAY - Agrade: A58054 - Employee#: 1679 , HUY DO - Agrade: A40954 - Employee#: 873 , IMMANUEL KAWITI - Agrade: - Employee#: 2023 , JACKSON SHARPE - Agrade: A53801 - Employee#: 1540 , JAMES MARASCO - Agrade: A55184 - Employee#: 1758 , JAMES PLEASANT - Agrade: A62956 - Employee#: 1976 , JAMES SPOKES - Agrade: A48756 - Employee#: 1770 , JASON CRAMER - Agrade: A57832 - Employee#: 1673, JASON GARETTO - Agrade: A46469 - Employee#: 1896, JASON MASTROPASQUA - Agrade: A52370 - Employee#: 1756 , JASON MURAWEZUK - Agrade: A58791 - Employee#: 1719 , JASON PERL - Agrade: A36692 - Employee#: 1868 , JASON SALE - Agrade: A28662 - Employee#: 1615 , JAYDEN ZAHRA - Agrade: A64270 - Employee#: 2029 , JESS ZAHRA - Agrade: A52969 - Employee#: 1403 , JOEL BASSETT - Agrade: A39498 - Employee#: 1958 , JOEL COGHLAN - Agrade: A43339 - Employee#: 1220, JOHN BATTISTA - Agrade: A41810 - Employee#: 1908 , JOHN GREEN - Agrade: A55589 - Employee#: 1734 , JOSEPH PETROVIC - Agrade: A55175 - Employee#: 1682 , JUSTIN CROCKER - Agrade: A43258 - Employee#: 1720 , KALE BLACKLER - Agrade: A39293 - Employee#: 1751 , KAYNE WALKER - Agrade: A38805 - Employee#: 1718 , KEVIN MURPHY - Agrade: A63544 - Employee#: 2022 , KEVIN SOUTAR - Agrade: A32524 - Employee#: 1698 , LUKE O_KEEFE - Agrade: A43627 - Employee#: 1834 , MARC MCLAUGHLAN - Agrade: A45201 - Employee#: 1308 , MARK D_ANGELO - Agrade: A40610 - Employee#: 1832 , MARK GASCOIGNE - Agrade: A48674 - Employee#: 1352 , MATTHEW COX - Agrade: A42092 - Employee#: 1704 , MATTHEW JOYNSON - Agrade: A35535 - Employee#: 1894 , MATTHEW KNIGHT - Agrade: A43800 - Employee#: 915 , MICHAEL BRASHER - Agrade: A29237 - Employee#: 954 , NICHOLAS EVANS - Agrade: A56890 - Employee#: 1748 , PAT DOUBLE - Agrade: A46604 - Employee#: 1118 , PAUL HARMAN - Agrade: A26306 - Employee#: 1728 , PAUL RABAHI - Agrade: A52747 - Employee#: 1939, PAUL WAISTELL - Agrade: A41819 - Employee#: 1190 , PETER LEWIS - Agrade: A53556 - Employee#: 1749 , PHILIP BROWN - Agrade: A55466 - Employee#: 1940, PHILLIP CHOW - Agrade: A55466 - Employee#: 1612 , ROB POLLARD - Agrade: A56906 - Employee#: 1754 , ROSS KOSTOGIANNIS - Agrade: A46721 - Employee#: 1132 , RYAN DEPRADA - Agrade: A41361 - Employee#: 1848 , SCOTT RYAN - Agrade: A59062 - Employee#: 2017 , SEAN SMALLACOMBE - Agrade: A64078 - Employee#: 2034 , SHANE SINCLAIR - Agrade: A55009 - Employee#: 1771 , SIMON COLLARD - Agrade: A32749 - Employee#: 883 , STEVEN THOM - Agrade: A48941 - Employee#: 1199, STUART MALVENAN - Agrade: A61071 - Employee#: 1829 , TOM HAMILTON - Agrade: A48254 - Employee#: 1434 , VAUGHAN ROBINSON - Agrade: A45819 - Employee#: 1218 , WILLIAM FISHER - Agrade: A20679 - Employee#: 859 , Other (Specify below)
text | 91006443-068c-50f9-9f2c-bc65d31e7fdd |  | textbox | Other (Specify here)
label | 02dbf9e6-9543-55e4-b2bd-903b8d8595b2 |  | note | Signature Sign-Offs - Attach signature(s) below