## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-SP2-030-002 ITP Wastewater Pressure Testing | itp |  |  |  |  | DN1210-SP2-030-002 ITP Wastewater Pressure Testing Rev 1
section | SECTION 3 – PRE-CONSTRUCTION - MATERIAL , PERSONNEL & THIRD PARTY APPROVALS (P&G / ESTABLISHMENT)
checkpoint | 3.1 - Work method statement
label | Detail / Activity - Provide the Engineer with a detailed work method statement (WMS) with details of how the pressure testing will be carried out at least 10 Working Days prior to the test
label | Acceptance / Conformance Criteria - WSP sign off
label | Standard / Specification - PS: 22.7.12 d)
label | Verifying Document - Ineight approval
label | Testing Quantity Required (based from schedule qtys) - Pre aproval
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Witnessing of Pressure Testing
label | Detail / Activity - Pressure testing will be carried out at least 10 Working Days prior to the test
label | Acceptance / Conformance Criteria - On site
label | Standard / Specification - PS: 22.7.12 b)
label | Verifying Document - Email
label | Testing Quantity Required (based from schedule qtys) - All Testing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 4 – CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE TESTING
checkpoint | 4.1 - Pressure Acceptance Testing
label | Detail / Activity - Backfill/cover with embedment before testing.
label | ○ Complete pressure acceptance template.
label | ○ End caps in place, provision for filling the pipeline and bleeding air.
label | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
label | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
label | ○ Complete pressure acceptance template.
label | Standard / Specification - PS 22.7.12 d), PS 22.7.13 b), Appendix XXI
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature