## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
8cff2206-129e-4644-90b8-be16ef09adb0 | checklist | DN1211-001 ITP Stormwater Rev 0 | itp | DN1211-001 ITP Stormwater Rev 0
2d4d7028-cc67-47fb-bc4a-85c5fb76d593 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
4527df09-8192-41d9-91e4-0a524ba75d96 | checkpoint | 3.01.01 - Construction Pack
ed941b59-045d-5324-935c-4edacad53d24 | note | Acceptance / Conformance Criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
7607b137-0671-51a1-951e-8fe699bca7cf | note | Standard / Specification - Downer
1a261d26-8d45-54cd-974c-ca5bb4ac14e5 | note | Verifying Document - Construction Pack
dea16211-027b-5047-9162-7ec4d561fef0 | note | Frequency - Submit 5 days prior to commencement of works
e9ed4920-b239-5865-b2fa-0990017f31df | note | Verification Activity: Activity - H
a5d7357f-7bdd-5493-86b3-a183043befc6 | note | Verification Activity: By - PE
0f7a9e73-1447-4c56-b835-e7944a700dd0 | checkpoint | 3.02.02 - Survey Setout
560b023e-147d-55a2-8e7a-6f19ffb12b8f | note | Acceptance / Conformance Criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
4a613baa-0a12-558a-9c2d-7fd82d39c8f2 | note | Standard / Specification - Downer
ae9eaa9a-093e-5ab9-9194-2e331e70a97f | note | Verifying Document - Survey Records
c218bedd-8cca-5021-8535-712a63f6ba1a | note | Frequency - Prior to Works
331200dc-2a8c-5760-bf25-c2480cb1e2e3 | note | Verification Activity: Activity - H
2c23c83f-acf0-5b8d-a45d-f108326dc0ea | note | Verification Activity: By - SV
bfe23b37-5f1c-4380-b939-e4ed0c30ac3b | checkpoint | 3.01.02 - Service Location
4c237af8-4b41-5255-a9a3-16dc1c9cb2f9 | note | Acceptance / Conformance Criteria - Complete the Excavation permit process to identify, locate and protect all services.
70b89522-a4f1-59a0-a34a-0763adc06ad0 | note | Standard / Specification - Downer
2fc828f2-420d-566d-bf73-eeb8dee67d5e | note | Verifying Document - Excavation Permit
ab07887f-321d-5f8c-90d1-45ba4fd516de | note | Frequency - Prior to Excavation
8a58eb97-5274-50e7-adf9-f0281a9d1263 | note | Verification Activity: Activity - H
d3bc6fa7-571e-57a9-9f9c-a1f93196bfc6 | note | Verification Activity: By - SE
4f68fe33-f844-431a-a65d-f2861ef54a9c | checkpoint | 3.02.03 - Internal Permits
a347d2b0-a5ba-55b1-9e68-bfd7c210480a | note | Acceptance / Conformance Criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
4d2a1a95-aec1-51d6-927c-a766ee451138 | note | Standard / Specification - Downer
6e7adeed-b1bd-5543-8106-9a55f1345623 | note | Verifying Document - Internal Permits
85667c04-f2ca-5162-97df-39d3d645efdd | note | Frequency - Prior to Excavation
edd023ec-719b-5ce7-b19e-16a2885d6309 | note | Verification Activity: Activity - H
76da0f14-88c5-5dca-8c1d-05244ea3889b | note | Verification Activity: By - SE
321ebddf-81df-4ed6-91a5-aef27fd4ed7a | checkpoint | 3.01.03 - External Permits
467ca4c7-a6dd-5676-bcb1-2e7a71015ad7 | note | Acceptance / Conformance Criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
79a18264-8b33-5111-81b4-a0a57702ebde | note | Standard / Specification - Downer
12b31bbf-e3f9-5351-8e68-cacdbfa3358d | note | Verifying Document - External Permits
0c3697d8-606a-5355-88b4-ddff917a49e1 | note | Frequency - Prior to Excavation
85ad7aba-b471-542e-9548-bf1406fb8e7f | note | Verification Activity: Activity - H
19b250c0-3c4f-521b-bc99-55e8680c70b3 | note | Verification Activity: By - PE
5c76e8e8-367c-46b3-b7ab-81bf7505081c | checkpoint | 3.02.04 - Approved Construction Drawings
44e9c8ba-e41e-5511-8474-4941676b1db9 | note | Acceptance / Conformance Criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
9b958b4c-d9cd-5460-9bd7-e0ba192ad0e6 | note | Standard / Specification - Downer
95dbed92-8d36-5187-b9f1-f7f29077e822 | note | Verifying Document - IFC Drawings
188acaf8-10f8-5fb7-b161-ddf2b5eee7b5 | note | Frequency - Prior to works start
cca3b916-fec5-57fa-a8fd-438689df35ab | note | Verification Activity: Activity - H
f7e4c0d9-2353-537c-aff2-ab5a287ae4c8 | note | Verification Activity: By - PE
b4243508-5f7b-4b84-acaa-52db86020dfa | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
195eaba4-e2c8-4dab-9b1a-f403d94170f1 | checkpoint | 4.01.01 - Concrete pipes
9adc9a2d-045e-5e23-a8ac-539783ed6e25 | note | Acceptance / Conformance Criteria - RC pipes shall comply with AS/NZS 4058 for the class nominated on the drawings.
4cefca3e-c621-5384-a3a7-52d9d3957ef4 | note | ○ Pipes shall be rubber ring jointed unless otherwise shown on the drawings and rubber rings shall comply with AS1646.
4b3af587-9683-5923-b97a-2bfc64d92402 | note | Standard / Specification - Aurecon Civil Spec Section 17.11.1
d957498e-344a-57b7-bc91-3d990a19576c | note | Verifying Document - Material Certificate / Datasheets
bac41fe5-9ce6-59c4-b3ab-d1c73971b886 | note | Frequency - Prior to use
ac78369b-cfc5-5723-96e4-2361a3ea32fb | note | Verification Activity: Activity - R
4448271c-aec9-5d34-8708-fcdef0f9b7ee | note | Verification Activity: By - DES
a1d7b594-a2e5-4b36-9cdd-49a30fa661b0 | checkpoint | 4.01.02 - uPVC pipes
f0683e84-9738-50b3-a41d-35b92162d092 | note | Acceptance / Conformance Criteria - uPVC pipes shall comply either with AS/NZS 1254 or AS/NZS 1260 and have the minimum strength as detailed on drawings
34947458-a0d6-5828-ba75-4190b714238e | note | ○ Pipe joints to be factory‐made spigot and socket, flexible type
8b2d6460-6cff-5daa-b6e6-7f8288a29694 | note | Standard / Specification - Aurecon Civil Spec Section 17.11.3
2f44b398-a028-5729-9e98-860cb7cc8c61 | note | Verifying Document - Material Certificate / Datasheets
84214fde-6e5e-5352-9163-1b824e0d5510 | note | Frequency - Prior to use
fcdf153b-3aca-58c7-a3bf-d188895bcd64 | note | Verification Activity: Activity - R
9bb0cce1-3ec6-5419-8760-d7c55f74dc34 | note | Verification Activity: By - DES
7e0ecffd-10d8-4ee8-8516-79c11f006f55 | checkpoint | 4.01.03 - PE Pipe – Profile Wall
9a308a55-0860-5992-9be5-44b36c805e80 | note | Acceptance / Conformance Criteria - PE pipe to be used in gravity situations shall be PE100 Profile Wall pipe to AS/NZS 5065.
aed94f90-05ff-55a9-91c5-c36e1f1afcbc | note | Standard / Specification - Aurecon Civil Spec Section 17.11.2
35bad388-3360-5371-b7d9-77932a998b8b | note | Verifying Document - Material Certificate / Datasheets
6cad8bac-24a2-58fa-a02e-35d4e65dc46f | note | Frequency - Prior to works
a04ea7b9-a44d-5eb9-8261-97022c172090 | note | Verification Activity: Activity - R
b9872fda-1592-5ae4-941b-92c0d17856e2 | note | Verification Activity: By - DES
bd47eec3-a6f8-49ca-805c-35fcbc826807 | checkpoint | 4.01.04 - Other Specialised Materials
23d596fc-3fa7-5ae4-a8c0-c4b3e8b0ffde | note | Acceptance / Conformance Criteria - All other pipes and pipe fittings supplied as per drawings, including:
8d607cc9-c0b6-5df4-b5fc-7a77c38c3ccd | note | ○ Any Mortar Lined Mild Steel (MLMS) pipes manufactured from arc buttwelded steel tube with external black HDPE coating. Pipes joints to be flanged, welded hemispherical joints or jointed with welding bands.
be72994b-f283-591d-a395-ca199073eac8 | note | ○ Gibault Joints assembled as per manufacturers recommendations
3eb05f78-a6db-5899-8f27-69377fc491cc | note | ○ Flanged Joints made with moulded rubber gaskets or jointing rings as per spec. All proprietary products supplied and installed as per manufacturers instructions.
26689c0a-4f0e-5284-9764-c5cb9f2e9ac4 | note | Standard / Specification - Aurecon Civil Spec 17.11.5,17.11.6
737bfd8a-2e51-50a6-8bb2-b254641c9aeb | note | Verifying Document - Material Certificate / QA Sheets
f7d167bc-441a-50fe-a6ae-2bda3a7f34e9 | note | Frequency - Prior to Use
911ec583-2bc6-5bfc-820b-45d0ad9e6435 | note | Verification Activity: Activity - R
a28b0823-fdf8-55cc-8bd4-2d6e9f9cda4f | note | Verification Activity: By - DES
72a56231-7abc-44ef-885c-6aaf5ad520f1 | checkpoint | 4.01.05 - Concrete
127c0086-aff3-57e8-9c26-e03167393225 | note | Acceptance / Conformance Criteria - Any structural concrete or mortar mix requirements as per Section 14 of this civil spec.
9819d098-86ad-5654-bd5b-242509481579 | note | ○ Site concrete used for pipe bedding to be 1 part cement to 7 parts AP20 with water as required to produce firm, moist mix with min 10MPa 28‐day strength
7defe212-9dbe-50da-976a-ab20cf25d894 | note | ○ Arrange pre‐pour inspection with Engineer 1 day prior
506a82f4-c60f-51c6-a67c-56c06132ec5a | note | Standard / Specification - Aurecon Civil Spec Section 14,17.11.7
cd472632-f0f8-5553-a4d1-1cc26f09f46d | note | Verifying Document - Supplier Records, Concrete Dockets
149e14bd-6c58-531f-b542-fe6bfbc6d42a | note | Frequency - As required
7ed4c668-3f4f-5693-8b1e-9d8a5fcac2a3 | note | Verification Activity: Activity - H
3745e15d-fe1e-5e5a-8359-2e5960a922b7 | note | Verification Activity: By - PE
2b22b82a-c061-4034-995c-408cdd287b85 | checkpoint | 4.01.06 - Pipe Bedding and Backfill Material
debfae14-ef3a-55b5-98fa-91e693499337 | note | Acceptance / Conformance Criteria - The basecourse aggregate shall be sampled and tested by an IANZ Accredited laboratory for Crushing Resistance, Weathering Quality Index, and California Bearing Ratio.
a03d4765-5fb9-5c33-945c-d1720efc57d5 | note | Standard / Specification - Aurecon Civil Spec 17.12.15 TNZ M/4 Asset Owner Specifications
1364df2c-b6ed-5467-8ab4-0e54e447ce09 | note | Verifying Document - Material Certificate / QA Sheets
ce51d16b-059d-5684-8ab9-3b333f0090ff | note | Frequency - Prior to Use
c5b9cfa1-d202-57f0-b540-98d5abc01437 | note | Verification Activity: Activity - H
6cfc08a5-cc34-5264-8174-e6086579958d | note | Verification Activity: By - DES
cbcfc19c-9f81-4dfc-8f81-af17e67834f4 | checkpoint | 4.01.07 - Catchpits, manholes, and drainage structures
233fa766-7dd9-5a5f-b80c-37865b637a36 | note | Acceptance / Conformance Criteria - Manhole, catchpit & service pit frames and covers supplied and set to correct grade and finished level as per drawing details.Pre‐cast items manufactured and supplied as per NZ standards. Manhole segments to be minimum 20Mpa
8eedeedc-6c24-5800-9c29-160f7e065735 | note | ○ Manhole/service biscuits to be level with top of subbase.
6647dd47-6eda-590e-b7f7-dee6b0f2fe72 | note | ○ Re‐entrant corners require trimmer bars as detailed on drawings
95968c82-1db1-555c-8676-b97f79074adf | note | Standard / Specification - Aurecon Civil Spec; Section 17.11.16-18
cf6888f5-b4c9-5ca6-8f5d-daa500bcef3f | note | Verifying Document - QA Checksheet and Supplier Records
66a52d92-9afe-5042-8b89-7f159e8e617a | note | Frequency - Prior to place pavement concrete
bdb90f46-3150-5a49-8a21-2eedb579311e | note | Verification Activity: Activity - R
f64ca9f9-233b-5451-a09a-2eed002bb5dd | note | Verification Activity: By - PE
fdcb322e-f85c-432a-8b42-e0f44f21d46b | checkpoint | 4.01.08 - Step Irons - Access Ladders
1585664f-66c4-5f44-b291-8be4da1ffb82 | note | Acceptance / Conformance Criteria - Check if amended by Drawings to be Type 316 Stainless Steel or Plastic Coated.
f2163e57-1279-5bab-9bb4-f79a1bde9a7f | note | ○ Otherwise, Step irons shall be “safety type” 24mm dia mild steel to the dimension shown on the Drawings, galvanised after fabrication at the rate of 0.7 kg/m2.
2f11480c-647a-5753-a120-cabeddf52a92 | note | ○ Installation shall generally comply with section 5.7 of AS/NZS 1657 except that ladder cages shall not be fitted
95ab47bf-2125-591c-9a2c-e8f7bab25acc | note | Standard / Specification - Aurecon Civil Spec Section 17.11.19
03f3f629-b02a-5fbf-b5c3-4d4a3f4c41d6 | note | Verifying Document - Supplier Records and QA checksheet
0dde39a7-86a2-5525-8b83-3d832eb6e3ee | note | Frequency - Prior to use
64df4f6d-5416-5dd9-8fff-99a21a97493f | note | Verification Activity: Activity - R
b2d03611-494e-5951-a765-cf6135780868 | note | Verification Activity: By - PE
ff1b383d-b706-431d-9ae4-42b8e629d255 | section | SECTION 5 – CONSTRUCTION ACTIVITY – DRAINAGE INSTALLATION
9d4d0c9e-435e-48f6-84db-f2992a12a460 | checkpoint | 5.01.01 - Protecton of Piplines
f78a821e-415f-5e2e-b73d-12755d4c10c2 | note | Acceptance / Conformance Criteria - During construction, the Contractor shall be responsible for the protection of all existing and new pipework.
79d110c4-a6f1-5a7b-9c4a-d4bb116e1575 | note | Standard / Specification - Downer
d5f090a2-98e9-5bb5-9c33-317628bfec03 | note | Verifying Document - QA Checksheet
7aa323ce-0bf2-51aa-bed4-bea82733419f | note | Frequency - Daily
e11d4164-f482-5196-b2f6-cfe5399e7ed0 | note | Verification Activity: Activity - I
bb8094cd-984d-53e2-ab88-a054c27a114a | note | Verification Activity: By - PE
a345a459-81d5-401f-9b6c-5efc0032e920 | checkpoint | 5.01.02 - Depth of Cover
243d57b8-72c2-5de5-8e07-495866fa8eb0 | note | Acceptance / Conformance Criteria - The minimum cover as detailed on the drawings.
52dd0f39-9f8f-5b99-9415-0d0f0bb8259d | note | ○ If minimum cover cannot be achieved notify Engineer and provide adequate protection to the satisfaction of the Engineer.
f932b781-7a84-51f9-8eb8-5480477b8911 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.17
63690037-5f08-537e-b78f-7239f40fa81e | note | Verifying Document - Site Record
cb9cd2d0-c8d0-5f02-b5f3-c8f666eacf4f | note | Frequency - During Installation
0e7f727e-040d-5830-a7ad-691f2a2c6464 | note | Verification Activity: Activity - R
378d59e2-471b-5ae4-9551-fa2d5219ec41 | note | Verification Activity: By - SE
782406fe-3996-4549-8990-75ef934d7938 | checkpoint | 5.01.03 - Length of Open Trench
be4d85dc-0814-58ae-b359-044c531fa8f1 | note | Acceptance / Conformance Criteria - The length of open trench shall not exceed the greater of one manhole length or 30m and when offsite this open trench shall be reduced to a maximum length of not more than 10 metres.
c1fc1e3f-0427-5c6d-8d7f-ceed5d0837aa | note | Standard / Specification - Aurecon Civil Spec Section 17.13.3
f60db694-6383-5f4c-8200-de2a6a2562b0 | note | Verifying Document - QA Checksheet
b02390a5-ab99-5a50-9c7c-467ae16684f5 | note | Frequency - Daily
cc9e8e61-6d2f-521e-9214-3253db507e97 | note | Verification Activity: Activity - R
a65c64cd-9b3b-56cd-887c-d2a6ae05f037 | note | Verification Activity: By - SE
5b80427c-41a2-40c3-b07c-5a2a6584f46d | checkpoint | 5.01.04 - Trench Dimensions
7bbb3f16-a2d4-57be-b31f-e6d1fd87fe10 | note | Acceptance / Conformance Criteria - Excavate trench to lines, levels, width and gradients shown on drawings.
9b504735-98aa-5d86-a5d7-1db6b1b9cceb | note | ○ Trench of sufficient width to permit installation of all materials and fittings.
a874d695-57ab-5bb3-b931-01c9114413f3 | note | ○ Pipes minimum 100mm from trench wall.
492749dd-1523-5761-b1b5-d6da9aa5d14f | note | ○ Trench width <600mm pipe diameter at top of pipe level.
29734e0c-11ca-5ec5-8e90-7f62f02dac9c | note | Standard / Specification - Aurecon Civil Spec Section 17.13.4
8c7ca7c7-788d-511b-aa79-e1397c8aeff1 | note | Verifying Document - QA Checksheet
b21a2c41-b238-5a2d-adf3-6f9bdc934c18 | note | Frequency - Every 10m
9416b7bc-a97d-5f66-bc1c-8a231bdfbd3d | note | Verification Activity: Activity - R
1eafbd54-b51c-50ce-b6ee-98564bf17c0f | note | Verification Activity: By - SE
5fdf8d9e-095f-4361-89bb-27b8cb8ec707 | checkpoint | 5.01.05 - Keeping the Excavation Free of Water
1a850783-2d0b-582e-a04f-6a1c76590acf | note | Acceptance / Conformance Criteria - Subsoil water shall be kept below the metal foundation
141cf7f6-e550-5f0f-af0e-a79cb3d9383f | note | Standard / Specification - Aurecon Civil Spec Section 17.13.5
1cd856c6-f750-5b18-a059-93049a8ed452 | note | Verifying Document - Site Record
2fac5181-acf0-57ba-b625-13a4d0d8672a | note | Frequency - Daily
69db99de-4638-53fe-99bf-b4a5cb5f4e8a | note | Verification Activity: Activity - R
9849c5af-a222-52aa-bac6-f9d48347e9c0 | note | Verification Activity: By - SE
89ca5935-9df6-4b6a-83c0-313c4a7c8d7a | checkpoint | 5.01.06 - Trench Subgrade
045a70b3-71d5-5287-b9e6-1d9ecd5a009d | note | Acceptance / Conformance Criteria - Trench subgrade to be inspected to assess if suitable for pipe laying or construction to proceed. Advise Engineer if unsuitable
040755ef-c1a0-5c4a-a018-520ed2ae7428 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.9
31180b77-512b-51cb-b23d-5f2c07b62905 | note | Verifying Document - QA Checksheet
973ed82b-de82-5f5a-954f-2255a59abbd6 | note | Frequency - Prior to pipe laying
552ba684-0153-5b26-a150-96e9121023c2 | note | Verification Activity: Activity - I
a5e69fa0-b3a2-577b-a9aa-bd02a31b1c94 | note | Verification Activity: By - SE
b014b3a8-e695-4f36-90b8-a1a4ee48c3d0 | checkpoint | 5.02.01 - Line and Level
1dc26ab6-a3fd-5455-8d0a-2e116f3feb33 | note | Acceptance / Conformance Criteria - Pipes laid to line +/‐25mm, grade and invert level shown on drawings. Lateral tolerance +/‐25mm from centreline between manholes or change in grade.
bab9ffc4-45ce-53ac-9d04-4cf32bb9532f | note | ○ Engineer notified prior to pipe laying.
3ea82a8d-8547-5028-b673-da7ff2fa58fd | note | ○ No pipe laying shall be carried out without Engineer being notified 24 hours prior
26db5922-2ff0-518b-83a4-ac59cb83f6c8 | note | Standard / Specification - Aurecon Civil Spec Section 17.13.16
42c6fb70-72aa-5cff-8a2f-3377e7ef102a | note | Verifying Document - QA Checksheet
cf15610b-6709-56bd-8349-680cd7f3e761 | note | Frequency - Before Backfill
c2065efc-7a74-5eb8-928d-f9a1bf197541 | note | Verification Activity: Activity - HP
cd506cb8-369d-538d-a2cc-c27971e5e235 | note | Verification Activity: By - DES
d55230cb-87fc-47e6-a50d-3a73a887e4df | signoff | AUTHORITY HOLDPOINT
5e31d25d-ad2b-4c81-a38d-b41c1f84f1a8 | checkpoint | 5.02.02 - Cleanliness
0af505bb-9062-5fcf-821c-26439672b306 | note | Acceptance / Conformance Criteria - Internal pipe walls shall be kept clean and free of all dirt, rubbish and water. Spigots, sockets, rubber rings, etc. shall be thoroughly cleaned before jointing.
78d5aea9-466e-5f0d-a183-2076429b8ac6 | note | ○ Pipe condition inspected prior to laying and line checked prior to backfilling
8cda70bb-97fc-54db-8fc5-858a07049eac | note | Standard / Specification - Aurecon Civil Spec Section 17.13.16
d0e5cbca-1d5f-5644-a551-010c0a583b7b | note | Verifying Document - QA Checksheet
3f6c573c-8dcc-58ee-861a-884d28cea776 | note | Frequency - Before Backfill
47625cff-e74d-5e8f-a2c1-5a53769a4b4c | note | Verification Activity: Activity - I
02e1e9a2-a583-5c28-b078-8ff18d52c72f | note | Verification Activity: By - SE
046e59e8-5098-48d7-9b9f-f2b2e560e0de | checkpoint | 5.02.03 - Bedding and Haunching
0e03011d-35c8-55b1-a15b-e5013c4064f5 | note | Acceptance / Conformance Criteria - AP<12 granular bedding material.
6618dfb2-3482-5ed7-8258-cedfd360ea1d | note | ○ Any sand used must be clean and well‐graded
7e475510-b6e6-57a2-8ca4-ceb444d44b49 | note | ○ Bedding and Haunching ‐ Clegg Hammer test minimum CIV of 12.
9d5c5a5a-b214-5b1c-8300-643623b45267 | note | ○ Results to be attached to checklist with photos.
5a6ce6de-cbee-5660-82b7-99dfc8a78011 | note | Standard / Specification - Aurecon Civil Spec 17.13.15
376eb8ad-6cac-55f1-b695-99daab7e05c0 | note | Verifying Document - QA Checksheet
81db3dc3-e702-50f6-b52e-90ae10f9e12b | note | Frequency - Every 10m
108ad5b7-4411-5c64-9af4-4f6c3a252c0c | note | Verification Activity: Activity - I
7b6b7c6a-d6cd-5b12-ab9d-683a8a86316e | note | Verification Activity: By - SE
59cfeed2-39e8-417d-9875-047bf9ef91be | checkpoint | 5.02.04 - Backfill Placement
31cff7bd-ce3c-5d2a-98f7-300be39ccfa3 | note | Acceptance / Conformance Criteria - Subbase quality AP65 granular backfill material to be used. Backfill and compact in 200mm layers.
859bb964-f286-5354-8b79-953ac6b7b317 | note | ○ Clegg Hammer test minimum CIV of 25.
bf6beecb-8536-5fc1-9593-ca8b2a7cf2c8 | note | ○ Results and photos to be attached to checklist with photos.
f82a8456-66a6-5a5c-b098-f0414837cf81 | note | Standard / Specification - Aurecon Civil Spec 17.13.15
a87877e6-3a4f-58e5-8ca5-579b593d536d | note | Verifying Document - QA Checksheet
9f6d7840-3e3c-5c3e-b04e-3e7b7697a536 | note | Frequency - Every 10m, in 1m lifts
c7fa6895-b54e-5487-b72d-73aa626da828 | note | Verification Activity: Activity - I
313ab56a-1c6b-5fee-aa8e-7f13da98b7d6 | note | Verification Activity: By - SE
556adb63-ec3d-44e1-a072-47b950b882e5 | checkpoint | 5.03.01 - Alignment
2a5507d3-41b5-51b8-815c-939aa47e5f26 | note | Acceptance / Conformance Criteria - Structures shall be positioned within 50mm horizontally of the location specified. All structures shall be watertight.
49ac3cb9-39f3-5e13-935c-97f134f6cf65 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
2fe2fa2e-8943-5a1e-8d39-51e02b34df88 | note | Verifying Document - Survey
d7353356-07b5-54ce-8b57-50bfe29a6e1b | note | Frequency - Each Manhole / Sump
74294371-5786-5745-9d73-973c301e8a47 | note | Verification Activity: Activity - C
e9d2e9ca-bdd0-5e6a-b104-7de62da52ae6 | note | Verification Activity: By - SV
eac41a61-564e-40df-a0ea-ef7181a260b8 | checkpoint | 5.03.03 - Drainage Structure Bedding
4b498e0e-de7a-54d8-8d7f-a76b8497ee04 | note | Acceptance / Conformance Criteria - Unless specified otherwise, all catchpits, manholes and other stormwater structures shall be founded on a minimum 150 mm bedding.
4db72a30-e2e5-57b7-b66c-76776888b6b8 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ac1a6220-36a3-522e-84d4-94618443f944 | note | Verifying Document - Site Records
9033a582-6abe-5407-b070-f17ffb48a613 | note | Frequency - Each Structure
23d9e508-9f50-53d3-b76e-81a7c148f583 | note | Verification Activity: Activity - R
4934ccd7-bd99-5921-8a57-22c572bdf8ad | note | Verification Activity: By - SE
03b960bc-b12f-4950-b50e-d4db8496a770 | checkpoint | 5.03.04 - Structure Backfill Testing
0b165c62-5756-5fdd-adf3-2e8134ae5072 | note | Acceptance / Conformance Criteria - Subbase quality AP65 granular backfill material to be used. Backfill and compact in 200mm layers.
7eb5fa30-0f81-59d1-917b-ed5246af465b | note | ○ Clegg Hammer test minimum CIV of 25.
1a7d9ceb-aa73-5e38-8f37-7494e8003176 | note | ○ Results and photos to be attached to checklist with photos.
a962c154-f6d6-534b-9b7d-c8ea96fb372a | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ffdde332-faf8-5fa5-955f-2be833774552 | note | Verifying Document - QA Checksheet
1b7f3a69-5b6a-52d6-9718-06a9783e4e45 | note | Frequency - One test every two layers per manhole
79a72f65-0b70-5915-871c-3777d3742d5c | note | Verification Activity: Activity - I
66926283-1cc5-5eaa-be19-58d5c86805b8 | note | Verification Activity: By - PE
2c9922e0-de78-4e14-8353-3209a20a8525 | checkpoint | 5.03.05 - Pipe Penetrations
83b73fc2-341d-58cf-b1ee-bcfa8ce2f6bf | note | Acceptance / Conformance Criteria - Pipe penetrations shall be formed by drilling holes around the line of cut before knocking the section out.
2beea6a6-ff8f-5576-8b40-234266f13fb3 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
ecae186e-1d05-50b8-955b-3594be52ac23 | note | Verifying Document - Photo
53200386-00de-5655-8178-677dd359fcd2 | note | Frequency - Each Structure
41efd525-3470-5d13-8f14-e3576d1e8f45 | note | Verification Activity: Activity - I
29bbe744-ff00-5809-8d73-b167c394b396 | note | Verification Activity: By - SE
0eddba25-2fe6-41d3-be93-96000b567d92 | checkpoint | 5.03.06 - Benching
eaf9f5d3-a6c5-5d92-8855-f67ecb80ff03 | note | Acceptance / Conformance Criteria - The concrete shall be rendered to a smooth finish and shall slope towards the channel. Particular care shall be taken to create smooth transitions at bends and junctions. Benching is to be in accordance with the drawings.
7f3b5d67-b357-52c5-8753-8da01e36fafd | note | Standard / Specification - Aurecon Civil Spec 17.13.18
2adc6455-2808-541b-b0d1-b986691e25dc | note | Verifying Document - Photo
b2ac9386-30e7-5dd4-a84d-cc6ae1997cec | note | Frequency - Each Structure
95477da3-238e-51aa-add5-33e48d8c1ae9 | note | Verification Activity: Activity - I
38b41d58-202b-5267-8310-293674658199 | note | Verification Activity: By - SE
5aede6b2-5baf-4f6b-b59d-3aeb04c8aa63 | checkpoint | 5.03.07 - Corbels
1b629889-2871-5781-9f4d-dddbcbaba577 | note | Acceptance / Conformance Criteria - Pipes shall be haunched and surrounded with concrete to a minimum distance of 200mm from the outside of the manhole in accordance with the drawings.
859eb528-5317-5bdd-aab8-70e7d22ccc74 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
e23c89f6-06b4-5a66-8467-7639c84b79d8 | note | Verifying Document - Photo
d8a7d9df-3370-516b-9aa8-d3162a6b57bb | note | Frequency - Each Pipe Entry
69b1725a-de06-5132-9d7e-aae25ff4b67f | note | Verification Activity: Activity - I
33423871-d2c8-5027-b60a-52d3a1813216 | note | Verification Activity: By - SE
37427201-020e-4f11-a046-9227ab94f4f1 | checkpoint | 5.03.08 - Pipe ends
311454d8-7750-5305-bfa0-62161cf191b0 | note | Acceptance / Conformance Criteria - Pipe ends shall finish approximately 50mm beyond the inside wall and be plastered with cement mortar or encased in benching concrete in accordance with the drawings.
29347e21-4363-5305-ba64-93dc74f0fc52 | note | Standard / Specification - Aurecon Civil Spec 17.13.18
3ab18a1e-6d14-5f42-a592-00c340041c51 | note | Verifying Document - Photo
20660926-01af-5155-a4a1-d5b33f753b57 | note | Frequency - Each Pipe Entry
00572355-483f-5c33-8ca3-27da9b3d4a98 | note | Verification Activity: Activity - I
1aa6d669-cf88-55fd-8da4-15ecba24dfcb | note | Verification Activity: By - SE
028d0e8f-10d6-4127-b82f-dd68ba26687e | checkpoint | 5.04.01 - Pipeline Testing
c9c20f4b-5d5c-5920-ad5e-e43b398641d7 | note | Acceptance / Conformance Criteria - Pressure test wastewater and stormwater pipes; PVC, steel, GRP, ductile iron and PE pipelines, rising mains and connections for water tightness.
91c966f2-5075-5998-ac40-f400b6658114 | note | ○ As‐built location of all manholes, surface level of manhole lids, depth to invert of outlet pipes, junction locations relative to downstream manholes
4bcd055f-a961-57fe-bb46-e4291484cb8e | note | ○ The Test must be witnessed by the Engineer or their representative. A record of all tests shall be made and forwarded to the Engineer within 24 hours of test completion.
d621b457-ce52-5ff9-920e-36f0e7c02b1d | note | Standard / Specification - Aurecon Civil Spec Section 17.12.22 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
321a7d50-135d-5862-bc12-94d5d44d1a02 | note | Verifying Document - Test Report
31a8e963-b89f-5957-b157-a88f7d6d4f62 | note | Frequency - Each Pipeline
669bbe73-8c21-5e90-8042-7f3d8181bc33 | note | Verification Activity: Activity - HP
b3b3e6aa-7e64-5d56-b7ba-c40a9dc0a534 | note | Verification Activity: By - ENG
601600f2-7244-4a09-93df-b7ca16ba4d87 | signoff | AUTHORITY HOLDPOINT
2666c36a-10f2-464a-9c34-135ae2cbdccd | checkpoint | 5.04.03 - CCTV Inspection
1b3fecfc-5de0-529b-b0d9-75eb6eef726d | note | Acceptance / Conformance Criteria - Lines fully flushed immediately prior to CCTV inspection.
8a253ffa-1890-5286-88d5-6988f6dae2b7 | note | ○ Inspect pipelines for correct line and grade between manholes. Pipes to be checked for visible infiltration and debris. CCTV submitted and reviewed by Engineer.
90689c79-3a91-5e81-9584-d79d797e00fd | note | Standard / Specification - Aurecon Civil Spec Section 17.12.23 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
2daa0de8-d726-5248-aba6-9bc43aecc181 | note | Verifying Document - CCTV Logsheet and Video
5f6d054c-e05a-5c0c-84f3-08441032f183 | note | Frequency - Each Pipeline
dbf10a59-2fc2-57b2-9172-c5ce43d61a3d | note | Verification Activity: Activity - HP
412477e5-c12d-57b9-b106-5e308f36fd52 | note | Verification Activity: By - ENG
e04848e4-2203-40f3-a22c-67c350706bb7 | signoff | AUTHORITY HOLDPOINT
2810c580-f74e-4b0c-85ce-c90fbd2f4943 | checkpoint | 5.04.04 - Manhole Testing
8ecf99e3-5f32-5fec-aa61-267e0b0bcaf1 | note | Acceptance / Conformance Criteria - Manholes and pipelines shall be checked for infiltration. Visible leakage in manholes and pipelines shall be rectified prior to acceptance.
02cc5bb6-a588-54bf-a86a-e710a85b8c0f | note | ○ Stormwater Manholes shall be free of visible faults or permeable zones and jointing or penetration repairs shall be to best trade standards
39b73db0-83a0-5c5b-988a-37efa896a833 | note | Standard / Specification - Aurecon Civil Spec Section 17.12.22 NZS 2566.2; Section 6.3.4.1 & 6.3.4.2
2b418a15-749f-59de-9ef5-d102ecb8af8e | note | Verifying Document - Test Report
9ad4f95d-15c0-5e6d-8f08-8f30d38e3576 | note | Frequency - Each Pipeline
affac232-4189-51dd-aa94-d531cef68068 | note | Verification Activity: Activity - HP
c52cc343-043f-5fb5-939a-8f2d5baf385c | note | Verification Activity: By - ENG
6786d93f-3dd0-4a03-853e-ab7f662202fb | signoff | AUTHORITY HOLDPOINT
6eff4f33-dac8-46f2-a493-858539323533 | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
dc05f96a-a9fe-4d5d-82dd-a10d3cdd1d5e | checkpoint | 6.01.01 - Construction Record Compilation
05fbf73c-b0c6-56dd-80b6-5af9fd47d612 | note | Acceptance / Conformance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
19053b39-aed1-5dac-aff5-6291198d3e79 | note | Standard / Specification - Downer
da20a950-2ef9-5833-8b40-b8a1794cbe3e | note | Verifying Document - Records
b52aceb2-c1bb-59fa-b386-46d3beda53c4 | note | Frequency - Post construction
ef181242-248a-5bcf-ba38-f1b93c6b1026 | note | Verification Activity: Activity - H
1fc31b8b-de60-56c5-a91b-27c074c62c12 | note | Verification Activity: By - SE
2a0db845-2476-4923-a971-74ef5157458b | checkpoint | 6.01.02 - Survey Records
da632324-26f1-582a-8fa3-fa3c6969a5a0 | note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting
98c2e71c-7c50-594e-aa1c-ff53238a0954 | note | Standard / Specification - Downer
598a8fd3-ffb2-55b6-b661-8f347a1ef381 | note | Verifying Document - Records
f27f5dbe-c222-55cc-8ee6-1a1a8ccca456 | note | Frequency - Post construction
5cbc269f-c871-5c8d-9585-13da86cbdfc3 | note | Verification Activity: Activity - H
5fd576f4-8fa0-5d10-b66a-2176e126a5dc | note | Verification Activity: By - SV
7c69b0d0-63c3-4a9a-aa46-c306afd7ce16 | checkpoint | 6.01.03 - Redline Drawings
c8c39aed-40ea-5a9b-8ba4-634a45caf263 | note | Acceptance / Conformance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen.
a0f9ef5b-e757-5ec2-ad2e-41496c8a59da | note | Standard / Specification - Downer
d78c191f-c650-541d-8a9c-537abc151cf4 | note | Verifying Document - Redlines
ecf17b12-8c1c-52a3-93fe-311df23fa837 | note | Frequency - Post construction
6a2301fa-118d-5b70-b9eb-b2e594de4d33 | note | Verification Activity: Activity - H
68d587cc-b4d6-5a4b-a78e-6a48f93b8c2f | note | Verification Activity: By - PE
bce5c348-70ed-4be4-9eb8-50372ce6715f | checkpoint | 6.01.04 - Defect, Snag and Punch List
664c81e5-ec5c-5003-9536-cd943d060457 | note | Acceptance / Conformance Criteria - Update the project Defect, Snag and Punch List Register
2c9185e0-efa9-5b1c-a558-e32bf0bf5f85 | note | Standard / Specification - Downer
d5793ac7-8cd3-530d-be9a-13f47f79a130 | note | Verifying Document - Register
8fe34fcd-9c07-5651-b70d-7ec7a6e35d33 | note | Frequency - Post construction
134e9368-dd0b-5bc8-a979-a689163e74fd | note | Verification Activity: Activity - H
a379b82b-f9e6-546f-ae9a-fa068099c087 | note | Verification Activity: By - PE
df5c59b1-6213-4cb0-b11b-e5ee56e8dca3 | checklist | DN1211-003 ITP Earthworks (Excavation, Subgrade, Sub-Base) Rev1 | itp | DN1211-003 ITP Earthworks (Excavation, Subgrade, Sub-Base) Rev1
ebac3ce4-76a1-4ca4-82b7-a8373e54d001 | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
606cf8d9-7009-41b6-bcc2-4ede93c00de4 | checkpoint | 3.1 - Pre- construction
157fbb22-4ea4-50d5-9482-237ab8926b24 | note | Acceptance/Conformance criteria - Site Clearance and service location completed. Before U Dig, GPR service locate and pilot holing as required. Protect existing services and liaise with utility providers as necessary
22d3097a-e4e5-53b4-be76-70b8aa1a4629 | note | Standard/Specification - Aurecon Civil Spec 19.5
07ee89fc-d9d7-5da0-9466-719ca1ebd46d | note | Verifying Document - Service Locate or Asbuilts / Sample Dig permit
0c6cae72-ec7a-567b-9c29-740978047413 | note | Frequency - Prior excavation
0a96a486-857f-544c-a3e9-968d1682008d | note | Verification Activity: Activity - H
8007f230-1d6a-598f-93c3-2771612c95be | note | Verification Activity: By - SE
bc903a26-ed65-574e-8aca-80cf89a0c7dc | note | Downer Signature - H
346570f8-d5cf-5efb-8852-51e777c25111 | note | Engineer Rep Signature - I
a83f8854-2be9-4fd4-b0e3-e261fd7251a8 | signoff | AUTHORITY HOLDPOINT
eb898848-e2f9-4308-8008-1f9186f89441 | section | SECTION 4 - MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
40055cbc-616a-4934-bae4-103e8ebb9780 | checkpoint | 4.1 - Aggregate MAR
9868eab0-7458-5c08-93cc-0e44ef7c5b97 | note | Acceptance/Conformance criteria - Sub-Base to be ATAP40 and comply with TNZ M/4 specification for aggregate properties - At least seven working days prior to delivery of Sub-Base course the contractor shall deliver to the engineer the results of production property tests carried out by an IANZ accredited lab in accordance with the relevant NZ standards
925ba0ea-98aa-59e0-b1f9-2d92436549e5 | note | Standard/Specification - Aurecon Spec 7.5.1
47aed118-0ed5-538d-bfe5-e3eb7a7c838c | note | Verifying Document - Approved MAR / IANZ test report
7b4c8756-408d-5d8e-87c3-ae8637b1c27d | note | Frequency - Once prior Sampling rate as per civil 6.5.1
81a14423-0226-57fd-aa13-28f5ab075627 | note | Verification Activity: Activity - H
3660d760-469f-5f01-bf45-5b2ada66c767 | note | Verification Activity: By - DES
ab34d506-69f5-586c-ac19-039a95fd0a75 | note | Downer Signature - H
e837ea8e-07af-570d-aea0-3915c351c3e4 | note | Engineer Rep Signature - R
b7cde855-a79e-53e3-9661-255ba4ea77ee | note | MSQA - I
1bc870a8-b3b9-444f-9211-ced3f11c8072 | signoff | AUTHORITY HOLDPOINT
21361c49-e63f-4ad0-8ab0-eee1af7a834b | section | SECTION 5 - CONSTRUCTION ACTIVITY
83abd295-8982-4214-920c-300a46b857e6 | checkpoint | 5.1 - Excavation
7098633d-fc75-5834-a299-347057a45da0 | note | Acceptance/Conformance criteria - Set- out position completed RL marked. For excavation level
593929bf-6d4f-53d6-8995-e898c6ac0dd9 | note | Standard/Specification - Aurecon Civil Spec Section 19.11.2
593f1b25-acff-55f6-adb0-f79af0f876b2 | note | Verifying Document - ITP sign off
a8422095-4641-547c-9104-12b286310033 | note | Frequency - In Process Check
a983b4a4-9846-5014-8f4d-5dde551c376a | note | Verification Activity: Activity - V
cf62f408-c544-5b21-b438-72e8ec10dc2d | note | Verification Activity: By - SV
75a2e896-d352-5d78-8151-66aae273681c | note | Downer Signature - V
51e3cb45-3e30-599a-a348-395fd9f4eb16 | note | Engineer Rep Signature - I
86c7fffe-0147-474e-9309-e3ce5b5da214 | checkpoint | 5.2 - Site Clearance (Cut to Subgrade)
3d570f03-86f4-5479-9a18-6573f4f0f7f2 | note | Acceptance/Conformance criteria - Area of work Cleared in accordance with Resource consent andlocal authority requirements. Discovery of unsuitable materials to be advised to the engineer and disposed of or repalced as directed.
350aced9-18bf-55c2-ae5a-e97d5777c3e1 | note | Standard/Specification - Aurecon Civil Spec; Section 3.3 and 3.6
0e49ee2d-63fb-537a-9aa3-5b22c9520e25 | note | Verifying Document - ITP Sign off
be0ed320-0793-5df3-9e28-b61aa4edc96e | note | Frequency - In Process Check
1643f8b0-72dd-5280-bf7f-738c71c9c403 | note | Verification Activity: Activity - W
b5b5137f-ac4f-5b8f-b8bc-2f7238546e4b | note | Verification Activity: By - SE
47de5d40-0d17-5409-9033-98005781bfec | note | Downer Signature - V
f880de85-4560-5470-b91c-8fdb0e7a9e49 | note | Engineer Rep Signature - I
4e206f62-7d4c-47ab-8372-336534cc3a8e | checkpoint | 5.3 - Discovery of antiques and valuables (If applicable)
b1e5327f-439c-5d91-981a-0023e8f7bd8c | note | Acceptance/Conformance criteria - Arcaheology: Works to be completed as per CMP Archaeoligical discovey protocol, records in site diary and Aconex sent to the Engineer. Antiques: Owners must contact the Heritage New Zealand for authority to proceed.
68264534-94b3-5e19-b19e-c2d36079abaf | note | Standard/Specification - Aurecon Spec 3.10 and Heritage New Sealand
0adbbf03-33b1-5fe0-b874-45ebbcfa67a7 | note | Verifying Document - ITP Sign off
f137ac76-6c26-5c6a-bf66-3e0c5617f41c | note | Frequency - Upon Discovery (May not be Applicable)
ae3ae940-513a-5af9-8e1e-c466c9cbf5a8 | note | Verification Activity: Activity - H
afa7ae41-c303-5c76-b3ed-987d778b4aea | note | Verification Activity: By - PE
fd5a099b-5265-57f3-9245-e2f5670c1636 | note | Downer Signature - H
f4e3fe3a-ed0f-53fd-99b2-3ccce10f21b7 | note | Engineer Rep Signature - I
9e42ce69-26a1-470c-a5e6-e31a057da1c4 | signoff | AUTHORITY HOLDPOINT
1855e229-89d4-493a-847a-c2305fbabc1d | checkpoint | 5.4 - Discovery of Contaminated or Hazardous Material (May not be Applicable)
a5950d5b-6a18-53df-be14-49203b12f891 | note | Acceptance/Conformance criteria - Contaminated material or Waste exhibitning hazardous characteristics handled and removed asper work safe guidnlines and taken off site to be tested. Hazardous or contaiminted materials disposed at approved landfills only. Volume or any disposed hazardous or contaminated materials to be recorded.
36c58dd7-15f6-5dc6-bbed-c6b59162fe36 | note | Standard/Specification - Arecon Civil Spec 4.5.6 and management plan
fb83e402-dd07-582b-8356-2b662b71d499 | note | Verifying Document - Disposal dockets (If applicable) /Site Diary (If applicable)
76c5d92f-d48b-57a9-ae46-3bee89ea5aa5 | note | Frequency - Upon Discovery (May not be Applicable)
caf118b1-acca-5221-8683-74042975bc94 | note | Verification Activity: Activity - H
cfe7e6ae-0fd7-5535-8847-a9d12e60a255 | note | Verification Activity: By - PE
360ddcac-c852-51d1-9bfe-5bf2771b5b32 | note | Downer Signature - H
d0e6c0ec-205d-5adc-9efe-26bcee737791 | note | Engineer Rep Signature - H
4c29e538-8bcb-4755-b255-82deff80b34b | signoff | AUTHORITY HOLDPOINT
f7a7b00f-d30a-479b-85ad-b44169aa120b | checkpoint | 5.5 - Disposal of materials
a110de08-6333-50f3-855b-6dee0b411e49 | note | Acceptance/Conformance criteria - Demolished Materials sorted as required and disposed of correctly. Materials or item salvaged for re-use as appropriate
a71ee29e-f11c-5a85-ae47-f88d5745b048 | note | Standard/Specification - Aurecon Civil Spec 4.5.7
f3af768b-dc89-57e1-9e30-e7cbbbfb8543 | note | Verifying Document - Daily Diary (If applicable)
fde50e21-db3c-58b8-852a-f3d2a37fda61 | note | Frequency - In Process Check
d1161184-5ad0-5a50-b957-5d5aac4f1240 | note | Verification Activity: Activity - I
da19820d-1251-556f-ae9d-625e010635a0 | note | Verification Activity: By - SE
a041e689-37fb-5212-8aa7-2973c26ed2f4 | note | Downer Signature - I
64b962ec-f66a-4ac6-a955-e63224ddbad5 | checkpoint | 5.6 - Demolition and removal of obstructions
38d4b0a1-33d5-5670-a869-d970ace359ba | note | Acceptance/Conformance criteria - Submit works over approvlas for Relevant NUO's where utilities found. Confirm approval to remove structure or protection requirements as per Aurecon DRG's
04b3619d-662b-5e23-b977-dfb2073b46a2 | note | Standard/Specification - Aurecon Civil Spec 4.5.5
bf0ef512-35fd-5348-bd54-5f9bd36cd64b | note | Verifying Document - Email confirmation where applicable or works over permit algining with the consent
5f2715d4-9855-56a4-871a-9adb593598c3 | note | Frequency - Upon Discovery (May not be Applicable)
e5082e0c-55dd-5a67-ab38-ea92549401ee | note | Verification Activity: Activity - H
262d3331-0c4a-5f3b-8c89-623962faa9ec | note | Verification Activity: By - PE
7fbe7460-46ca-5f91-9319-81b4ca1e9b55 | note | Downer Signature - H
6a49fa33-a0e6-585f-b870-a338566908f4 | note | Engineer Rep Signature - I
9f3c6c73-3fce-48ff-ad6f-99bfcda85c18 | signoff | AUTHORITY HOLDPOINT
02904483-d669-4555-87ab-93b7753cf40d | checkpoint | 5.7 - Tree Removal (If applicable)
97f46f02-228d-5686-993d-921d7f2fac50 | note | Acceptance/Conformance criteria - Refer to Tree Management Plan, Tree Management plan certification and relevant resource consents/approvals
60c115d6-0459-5a97-9108-40663a52b1be | note | Standard/Specification - Resource Consent
fa09273b-3d37-5728-970d-9eeced8e9955 | note | Verifying Document - Resource consent
852dd153-fa9d-56e0-9305-85ed74e344d3 | note | Frequency - Each Tree (If applicable)
256d6084-e217-53d3-8701-885dcf9a8e22 | note | Verification Activity: Activity - W
ea11632d-8d24-58fd-9f5b-4931fb5a74f2 | note | Verification Activity: By - PE/DES/ENG
002931a8-824f-5d79-b135-89a8badf5217 | note | Downer Signature - W
f813ed7b-eb6c-51fa-88ca-f9c83cbb0186 | note | Engineer Rep Signature - I
ea04302d-7a59-5fd8-bf18-abe9a98ae8d3 | note | MSQA - R
6a08e886-62ca-4593-871f-01e88485d143 | checkpoint | 5.8 - Services/Sun Surface infrastrucure removal
a107e850-0c59-564c-9915-74e2942f1ef5 | note | Acceptance/Conformance criteria - Existing services and drainage structures to be located where possble or as agreed with the Engineer. Pilot hole, disconnect or isolate live services prior to demolitions as required. Services or pipes to be abandoned are to be completely removed or grout filled as per drawing or approval by assest owner if different.
00161e19-35a2-560c-b9c8-5e8c5e840dde | note | Standard/Specification - Aurecon Civil Spec 4.5.4 and 4.5.5
e8bdf9e6-47da-5bc3-91b6-df1f144e6a79 | note | Verifying Document - Service As built
c2a405f4-1d07-5e4f-beb2-6e8cf5fe7a93 | note | Frequency - As Encountered
536216de-dd77-5166-beaf-809bacc2815b | note | Verification Activity: Activity - H
25affd75-5a08-5df7-a1af-465552736ad6 | note | Verification Activity: By - PE/ENG
ae955d07-74ee-570b-9570-aa18c8cd4965 | note | Downer Signature - H
478cdaaf-424f-5ebb-b68a-a32ed21d0181 | note | Engineer Rep Signature - R
59f07b88-ed9e-4760-8ed1-ed7b39d5fe11 | signoff | AUTHORITY HOLDPOINT
4dc9ee90-0c60-4ad8-b0af-47c55a2b5a7d | checkpoint | 5.9 - Subgrade Testing
fc97444d-f3bc-51b9-98a7-3369ced8bf4c | note | Acceptance/Conformance criteria - Contractor to Confirm subgrade strength and report to Engineer via Inspection. Clegg to CBR correlation to be confirmed and Clegg hammer results to be undertaken on Subgrade
6c465152-0b17-554a-be31-af58575a3ae4 | note | Standard/Specification - Aurecon Civil Spec 5.6.11
9433c091-29c6-5c96-89ae-417b89721ad6 | note | Verifying Document - QA sheet
4ec44b30-3e91-545a-b42c-9c1bb82a5257 | note | Frequency - Every 20m or as agreed by the Engineer
570e64a5-e02e-5b38-9c22-4e89778271bf | note | Verification Activity: Activity - H
2f2bd57a-d373-5d26-b428-72a36dd10a42 | note | Verification Activity: By - SE
6c0768d2-fcf3-5e29-9d01-42ec9f513e62 | note | Downer Signature - H
b93f016c-1858-533d-b13e-c718b0abc5e4 | note | Engineer Rep Signature - R
361d83a3-c4d9-5d04-847f-40da3e8c5a74 | note | MSQA - I
ad55ab19-8dcd-4b22-a15f-4bb2c3c215c9 | signoff | AUTHORITY HOLDPOINT
46cf1ae4-2abc-4964-9802-d39217a6d20e | checkpoint | 5.10 - Line and Level of subgrade
e889b0e8-a240-5e5b-8f34-d062f8b1c56a | note | Acceptance/Conformance criteria - Pavement Subgrade tolerance +/-10mm from design subgrade level (or as applicable with existing services). Excavation depth must be at least the design pavement depth for LMC locations. Subgrade shape as per survey set out. To be verified on site.
079c8333-a85c-55ef-a2d9-5c6d7b931b8b | note | Standard/Specification - Aurecon Civil Spec 5.6.9
7906a528-51e2-56a6-8fdd-d527b80dcbc3 | note | Verifying Document - As builts
5c467d89-dfb6-50d4-a49f-7b1d2800d826 | note | Frequency - Each Subgrade section
22bd7e11-7e29-5647-86e0-9708c8ae93af | note | Verification Activity: Activity - H
837ed48a-1fcc-537c-beb0-704a6760876a | note | Verification Activity: By - PE
69825dc7-693e-50f1-9a20-e81ea11c586a | note | Downer Signature - H
18604b0f-6b02-56c1-9b58-ecc9e029f85c | note | Engineer Rep Signature - R
2d37b44a-884e-50b7-84df-928cb6c66e3f | note | MSQA - W
c743d327-ae7a-4725-b793-dfc5a325457b | signoff | AUTHORITY HOLDPOINT
9b21aef5-7408-410e-b9fc-032a46c91bd4 | checkpoint | 5.11 - Sub-Base Level and Shape
588be7be-6e30-551e-8f09-c797d901f25e | note | Acceptance/Conformance criteria - Construct lifts between 2.5 to 5X maximum stone size to ensure good compaction (100-200m). Surface shape, finished and tolerances shall comply with requirments of TNZ B/02- -25mm/+5mm to design FL measured between centreline and pavement edge
d71381dc-fc9c-5f7e-8852-893040aa1e3b | note | Standard/Specification - Aurecon Civil Spec 6.7.4 TNZ B/2
c176cf89-f3a5-5be5-9f24-6d95fe6eb353 | note | Verifying Document - QA cheetsb and as built survey
3973c77d-fbbb-54f5-b51b-6b1b409bd435 | note | Frequency - Every 10m for each section of basecourse
dd7fbdff-a4f7-5680-bac4-6284151dae17 | note | Verification Activity: Activity - H
7671a628-e26d-58af-99e1-c12fab35228c | note | Verification Activity: By - SE
e1684dac-5122-5af0-871e-9b688e07cc25 | note | Downer Signature - H
dd4fbd72-f00c-59bd-bc13-ff660080c6b7 | note | Engineer Rep Signature - R
718c53cf-2093-560f-a225-715191388940 | note | MSQA - I
e2394237-bc53-4c74-8efc-15190151027a | signoff | AUTHORITY HOLDPOINT
cf422c2b-29e2-439a-a589-d17fcc3e95c7 | checkpoint | 5.12 - Sub base Compaction
479759f4-3e36-5e94-8da6-4ea70c6cf306 | note | Acceptance/Conformance criteria - Clegg testing of Sub0-base course to achieve CIV 25+
fb734540-9b9b-57f1-8081-a81fcf76f40f | note | Standard/Specification - Aurecon Spec 6.1 and GCOR-0042
31628a71-3489-5133-925d-b37078bd3c47 | note | Verifying Document - QA sheets
bbfe1a67-e4f8-5f7f-a6e8-0f38e0306dcb | note | Frequency - Every 10m for each section of basecourse
ee3bfe12-2537-5010-8234-c61005550bca | note | Verification Activity: Activity - H
d612db1d-22ee-5d78-9255-797bce3aad02 | note | Verification Activity: By - SE
78906bf4-759e-5793-88d5-effa1b4f3640 | note | Downer Signature - H
3a2bb8e6-bc70-5c1b-aac9-e6c30a1898fc | note | Engineer Rep Signature - R
a7f3a6e8-cc99-5336-aa2a-3b7766109832 | note | MSQA - R
669efbcd-9528-4e29-8b19-c7cfafa9f5f7 | section | SECTION 6 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
f5cb7731-a437-43b9-912c-6093f511c708 | checkpoint | 6.1 - Construction Record Compilation
1aeb38bc-073d-5877-af21-1ae0ca612635 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
860be32e-540c-5d2a-83f7-352dad1ec7e6 | note | Standard/Specification - Downer
1a457b29-b7a6-506c-b254-2c64dd1a5612 | note | Verifying Document - Records
00d05285-75d0-5540-b5b9-ce7a901e3ed7 | note | Frequency - Post construction
05859899-8319-5466-9549-aa920c89067c | note | Verification Activity: Activity - H
10eaaa42-f6b9-5c2e-a413-3ba1648da64f | note | Verification Activity: By - ENG
a07cf5ac-49ba-55bf-8818-ea3e5f0dca4d | note | Downer Signature - H
471d7c21-4e57-5991-9a94-5d418ac70888 | note | Engineer Rep Signature - H
be898af7-2614-59f1-97a0-b203619201f4 | note | MSQA - R
2881871d-dd22-458a-a1fb-8c5784fbcb71 | signoff | AUTHORITY HOLDPOINT
50b1a8ea-8ae8-4b9c-b462-84c6e1fb87b2 | checkpoint | 6.2 - Survey Record
d8e2c646-0c30-5bec-a803-c23c7a76026f | note | Acceptance/Conformance criteria - Installation of works under contract completed compliant in accordance with all relevant regulations, COP and standards
86862847-6c91-5878-b555-367c8dab1279 | note | Standard/Specification - Design Specification / Downer
47db299b-23a8-595e-91c7-ad57531ab189 | note | Verifying Document - QA Checksheet, Redlines
534ab2f8-ff85-58af-ad61-57b6604393ab | note | Frequency - Post Construction
f7ce147c-de7b-56bf-8bde-59ea915c13fd | note | Verification Activity: Activity - H
c9adad40-e43e-5ea0-86ac-00f4e278ef6d | note | Verification Activity: By - ENG
9f92064f-8139-5351-afe9-ea07fbffbb4b | note | Downer Signature - H
6af609e7-1652-56c3-9c64-8fd02a4468ef | note | Engineer Rep Signature - H
ca1e7db9-c93e-5d54-8f98-9d2c444229fb | note | MSQA - R
f6dd33ce-c493-4f82-825d-be195118f6c5 | signoff | AUTHORITY HOLDPOINT
5ca3dbf7-58c0-4f90-900b-16da871162fe | checkpoint | 6.3 - Redline Drawings
71a5457e-fde8-5b59-93e7-db2953e9f8fa | note | Acceptance/Conformance criteria - Ensure all items have been installed create a Redline Drawings for Asbuilt creation noting all changes with RFI numbers and departures in red pen
37d886d0-9d5c-5775-8a0b-c0b4448f47d8 | note | Standard/Specification - Downer
01258fc2-089c-5982-b621-0cfaa2eab4ec | note | Verifying Document - Redlines
432d0d34-11ec-556d-84ab-bb837933d41a | note | Frequency - Post Construction
183dbda6-03b7-5a02-8863-355b29823fe4 | note | Verification Activity: Activity - H
3caf2768-a49f-5a0a-9ae3-f79336364926 | note | Verification Activity: By - ENG
27394201-33e0-51c2-9cc8-020eeebae255 | note | Downer Signature - H
d14cb95d-2691-5318-b348-c8feefbdeee4 | note | Engineer Rep Signature - H
1e1450de-3b43-5be0-90e0-0a784c6e95b8 | note | MSQA - R
15dd0b29-7aeb-47a9-b9aa-6b78508b9929 | signoff | AUTHORITY HOLDPOINT
64371508-8226-4bc7-ad39-016be4733a37 | checkpoint | 6.4 - Defect, Snag and Punch List
6849fae8-8b76-5687-be1c-9ec8c1734dd2 | note | Acceptance/Conformance criteria - Update the project defects, snag and punch list register
c75272d7-adbb-5f85-9ef2-fe7eb0f9512f | note | Standard/Specification - Downer
717cd4a3-9fe3-5a23-89c9-f9269b726c50 | note | Verifying Document - Redlines
bd5a2127-1c3f-5a50-b8a5-13fb4f2d195a | note | Frequency - Post Construction
465802ed-acb2-5d4f-b675-fe344c82c914 | note | Verification Activity: Activity - H
dd40b5ac-0f73-5231-9eaa-665eec5102ab | note | Verification Activity: By - ENG
d2f2fbba-e42b-5365-9d8b-b61bfb349dfa | note | Downer Signature - H
3547d9dd-da30-534c-bd91-86fdc6b50640 | note | Engineer Rep Signature - H
24606f30-f85c-5416-a102-9b0fe2587bc6 | note | MSQA - R
322f3ded-9ef3-4812-b8a0-07a0e54cebc2 | signoff | AUTHORITY HOLDPOINT
773654b8-ccd0-4622-b37b-bef72a23ace8 | checklist | DN1211-010 ITP Concrete for Minor Structures and Incidental Works Rev 0 | itp | DN1211-010 ITP Concrete for Minor Structures and Incidental Works Rev 0
622b2438-a268-4028-8b80-e25d57bb7b7a | section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
892256e5-635e-4ba9-8b12-79ef7e07649e | checkpoint | 3.01.01 - Construction Pack
4a8023c5-7efb-5322-899d-40ffefd8f89c | note | Acceptance/Conformance criteria - Submit a Construction Pack including a Methodology and JSEA to the Engineer before works
016c94ef-6848-57de-9612-ac4cfc228a06 | note | Standard/Specification - Downer
b769fa44-d0e7-5e86-8e75-9bc6b50235de | note | Verifying Document - Construction Pack
08ddacc5-f8f6-56b4-bc23-e6ecf3d5ab79 | note | Frequency - Submit 5 days prior to commencement of works
dd893bd7-2003-5ab8-851a-962fee109d27 | note | Verification Activity: Activity - H
01136fb3-300c-5941-9463-ab9f70533979 | note | Verification Activity: By - PE
16ecc41b-6104-5588-8061-35d7a41d31fb | note | MSQA - R
1f78f9a1-4dd8-498a-b1b4-4f4fdbebb367 | checkpoint | 3.02.02 - Survey Setout
f07b6764-1290-55cd-b897-8780b845f8a7 | note | Acceptance/Conformance criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
7eeed186-dc5a-5519-8fdc-dbcae135231d | note | Standard/Specification - Downer
df08e0e8-efac-5ad9-9eb2-3cee9cfdb2f5 | note | Verifying Document - Survey Records
00d61209-73db-564a-9ea6-a0e3ec87390e | note | Frequency - Prior to Works
aec87e12-da4a-50e4-bddf-00d2014d1562 | note | Verification Activity: Activity - H
5c7d3bd4-acc4-5041-9e9d-69fc25ad920d | note | Verification Activity: By - SV
8fb4ba75-8093-411f-896a-f5f4795205c1 | checkpoint | 3.01.02 - Service Location
e1531bf5-a884-53f8-92bc-e440c3465945 | note | Acceptance/Conformance criteria - Complete the Excavation permit process to identify, locate and protect all services.
d3281e11-9d4e-54b9-bd57-f41526e2e7e8 | note | Standard/Specification - Downer
7b288ba4-b8a7-5850-8d6b-980bbfb3d7bc | note | Verifying Document - Excavation Permit
54b79b4c-41fc-5827-8119-bd242a297d43 | note | Frequency - Prior to Excavation
fddf8601-ff7c-50b3-84f5-a17570ba2219 | note | Verification Activity: Activity - H
45d1f44e-5dba-5cd6-a71d-14ce4dde8eff | note | Verification Activity: By - SE
3a77263c-bac2-487a-825b-9f677f0b50d0 | checkpoint | 3.02.03 - Internal Permits
5a57005e-1559-53ab-833a-bbb107de5c9d | note | Acceptance/Conformance criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
85444a20-f331-5a00-b4ce-d862c4d22011 | note | Standard/Specification - Downer
14cac2f7-d153-5022-b8dc-9bc3a2b68f86 | note | Verifying Document - Internal Permits
bb8384cf-c36a-55b8-876c-edcabbabe181 | note | Frequency - Prior to Excavation
91083ccf-e70c-50c3-a14e-a41f512572ff | note | Verification Activity: Activity - H
a4fe0e9a-190e-5608-8d79-91ba7c7d7961 | note | Verification Activity: By - SE
f26fbc0b-809f-4260-8c2e-a8813fa10628 | checkpoint | 3.01.03 - External Permits
0773d4f6-1944-531b-a009-10a577705036 | note | Acceptance/Conformance criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
2101e6b3-b346-570c-8e98-afa38fc531b4 | note | Standard/Specification - Downer
9412a2cd-99fa-577e-abeb-c7dc118495fd | note | Verifying Document - External Permits
cdfa5487-4abd-5996-9fc3-1b9089f2d0de | note | Frequency - Prior to Excavation
3b509c5d-5679-56f7-af14-6f04c9ec23f3 | note | Verification Activity: Activity - H
24b7528c-9e51-5ab5-ac7d-055f1f279e7a | note | Verification Activity: By - PE
52c50d47-9186-5d5f-a154-efdaf3a822dd | note | MSQA - R
1ac81670-3c84-4137-ad20-c4cde6ca3f05 | checkpoint | 3.02.04 - Approved Construction Drawings
ce060d30-a432-5d71-8617-f1f6871e24b5 | note | Acceptance/Conformance criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
7bba1412-4185-5c6b-b775-1d00d0970ffb | note | Standard/Specification - Downer
9e74153f-628c-5c49-92eb-b8c789ba94e0 | note | Verifying Document - IFC Drawings
33b0854d-94cf-5f55-84cb-8de71621a009 | note | Frequency - Prior to works start
00bb9a9c-ebed-5026-a4f8-423c7e857bdd | note | Verification Activity: Activity - H
b111b76e-577a-5001-aea9-94a5b4bfba04 | note | Verification Activity: By - PE
44b2ec36-6e68-463c-8cd4-ff7f24786a75 | section | SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
e65e08b8-801f-4aae-bd04-4c4be996eff5 | checkpoint | 4.01.01 - Mix Design
6f29ddf7-5f7c-5810-8490-0c505fa5fd45 | note | Acceptance/Conformance criteria - Typical structures ‐Confirm supply of 'high grade' 20MPaconcrete; 19mm max aggregate size.
b68c85c3-ab23-5c43-a0b6-94b6b824ec79 | note | General site concrete
73d7cc22-4e58-5242-a4bf-ee1950718859 | note | ○ 10MPa Where specified ondrawings, use marine grade concrete
6f256e90-6bfe-5a33-8c6e-3c9f167f8f47 | note | ○ 30MPa The Contractor shallensure that the readymix supplier can provide mix designinformation andstrength testingrecords on request.
bf23ff68-2109-5982-82c9-a8c63f03ed1f | note | Standard/Specification - Aurecon Civil Spec Section 14.6
4d998f4e-ad4d-57b7-ba01-a78baefaf788 | note | Verifying Document - Mix Design Report Approval
bd64bc60-5ca8-598a-a290-17082da7b114 | note | Frequency - Upon Request / prior to Use
c700dcda-9da7-598b-8820-5728603c6cc6 | note | Verification Activity: Activity - H
6aca4692-92ec-50ff-ba89-a0adb1f5b131 | note | Verification Activity: By - PE
145f82ea-a1e2-5fbf-a32b-9d6c0ec86de1 | note | Engineer Rep Signature - R
4ad54ec5-a519-5ca8-a04d-bb87c962846d | note | MSQA - R
bc77ac5f-cbc2-45f4-a4c2-d71e605d78dc | checkpoint | 4.01.02 - Motar
e316f605-d1e4-5bd3-9e6b-b1da94f3504a | note | Acceptance/Conformance criteria - Consisting of two parts fine, sharp, well graded sand to one part dry cementMix by hand or mixer in small qunatities,use within 30 minutes
03a22fa1-af97-5985-8ee5-fcf5cc4d7727 | note | Standard/Specification - Aurecon Civil Spec Section 14.6.5
9e50c1cd-7459-5567-a8b4-092bdc767b73 | note | Verifying Document - In process check
513eb805-1e48-5b33-82bd-ab5948a19874 | note | Frequency - Prior to each pour
ce379b64-9ca3-5a9c-b845-2a8ef6850052 | note | Verification Activity: Activity - I
15725fb7-f315-5d67-b454-37af919b4b1f | note | Verification Activity: By - PE
0a7a52ce-c2ff-42be-91d5-7dfec78dae58 | checkpoint | 4.01.03 - Reinforcement
5754e492-6d17-56d8-8273-4160dc988509 | note | Acceptance/Conformance criteria - Reinforcement andembedded items cut, bent (cold) andaccurately placed asshown on design drawings. At least30mm cover to all reinforcing +5mm/‐0mmBar spacing as per drawings +/‐ 10mmBend locations as perdrawings +/‐5mm
d90ef18e-01b1-5578-8f45-cbbc0bcd371d | note | Standard/Specification - Aurecon Civil Spec Section 14.6.7, AS/NZS 4671
bcefc48d-4878-56c7-9c85-a03cf3fec629 | note | Verifying Document - In process check
015fb55e-b05a-5b0e-aa14-86df900ee31a | note | Frequency - Prior to each pour
47079d23-4450-503e-af8b-ce8fb7a79c22 | note | Verification Activity: Activity - I
8c360f37-9514-519c-9b09-dfeb789d8a72 | note | Verification Activity: By - PE
ef8aaf48-59f2-552f-b692-99bdb6cdb223 | note | Engineer Rep Signature - R
7fec4fe9-fa9b-4a3f-9ecb-e42d3a309097 | section | SECTION 5 – CONSTRUCTION ACTIVITY – CONCRETE INSTALLATION
9f2901f2-c9c8-49b1-80fd-fccc8d1b55db | checkpoint | 5.01.01 - Pre Pour Inspection Concrete Placement
be0be8fc-c113-5565-8622-4eb77110c468 | note | Acceptance/Conformance criteria - Notify Engineer for inspection of formwork 24 hours prior to pour forinspection
a4ca186f-f821-59ce-9027-8af30a2437b4 | note | Verifying Document - QA Sheet
c7667a4f-9e60-55e8-906e-28fd28b83c2a | note | Frequency - Prior to each pour
434d97fc-9998-5676-b3c0-b7548eb7a5af | note | Verification Activity: Activity - H
2b39dbcb-5416-599c-8bf6-a714c4fd07f0 | note | Verification Activity: By - SE
9e0558b3-6811-5084-ab94-5b03befea03f | note | Engineer Rep Signature - I
f0ce640d-14b4-5ced-80e0-9d2ffa79a482 | note | MSQA - I
c715e96e-1ce4-458a-93c2-fe322c35139d | checkpoint | 5.01.02 - Pour Plan
b7764a51-86dd-5f07-984b-a7b72d9fc767 | note | Acceptance/Conformance criteria - Place concrete and construction joints as per design drawings Exposed surfaces: F4 formed finish (or F5 if specified), U2 screeded finish Slabs: U3 trowel finish for internal slabs, U5 textured forexternal slabs
13adc547-4bc5-5a97-813a-bc1e22250fbe | note | ○ Delivery dockets dated and showing the concrete supplier and design strength shall be collected and held for every pour. Record location and date of each pour
13ae81e8-aaaa-5737-9665-97074ab44b46 | note | Standard/Specification - NZS 3124
983fda1a-e3bf-5445-8c5f-dbb53d2142ca | note | Verifying Document - QA Sheet Delivery Dockets
fe20b649-0ffc-5357-8633-f7647e725893 | note | Frequency - For Each Pour
84654cdb-d6f7-511b-ac81-6012ef18bec0 | note | Verification Activity: Activity - W
59b62bd1-e9be-5d65-9687-77d36cf8a9c9 | note | Verification Activity: By - SE
44fd9742-845b-5112-b82a-59544d714ba1 | note | Engineer Rep Signature - R
43db9f80-73e3-54dc-bc65-c04a36c4f544 | note | MSQA - R
d28432ed-f860-400c-84f8-47449c53ed92 | checkpoint | 5.01.03 - Testing
ce373514-50b6-5d91-b1a0-7225cf3c6df3 | note | Acceptance/Conformance criteria - Slump test during pour to check workability of concrete or as directed by Engineer 3 cylinder tests taken for each pour. Slump target as per mix design 120 mm when measured at the point of delivery to site.
6e2aabf0-df1a-56ec-819e-07c7dbe5a6b1 | note | Standard/Specification - Aurecon Civil Spec; Section 14.7.12, NZS 3112
f1bab556-6f74-5d36-8f2a-b1f8b05b001c | note | Verifying Document - QA Sheet, UCS Test Report
7b9ed90d-6c1a-57ba-80ed-8b421cacb0f2 | note | Frequency - Each pour / every 75m3 (one sample for pours less than 75m3)
4c9c7f76-1193-503f-8589-6685ec24c0be | note | Verification Activity: Activity - H
224d1046-f2a3-5acf-a5fd-32b425f802e4 | note | Verification Activity: By - SE
9c30573f-8bad-5f48-831d-fd366c50a6e0 | note | Downer Signature - H
10627c03-b062-5f27-9193-d72666cd85ba | note | Engineer Rep Signature - R
689daee3-0199-52a6-a1d6-b93a87e60d63 | note | MSQA - R
2b90febc-ea53-4836-b1a1-71f249ffa509 | signoff | AUTHORITY HOLDPOINT
e93acb74-d2df-40a7-aa48-a426116ec26d | checkpoint | 5.01.04 - Independent Testing
0c64d66e-652e-5191-92f3-baf9ee9cd48f | note | Acceptance/Conformance criteria - The Engineer's Rep may request site samples/cores for independent testing of fresh or cured concrete to review the grading, mix design, strength and thickness.
de536963-d09b-5630-8a9d-f4a7e6907d8f | note | Verifying Document - IANZ Lab Report
8e35e34f-9d36-50ee-86d4-6d32940260f2 | note | Frequency - Upon Request
e6a9cf62-e6f1-5296-b64e-95bcfc09ed32 | note | Verification Activity: Activity - W
761acbc2-a99e-5ac7-b244-3f91958fdd69 | note | Verification Activity: By - SE
8e7f0dc7-f06e-5535-84fd-52817e21abbe | note | Engineer Rep Signature - R
9c37305b-4a15-5fa3-8720-c7ccb3f5d283 | note | MSQA - R
cc1c554f-bcef-4561-904d-db1680c85c0e | section | SECTION 6 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
42515b02-ef7b-40f5-b150-33e1148c7091 | checkpoint | 6.01.01 - Construction Record Compilation
9aeaed43-0483-5191-82df-54ddbfdcf012 | note | Acceptance/Conformance criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
6700efc3-f786-56f1-ad55-7c9ace4666cc | note | Standard/Specification - Downer
2107edea-a3f4-5810-9df1-c78087f1c181 | note | Verifying Document - Records
f8e8249d-a232-5de7-be4d-54b1a7f4f84d | note | Frequency - Post construction
2fd13370-31e9-51bc-b4d1-a5fdf7ddd15f | note | Verification Activity: Activity - H
ca842d43-3f59-5dca-947c-6dc4042524ab | note | Verification Activity: By - SE
9333d873-7061-54b0-b3cb-e0dd34e550ca | note | Engineer Rep Signature - R
9fb4f35e-f9d7-59fe-92e8-6d9b433f7791 | note | MSQA - R
4683034b-813c-49cb-b645-e8b084dda74c | checkpoint | 6.01.02 - Survey Records
d2b61a3f-7cbb-558d-9620-240fd5434c2c | note | Acceptance/Conformance criteria - Ensure all items have been surveyed and records are assembled for asbuilting
127f3b87-1e8e-5465-a7b2-54e5a47f7c83 | note | Standard/Specification - Downer
d8d44068-8eba-586b-bf15-079dda7a6388 | note | Verifying Document - Records
e762692c-de24-5a53-b406-63c0ce267feb | note | Frequency - Post construction
a57b0a99-9572-5705-a658-23547269a38f | note | Verification Activity: Activity - H
cdd50653-4aab-5355-a419-2cdb4daf5612 | note | Verification Activity: By - SV
e9e681eb-cae8-5017-9336-44771768b6c0 | note | Engineer Rep Signature - R
c6643a22-dd58-5d32-815d-354c9a729f23 | note | MSQA - R
1f04b71f-e557-4366-b742-ef058f0c7830 | checkpoint | 6.01.03 - Redline Drawings
8aa4de9c-4f31-5b9d-a730-7f9dc6ac77be | note | Acceptance/Conformance criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen/RFI reference
8f2b043f-d880-52fe-805e-06d5da5ce194 | note | Standard/Specification - Downer
631d74a3-e7c8-5374-bec6-33f06f26679c | note | Verifying Document - Redlines
98c8e754-b52f-541b-9e46-ddd7311eab45 | note | Frequency - Post construction
48e9b07a-b52b-5cae-ba41-36425372402e | note | Verification Activity: Activity - H
70b9a925-5001-56a3-b47f-b830e0a9b03c | note | Verification Activity: By - PE
8826964a-c74d-52e7-9433-6d48d1283ebd | note | Engineer Rep Signature - R
ce6b6f57-51ad-5d9e-be35-904d03256665 | note | MSQA - R
1bcf1d21-9866-4b83-98fd-ae6d3aed74ae | checkpoint | 6.01.04 - Defect, Snag and Punch List
f5860d29-c37a-58ed-83fc-f40ad8fc22dc | note | Acceptance/Conformance criteria - Update the project Defect, Snag and Punch List Register
252f89f9-1c90-577c-9acb-3ebff19a06a2 | note | Standard/Specification - Downer
ef361d0e-c4b3-5430-a87c-7f06dbd1852a | note | Verifying Document - Register
0189ca1b-1561-5a10-9fc2-4868d8ac9468 | note | Frequency - Post construction
11d0a072-4c9c-5cbb-8788-26c9ae37e5ad | note | Verification Activity: Activity - H
9726a5ce-d579-54d0-869e-8ae1bf8f73d2 | note | Verification Activity: By - PE
0e6567a3-2144-5c65-b43e-330e866fae7e | note | Engineer Rep Signature - R
ef12084e-1709-5a49-9fae-8e026a43606f | note | MSQA - R
2a108de0-5d9c-405e-9e6c-1391f1b63163 | checklist | DN1211-CHK-001 Stormwater Drainage Quality Check Sheet | itp | DN1211-CHK-001 Stormwater Drainage Quality Check Sheet
d01bb0fa-981b-4257-b668-0f306a57ced6 | section | Materials
6375d497-c66c-411e-8e65-c821b8b7516d | checkpoint | Materials available and comply with specs (all materials)
dfc8a7fb-9923-5c27-ab86-aa4f27b84d37 | note | Comments - Sent to design engineer for review
f6ee3ef9-4655-4f4c-bcb1-e4cedf653d21 | section | Excavation
0b2aaef9-f488-4320-87f8-d16be8f71521 | checkpoint | Has the permit to excavate been completed
750d7c78-b56c-5cb2-bb08-c5151c3d8e64 | note | Comments - Services clearly identified (Both KR and DNZ)
a6249c29-bb87-56cd-91d7-a48b6f7b4d2d | note | ○ NUO standover on site if required
d8cf0920-849b-480e-a28a-bf2ab731bd04 | checkpoint | Set out complete
930f5fc4-91b2-5173-a32d-64345a7d446d | note | Comments - As per IFC Civil Drawings
17db364a-cf29-4213-ae66-a65ce559eecf | checkpoint | Protection of existing pipelines / utilities
ee79636b-9caf-4166-b768-2003fcef790e | checkpoint | Trench excavation to line, level and grade
512a44a1-88a9-5741-9f63-a507ff58d3ef | note | Comments - Every 10m
2b2fba20-fd9c-59ba-afa1-b1a91256db76 | note | ○ To lines, levels, gradient as shown on drawings
7df5fb38-572f-5308-95ab-c719b6df0de7 | note | ○ Sufficient width to permit installation, pipes minimum 100mm from trench wall
baa05405-c473-587e-96c1-0f64f1998c9d | note | ○ Width ,<600mm greater than pipe diameter
e5eb6bee-37c3-4fa7-b723-fd04ed8cacf9 | checkpoint | Trench excavation open length
33bda56c-2426-5500-b59c-bc83f26e5e24 | note | Comments - Not to exceed manhole length or 30m
3937519b-92a6-4ac0-a3cd-3433a30edbef | checkpoint | Materials removed and stock piled
99d6f212-7bdd-49d3-830e-175cac2ad942 | checkpoint | Bottom of trench foundation condition
f519ec45-2b30-524b-9b68-a830e6114c9f | note | Comments - Water ingress kept below bedding level
ea4cb0fe-ca55-576d-8ade-ebc14a5ab7fa | note | ○ Subgrade suitable for pipe laying
c8031554-cb2f-4a91-a18c-38150db3c5b7 | checkpoint | Over excavation required?
ded950d0-d587-5819-859c-1277ed1a653e | note | Comments - Engineer to be notified and approval received prior to undercut.
a0666b6e-f2f0-491e-bc07-8b9486f6c50f | signoff | HOLD POINT
ba394402-0b3b-4be8-9340-f1f9fd577a76 | section | Pipe Installation
a5f16f4e-ea65-4c6c-a76b-23bc4488bf77 | checkpoint | Hold point
aacd42fe-5b5e-5540-b8ca-2456368f2aaf | note | Comments - Engineer to be notified 24hrs prior to pipe laying
51add03e-2fcc-42ee-942b-162ce3bcfcac | signoff | HOLD POINT
65dd0300-17c3-4d8f-8f2b-278ff1bf8536 | checkpoint | Pipes transported to site , stored and lifted correctly to prevent damage
67eec2f8-b35f-465d-94a7-b04f9409d473 | checkpoint | Trench shield/Benched/battered
78ef0102-6181-5c8e-a32f-eafebfb34949 | note | Comments - If the trench is deeper than 1.5m
ff0fad76-9676-42eb-b206-45b8cfac80f3 | checkpoint | Line and level
5fe3b340-7fda-5832-96d1-b61bd7280c20 | note | Comments -
f06b8532-63b4-5735-8061-8b03398cc5f0 | textbox | Design:
e0b070e2-0f92-558e-a6d2-7510a13edaec | textbox | Achieved:
89e23c3e-aa4b-4d5b-b6c5-76b82ab003bc | checkpoint | Cleanliness and condition
79980bda-084a-5b83-99b1-6440a99602aa | note | Comments - Internal pipe and joints clean and free of dirt/debris
b7c9b724-65cc-5179-bb1a-e22f9c1312c5 | note | ○ Pipe condition inspected prior to backfilling
a91200ca-46c1-4c73-a4b7-0717a9b850a9 | checkpoint | Bedding and Haunching
370a2d05-8021-5929-a27c-b05ff0fd7fdb | note | Comments - AP<12 granular bedding material
9ee42627-75d2-5549-a1b6-262140f60db6 | note | ○ Clegg hammer tests (every 10m, min CIV 12)
316fcf5e-34e6-5ced-8047-7d2358042d97 | note | ○ Clegg Results:
84c6155d-2fc0-4699-8b47-4d0804851837 | checkpoint | Temporary capping of end of pipes
c4ebc408-9d1d-4018-afc7-14aa947b6edb | checkpoint | Backfill Placement
008a00f8-0ff1-5c52-a338-b35d96e96f3e | note | Comments - AP>40 granular bedding material
6288a32c-3e7d-523a-b0ba-d38a38a19780 | note | ○ Clegg hammer tests (every 10m, min CIV 25)
91d3d9aa-9de7-55fc-b183-e5c2df6731f9 | note | ○ Compacted in 200mm layers
a72828a9-2355-5256-8dde-0a4d7e9da188 | textbox | Clegg Results:
71395699-e98e-4c69-aa04-981879084797 | section | Manhole Installation
e92be3b1-1d0f-4238-8b40-153b93563954 | checkpoint | Alignment
32ae0601-296b-510e-9fb8-2e91758f7cb8 | note | Comments - Correct position (<50mm)
495de50c-8582-5a2b-a913-7c00c3b82bf5 | note | ○ Vertical
b43608b4-ee23-47ff-b835-b6204482687e | checkpoint | Bedding
4c8de7d6-de0e-5e9e-9b92-108286954e9b | note | Comments - Bedding material – min 150mm
3b0086bb-6939-5ef4-939b-ba1eda95e5e9 | note | ○ Clegg hammer tests (min CIV 12)
80bfd47f-05ed-5264-82b7-477b14419e81 | textbox | Clegg Results:
c8a5e9a8-cc24-4372-b29b-9167c21c5496 | checkpoint | Backfill Placement
df912de1-e683-5890-86d2-53a5cb241474 | note | Comments - AP>40 granular bedding material
7f8874d1-dd27-570f-8e4a-6f88e16b89a4 | note | ○ Clegg hammer tests (min CIV 25)
895ce9b5-c603-51da-94c3-38a48789aea1 | note | ○ Compacted in 200mm layers
726aabc2-a1e4-5d4a-94bc-059d0499bdec | textbox | Clegg Results:
5b273b34-232e-46fa-a213-21ea23e7f3e0 | checkpoint | Penetrations
a974ae65-477e-531f-8343-5c3388ae2d75 | note | Comments - Formed by cutting or drilling prior to knocking section out
81a53eb7-2d6d-46fa-9816-835dfee8e2ee | checkpoint | Pipe Ends
26aa13a1-4872-5b92-a366-2efac5679c24 | note | Comments - Finished approx. 50mm beyond inside wall
f83d50ae-c99d-5c09-9a8d-238b788841a1 | note | ○ Plastered with cement mortar or encased in benching concrete
47d8195e-e8da-4630-8ec7-58d0147515b6 | checkpoint | Corbels
7354aa82-1834-5050-88d2-369a4606c285 | note | Comments - Pipes haunched and surrounded by concrete by >200mm from manhole
b8a83028-f4c4-4cdf-9942-7ba34e706d68 | checkpoint | Benching
210fcd71-94fd-51a3-834f-5816bd719a9a | note | Comments - Smooth finish, graded to channel, in accordance with drawings
b272941b-fe4c-4a30-b891-b42dc5e6353e | checkpoint | Works completed as per design requirements and work area is ready to be handed over for sign-off
12d4a07d-7860-45c0-8701-8b6e8747b438 | signoff | Signed by Sub contractor Representative
645d8739-1e43-4519-9a72-77d5102eed3f | checkpoint | Final Approvals
f0fae84f-1101-57e3-9a4d-2af8502b247d | textbox | DNZ Check - Name:
a7496307-ebff-5601-932a-0c785cf07fa3 | date | DNZ Check - Date:
eaba1159-b424-5fdb-9f05-e1dbb65424bb | textbox | Engineer / Consultant - Name:
60f0f80b-2b22-5876-b492-fe8a7412ff73 | date | Engineer / Consultant - Date:
8e383c3e-00df-4eb5-a377-bb108e0aa8dd | signoff | Sign-Off
5f433e59-776e-4e8a-bf0e-cb809e243ac2 | checklist | Documents & Photos |  | Documents & Photos
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dd77a1e6-4546-407a-bdc7-2fb24ca37b74 | checkpoint | Please upload the relevant document(s) / photos and press PASS.