## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - MT GRAND to WINGATUI | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561483 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | CM | Construction Manager | Stephen Vorgers
Contract Number: | DCC11014-WPS004 | [5 empty] | C | Check | CR | Cust. Representative | Joff Riley / Mark Todd
Area/ Sub-System: | Switchboard Upgrade & Electrical |  |  | Lot ID Number: | N/A |  | D | Dimension Inspection | IP | Inspection Personnel | Hamish Watson
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | 561483-ITP-010 |  |  | Version: | DRAFT |  | H | Hold Point | OP | Operations Manager
ITP Description: | Electrical Installation, Generator Changeover & Switchboard installation. | [5 empty] | I | Inspection | PM | Project Manager | Matt Paterson
Discipline: | Electrical Works | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | "Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-SS-DRG-GN Drawings: G0001, M0001 through M0004 & P0001" | [5 empty] | S | Subcontractor | SP | Supervisor | Hamish Watson
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Hamish Watson / Matt Paterson |  |  | Date: | 19-12-24 |  | W | Witness Point | SV | Surveyor
Quality Specified: | None - As per Specification requirements & NZ Electrical Regulations | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Hamish Watson |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson/Stephen Vorgers |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Mark Todd / Iain Partington |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Inspection of Generator Changeover Switch Cabinet | Check overall condition. check connections for internal electrical components | Visual check and report any defects or areas of concern | Email or NTE to report | once | Visual + Photograph | C | IP/B
3.2 | Inspection of Generator Connection Enclosure. | Check overall condition. check connections for internal electrical components | Visual check and report any defects or areas of concern | Email or NTE to report | Once | Visual + inspection | C | IP/B
3.3 | Delivery of Generator Changeover Switch Cabinet to Site | Check and verify that the Generator Changeover Switch Cabinet has been delivered damage free | Cabinet is damage free | Switchboard Builder Delivery Docket | Once | Visual + inspection | C | IP
3.4 | Delivery of Generator Connection Cabinet to site | Check and verify that the Generator Connection Cabinet has been delivered damage free | Cabinet is damage free | Switchboard Builder Delivery Docket | Once | Visual + inspection | C | IP
3.5 | Inspection of Switchboard | Check overall condition. check connections for internal electrical components | Visual check and report any defects or areas of concern | Email or NTE to report | once | Visual + Photograph | C | IP/B
3.6 | Delivery of Switchboard to site | Check and verify that the Switchboard has been delivered damage free | Switchboard is damage free | Switchboard Builder Delivery Docket | Once | Visual + inspection | C | IP

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Mount Support Brackets To Hand rails for Cabinet | Support Brackets mounted to Handrail | Mounts are secure and firm, with no excessive deflection | This ITP | once | Visual | I | IP
4.2 | Mount Generator Change over Cabinet to Mounts. | Cabinet Mounted | Cabinet is mounted securely, all bolts tight, seals intact and in good condition | This ITP | once | Visual + Photograph | I | IP
4.3 | Mount Generator Connection Cabinet on outside of Building | Cabinet Mounted | Cabinet Mounted Securely to wall | This ITP | Once | Visual + Photograph | I | IP
4.4 | Install Cable Supports for generator Change over | Cable ladder installed securely, with adequately spaced supports. | Cable ladder mounted correctly. | This ITP | once | Visual + Inspection | I | IP
4.5 | Mount Generator Connection Cabinet on outside of Building | Cabinet Mounted | Cabinet Mounted Securely to wall | This ITP | Once | Visual + Photograph | I | IP
4.6 | Install Cable Supports for generator Change over Cabling | Cable ladder installed securely, with adequately spaced supports. | Cable ladder mounted correctly. | This ITP | once | Visual + Inspection | I | IP
4.7 | Install Cabling Between Generator Connection Cabinet and Generator Change over Cabinet | Cabling installed, secured to support systems, no excessively tight bends on cables. | Cables adequately Secured, Cable Ties cut off clean with no sharp edges. | This ITP | Once | Visual + Photograph | I | IP
4.8 | Terminate cables into Generator Connection Cabinet | Cables fit off into cabinet. | Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated | Cable/Cabinet ITR's | once | Visual + Inspection | I | IP
4.9 | Isolate Supply to Pump Station at WTP Switchboard. | Supply isolated | power to Pump Station isolated, no voltage/ current present on cables | This ITP | once | visual | W | SP
4.10 | Disconnect Mains Supply from Pump Station Switchboard and relocated to Changeover Cabinet | Cables disconnected and routed to changeover enclosure | Cables clearly identified for origin/phase. | This ITP | once | Visual | W | SP
4.11 | Terminate cables into Generator Changeover Cabinet | Cables fit off into cabinet. | Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated to correct terminals on Changeover Switch. | Cable/Cabinet ITR's | once | Visual + Inspection | I | IP
4.12 | Install New Cables Between Changeover Switch And Switchboard | Cables installed and secured to existing cable trays | Cables are correctly sized, secured adequately to cable trays. | Cable/Cabinet ITR's | once | Visual + Inspection | I | IP
4.13 | Terminate Cables into Switchboard | Cables fit off into Switchboard and Generator Changeover. | Cables enter into Enclosures through appropriately sized glands, cables fit off correctly and terminated | Cable/Cabinet ITR's | once | Visual + Inspection | I | IP
4.14 | Mount Switchboard | Cabinet Mounted | Cabinet is mounted securely, all bolts tight, seals intact and in good condition | This ITP | once | Visual + Photograph | I | IP
4.15 | Terminate cables into Switchboard | Cables fit off into cabinet. | Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated | Cable/Cabinet ITR's | once | Visual + Inspection | I | IP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Switchboard | New Cables installed, insulation, continuity and polarity tests completed, phase rotation confirmed | Electrical Testing completed, board Livened and operating as prior to modification. | Cable ITR's/ COC | once | Visual + Document | I | IP
5.2 | Generator Changeover | Cabling installed and terminated. changeover tested and inability for back feeding of supply confirmed. | Changeover operation Verified as satisfactory. unable to live test due to lack of a suitably sized Generator | Cable/Cabinet ITR's, COC, ROI From Inspector | once | Visual + Document | I | IP
5.3 | Generator Connection Cabinet | Generator Connection Cabinet mounted, cabling fit off, testing completed. | Cabinet Mounted Securely, polarity of connections correct, | Cable/Cabinet ITR's, COC | once | Visual + Document | I | IP
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: