## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
8d671891-fbb2-4912-9fa3-402fe0d9ad85 | checklist | 561483-ITP-001.1 - DRAFT - Installation of Stoney Knowe Air Valve1 - HOLD POINT | itp | 561483-ITP-001.1 - Air Valves - Delivery & Installation
186b3f17-ca8d-43ba-9e0f-e57570959888 | section | SECTION 3 – RECEIVING INSPECTIONS
abea91eb-c8a5-468c-add5-2ca35a76e53b | checkpoint | 3.1 - Take delivery of air valve 1
61f18b84-3e92-55c2-9753-12ca514c8f5e | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
c7761eb3-8bd3-50ee-8129-6a6af1338ec4 | note | Acceptance Criteria - Matches Design Drawings/Documents
1481590a-6a4d-50a2-b73e-b018d9b50a14 | note | Verifying Document - Drawings & Specifications
0ac74455-252c-5edc-93b5-f1209e828341 | note | Frequency - Once
2a1651bd-a758-512a-8c92-1440b5d5dc94 | note | Inspection Type (Visual, other) - Visual + electronic
d3e027eb-4a45-5196-a793-a110d00aa2bd | note | Inspection: Key - H
0e511fd1-d214-50ff-9473-6d84eb137ba7 | note | Inspection: By - IP/PM
f821d528-4094-41e2-90db-f40c32251022 | signoff | HOLD POINT
857bfa98-8ea5-468c-8163-6f1d6ff26ee4 | checkpoint | 3.2 - Inspection of Air valves for any sign of transit damage
720be9de-52e3-5976-a268-015e808b209c | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
e954f7d6-0eec-5336-a86d-bd2a55ce6f23 | note | Acceptance Criteria - No chips to protective coating or any mechanical damage
d2f26c37-5ee6-5e7d-80b9-ba0b22dc12d3 | note | Verifying Document - This ITP
a7a41c24-414f-5a3c-97b0-f8e2dd466999 | note | Frequency - Once
296dd81c-85df-5945-afcb-770f9af7c379 | note | Inspection Type (Visual, other) - Visual + Inspection
2a7d503c-8f33-5192-8082-eeb97bdda8f7 | note | Inspection: Key - I
b2359ffa-eff8-5672-9230-84d2b1d31bc2 | note | Inspection: By - IP
b98d27ab-7d51-4047-ba04-c9e262c95a26 | checkpoint | 3.3 - Fitment - Spatial constraints
23e7326c-374c-5489-84e7-5799488e8fee | note | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
ee6f91fa-b831-5002-bb20-880ddf342f27 | note | Acceptance Criteria - Measure & Check
b7e8eeeb-573b-5e77-8dff-6a8cf4e4efbe | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
a685ae80-0b7d-53ec-8b77-1bfb071c726a | note | Frequency - Once
87709857-d61a-5a16-915a-f4ce5f7ed434 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
be2ac74f-a01c-5637-af3e-301f3ecf5322 | note | Inspection: Key - I
259b4541-df98-5dec-a7d9-14ca09e0a6e0 | note | Inspection: By - CR
33e4b609-1f73-4424-adfc-d62a83d68043 | checkpoint-no-value | Note:
a71a4dee-7c84-538d-b716-1c052bde49cc | note | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
19f67f27-2030-57b2-965d-72d0c4d9b9d9 | note | Downer to notify Engineer once confirmed.
82270cd4-e89c-4c48-9bf5-878b7072c986 | section | SECTION 4 – IN-PROCESS INSPECTIONS
996792ed-6f35-450c-8615-3c28d7033f4b | checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valve 1
42a9c192-4bb1-5ec9-9521-5839d3fdecab | note | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
42aba608-6615-5ac3-84ef-7dcf7e2c3533 | note | Acceptance Criteria - Thread is in good condition
e9a698fa-e9f2-502c-9168-3535b2493daf | note | Verifying Document - Visual Assessment
e0954858-9295-5fb9-8946-d7715759f965 | note | Frequency - once
ba79d56f-1f8b-56ad-98a2-9f7168fea971 | note | Inspection Type (Visual, other) - Visual + Photographs + docket
2db86a84-acdd-5181-b3e8-50c18bc02f4b | note | Inspection: Key - I
c6fbb0af-92e9-5459-9344-c1f38bf09527 | note | Inspection: By - IP
f79c6ebc-9788-435d-8b06-470795d2b755 | checkpoint | 4.2 - Isolating Valve Installation - Valve 1
cb0c2cc2-6572-5be0-bb46-b5236c34da1f | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 1
f7d48748-a451-5b47-88c9-5c5dd50d54da | note | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
c6048362-acf6-5aa2-835e-29932798badc | note | Verifying Document - As per drawings/Specifications & Best Practice
ac3fafe3-928d-58f0-9ce9-fc01468045dc | note | Frequency - once
b487831f-8c2e-5c91-853d-380c05585b91 | note | Inspection Type (Visual, other) - Visual + Photographs
ae79cac0-7b41-50af-aa97-caab559568ea | note | Inspection: Key - I
7387eccf-5cfb-5e38-bd89-0c417feb27e1 | note | Inspection: By - IP
39be4fc0-c5ff-4d9a-90df-fe1eca355589 | checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 1
9482acb1-2480-5b55-976a-87a2f36cef20 | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 1
210d43bd-3303-586f-9343-95f8ac7558b2 | note | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
22a60e82-66b2-5a3a-b83d-d5fdf2ea505d | note | Verifying Document - Visual Assessment
4cf321fd-f7c5-5b50-8fd7-faac74ddd882 | note | Frequency - once
cb5b88d1-46fd-579c-9098-9fd44e0ce51c | note | Inspection Type (Visual, other) - Visual + Photographs
f49fd000-3c74-5efb-b3f9-dc95576bea01 | note | Inspection: Key - I
6b08a01e-bd39-5fba-8a97-8f9f42ba300e | note | Inspection: By - IP
2bb98c0b-daf0-4336-be4a-cfc94c79e8e3 | checkpoint | 4.4 - Isolating valve 1 - Off position
13c93f70-6f1e-54ee-b6eb-d9d543416551 | note | Inspection Point: Quality Control Activity - Pressure test
f5d994a9-468d-5465-ab12-9d35885d7a4b | note | Acceptance Criteria - Ensure all isolating valves are in the off position
9ebaab62-6d02-5978-b4d0-a0abef6bca47 | note | Verifying Document - This ITP
1a37f20e-2573-5f32-a1ae-ba091e4e3b88 | note | Frequency - once
c7813148-db31-5a7b-aa95-ae785b9d8aab | note | Inspection Type (Visual, other) - Visual + Photographs
502e50fa-d4a7-5025-a3b4-dcc76b7069b9 | note | Inspection: Key - I
b91b428c-c7cb-549b-bed6-d41a55afa481 | note | Inspection: By - IP/CR
85d7dc89-70fd-46a9-90f1-dbf805f913d4 | checkpoint | 4.5 - Security
5d999c22-d942-5f99-97d4-40e5c49c748c | note | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & security
89c1c3bc-f97e-5d02-aac8-8b5c0e32c06e | note | Acceptance Criteria - Valve covers are replaced and securely in position
db78d992-be3a-5e14-bc99-62179bd23354 | note | Verifying Document - This ITP
c2eaaddf-3856-5a85-865b-743ad8eeea73 | note | Frequency - once
e44a8dc9-123f-5f0d-87ff-7dc03c1163ab | note | Inspection Type (Visual, other) - Visual + Photograph
12148225-2267-56f4-bf19-d44e692a0e6b | note | Inspection: Key - I
d4dcbd10-eb02-5829-8d14-3582dbe224b9 | note | Inspection: By - IP
07728fe9-a1ca-4416-8967-c82fbdc373be | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
39995029-25f7-4f80-8151-c19c20268f77 | checkpoint | 5.1 - Red pen Mark up
a2c833b0-7c81-5987-bd42-c1fec4fbe421 | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
caf1bfce-4a7c-5f37-9a25-1beb2fd885f3 | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 1 make & Model at each location
d50464a8-db9f-5cdf-bd74-a489141d3929 | note | Verifying Document - Red line mark up drawing / This ITP
be7dca77-7a27-5329-9887-f33d8413943f | note | Frequency - once
79926592-83a5-5044-8c53-33b5ca2290ce | note | Inspection Type (Visual, other) - Visual + Document + Photograph
37057a6e-a3d4-589f-8c60-dcb41d3c0033 | note | Inspection: Key - I
59be586b-b78e-5f59-a268-fad6ee3a2fc6 | note | Inspection: By - IP
b0a29233-1b69-4f5e-b0af-4aaa77403663 | checklist | 561483-ITP-001.2 - DRAFT - Installation of Stoney Knowe Air Valve2 - HOLD POINT | itp | 561483-ITP-001.2 - Air Valves - Delivery & Installation
007ebc97-eca4-42d2-9cb2-cc97cdf49bb5 | section | SECTION 3 – RECEIVING INSPECTIONS
dde3aba5-8b22-417e-b1d3-f01abfd0adcc | checkpoint | 3.1 - Take delivery of air valve 2
be160cc4-094d-5fca-ac34-e8b3078b80ac | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
7aaaf4ab-822b-5fcd-a9e7-b2f19333dc3c | note | Acceptance Criteria - Matches Design Drawings/Documents
f112bc0f-9b5b-5b64-8f37-8b2dcacf1ef7 | note | Verifying Document - Drawings & Specifications
45fbe9bc-e831-5cb5-b5df-893f3d5fea6f | note | Frequency - Once
d6b0a023-27c2-5968-b8d9-62d424548162 | note | Inspection Type (Visual, other) - Visual + electronic
0526d0d0-68b4-5da6-a5ba-689c692797e5 | note | Inspection: Key - H
7335356f-47c8-5f50-9f78-32fc84f1fbf7 | note | Inspection: By - IP/PM
1c38c292-bca3-4976-a50d-f2cb3128437f | signoff | HOLD POINT
453151bd-f2fa-40b9-abb5-196a91cdc598 | checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
d43f417c-f317-5094-b953-3cee89f05085 | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
32e517fc-2010-56b5-afc8-0f63f08dfd32 | note | Acceptance Criteria - No chips to protective coating od any mechanical damage
7fbf691d-504a-59b7-8630-ab678ba6ba68 | note | Verifying Document - This ITP
022ddbde-3bbe-5c51-92a9-1c45bcec286e | note | Frequency - Once
b3dc5e28-7b9c-5ff1-901e-95017d7754db | note | Inspection Type (Visual, other) - Visual + Inspection
5182ca8a-f500-5744-97ef-f64a6428efb6 | note | Inspection: Key - I
0eb8995f-58cc-5cbd-9e1e-5f1d27fc30c4 | note | Inspection: By - IP
1dd6c262-996d-47e9-8019-a34d198fb770 | checkpoint | 3.3 - Fitment - Spatial constraints
ee778e1a-367c-52b4-878d-8d27eba5174e | note | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
af90f6cd-b319-500c-afa1-576fac798593 | note | Acceptance Criteria - Measure & Check
afd979e9-c4d5-5888-910c-11db4008b7b3 | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
ede7a670-de7d-5d20-87cd-3f0e3f445b95 | note | Frequency - Once
cd342d90-b291-590d-b337-c45d0406ab45 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
bebdbe77-2427-5a61-b572-c0f0327fb82a | note | Inspection: Key - I
db846020-71d6-5d68-bd6a-bfbf62a4a5f8 | note | Inspection: By - CR
96a60894-077d-4d96-85ce-ee7521ad41c6 | checkpoint-no-value | Note:
3af94b58-e609-5f32-9a50-53f8b0d5bae3 | note | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
563d29b3-faec-5c35-80a6-bb126d81c59f | note | Downer to notify Engineer once confirmed.
9b143505-b5da-4a6e-acb4-50f3bfc98b21 | section | SECTION 4 – IN-PROCESS INSPECTIONS
c907aed7-ff64-42f6-b44d-cb9a7699b98f | checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 2
240a58eb-d142-51ba-b7c1-b30b501f96c0 | note | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
f8867d46-3810-509c-9ce6-fe63efdc27a9 | note | Acceptance Criteria - Thread is in good condition
508e268d-ea29-5923-b9af-0ceada60b51c | note | Verifying Document - Visual Assessment
a231be76-a268-5d73-98d9-6906c7c1617a | note | Frequency - once
19669bc2-4bed-53a2-b1da-2f62ef04489f | note | Inspection Type (Visual, other) - Visual + Photographs + docket
cf067f5a-062f-5791-b5ae-d6f4674bee1f | note | Inspection: Key - I
41a26c74-ecee-5d9f-bdce-71ba20637dc8 | note | Inspection: By - IP
b940aecf-4ad8-4310-b24d-07b940076685 | checkpoint | 4.2 - Isolating Valve Installation - Valve 2
9f68411c-32c1-5b92-aee8-ef4721b6d8d9 | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 2
75184a9f-1a5a-5cd3-9cf4-d4e65716b1fe | note | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
9421fde5-0f84-5071-b93b-6876b54c1320 | note | Verifying Document - As per drawings/Specifications & Best Practice
25f881a3-f6b8-5bf1-93a0-497da9e9ccb4 | note | Frequency - once
cba43e89-32aa-5daa-b381-745fae2c820b | note | Inspection Type (Visual, other) - Visual + Photographs
5aba9090-5706-512b-9690-bbbd8e2ab3c7 | note | Inspection: Key - I
03a685de-f824-5afb-a1c8-0c4c0bcf4eac | note | Inspection: By - IP
5de8cbf7-5fea-48d7-83fb-581f9d525ba5 | checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 2
73d22a26-9359-57fc-a587-08612cc9b14a | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 2
93b17736-72c6-5bf8-9466-20fff0678b0e | note | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
8e5a0aed-56e5-5385-ac8d-58236884f265 | note | Verifying Document - Visual Assessment
6079b518-d15a-5ea0-b056-7ef12db622ea | note | Frequency - once
00010928-aa2b-5135-a672-50d0e12201d8 | note | Inspection Type (Visual, other) - Visual + Photographs
d5d8891c-6652-5524-9b3e-65cd0d04c3b5 | note | Inspection: Key - I
e26231a8-533a-5d4b-a3d8-6b0f2cc41c08 | note | Inspection: By - IP
f000caa2-feb2-4c48-98d0-0ea50d79e34e | checkpoint | 4.4 - Isolating valve 2 - Off position
208e055e-eefa-5eaf-a01c-72de5239a6ce | note | Inspection Point: Quality Control Activity - Pressure test
21e748c1-0fef-5557-b910-579b4ae9011c | note | Acceptance Criteria - Ensure all isolating valves are in the off position
75b04315-8ee2-5626-bdd9-aa8d6544c399 | note | Verifying Document - This ITP
5ddbb110-a5c0-5672-aaf1-f67d27524f54 | note | Frequency - once
c0217f63-1575-560e-bcd2-801f809a2ea2 | note | Inspection Type (Visual, other) - Visual + Photographs
da012c1d-0fb6-55d2-8000-5b8bc8982f89 | note | Inspection: Key - I
c99c5286-6383-5934-8ff2-852cd628f212 | note | Inspection: By - IP/CR
218d48df-9332-419e-aa9f-619674352a95 | checkpoint | 4.5 - Security
e74fe418-e0e4-5d8f-8d5f-f8dcd7a6daf2 | note | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
a4366264-c2b5-5451-b285-2f3e920f9307 | note | Acceptance Criteria - Valve covers are replaced and securely in position
53cc8d06-9ed7-58cd-9f59-b45f36edb20e | note | Verifying Document - This ITP
9d011d42-c4a0-57d7-9360-637225c0a10c | note | Frequency - once
351be1a2-19a1-5db5-9227-1524a98695ae | note | Inspection Type (Visual, other) - Visual + Photograph
38cca819-6f36-5c39-b53c-8c9f71885848 | note | Inspection: Key - I
9a9596ea-ab87-5153-8575-a7af39d903e2 | note | Inspection: By - IP
f8b0e3d5-7df1-4695-9c41-0e8d678d915e | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
e282142b-1b99-4030-9eb6-4e0665e360e2 | checkpoint | 5.1 - Red pen Mark up
e4f61915-deb3-568a-97ce-2cf5fd2d0832 | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
dbb247ad-4b0d-57d4-a265-cb38a4e9ebed | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 2 make & Model at each location
4819b9c6-6d30-5576-9f50-805ba3f0648b | note | Verifying Document - Red line mark up drawing / This ITP
f2c4ebbe-6aef-5048-886c-43ce3b358d5e | note | Frequency - once
2776b4d1-5fff-54b0-bc41-b0d130174134 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
48709341-95f1-589a-a147-d055f5213702 | note | Inspection: Key - I
0a865861-8da2-53fd-9855-0bb0442a7743 | note | Inspection: By - IP
3acf5f99-94f4-4e36-bb95-b4b518a09d38 | checklist | 561483-ITP-001.3 - DRAFT - Installation of Stoney Knowe Air Valve3 - HOLD POINT | itp | 561483-ITP-001.3 - Air Valves - Delivery & Installation
4e9465cc-f4ea-4245-91e8-9eda06aa72de | section | SECTION 3 – RECEIVING INSPECTIONS
c35ceed9-d603-42c4-bca7-3cdf89d160ab | checkpoint | 3.1 - Take delivery of air valve 3
3c6e4dfe-c6dc-53e7-8d7f-dfa0137d8e5f | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
3dd92725-d787-5e8f-95c1-68987c941b33 | note | Acceptance Criteria - Matches Design Drawings/Documents
a5ef46bd-2e0e-580b-ad8c-f9c329650a19 | note | Verifying Document - Drawings & Specifications
b5ed7bfe-8669-5396-9122-6a6b11285c0d | note | Frequency - Once
5df85d40-37a3-5a70-b249-3fc31f3001d0 | note | Inspection Type (Visual, other) - Visual + electronic
ac9eaa6a-895a-56be-aa1f-28c907b64090 | note | Inspection: Key - H
3d9bcb2e-1a46-561b-98e3-437e559a2e35 | note | Inspection: By - IP/PM
5185ced0-5e6a-4ba9-a7be-b105df8d86df | signoff | HOLD POINT
232be903-5516-4a58-9ae5-8530fd5cc310 | checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
a0a901fc-ad0a-576c-a286-e69558bc0443 | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
dcd9a734-164d-5467-92ee-97c38adf8325 | note | Acceptance Criteria - No chips to protective coating od any mechanical damage
768e1ad7-3e49-507c-b6c5-258878fb6ff2 | note | Verifying Document - This ITP
4af388c0-eecf-55de-b42c-9bcde9c9767b | note | Frequency - Once
b85e4bfd-c956-5709-a00e-a0efa06d66ad | note | Inspection Type (Visual, other) - Visual + Inspection
9db8e58b-9ec8-5b9e-9791-479e4e595a97 | note | Inspection: Key - I
3542a24e-4d04-50ac-858f-c26f7f2a8767 | note | Inspection: By - IP
bafcfbc6-a000-489e-8e9a-793f178d6c2b | checkpoint | 3.3 - Fitment - Spatial constraints
c2c79664-fcb6-575c-b240-ad7df1b5ae30 | note | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
b30cefc9-4717-5d3a-9360-68317d2f1468 | note | Acceptance Criteria - Measure & Check
43aa83fc-d7ca-5653-a615-280e96e0ccfe | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
49f2d594-af18-51e2-ac9c-136404e7de3f | note | Frequency - Once
bd9b3aa0-eb0f-53f1-b8a0-c13c36e69b7e | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
cc0dd8a3-e30b-5d70-9841-d98b4bd504d1 | note | Inspection: Key - I
6ce53aa9-b1ea-5167-88ac-c643d389cacb | note | Inspection: By - CR
29ed59fa-410e-4def-b01b-74bedd57a35a | checkpoint-no-value | Note:
81a729c6-f5b4-5094-80a7-c38c41153c71 | note | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
df474735-74e5-50b6-8d6e-4dae70f5256c | note | Downer to notify Engineer once confirmed.
de2b1eb3-5ba2-4fd9-a30f-ceb1ee32016c | section | SECTION 4 – IN-PROCESS INSPECTIONS
0ae877dc-dfb7-487d-8e8c-c3c7489c284b | checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 3
7200cab2-6a42-5695-9d27-bf2da3585fd4 | note | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
9b7f3131-e091-50b7-a3a5-4b82487254f5 | note | Acceptance Criteria - Thread is in good condition
e71c255f-4405-566d-ad78-42eb46678440 | note | Verifying Document - Visual Assessment
d21acd47-8087-5630-9f2a-179819e40762 | note | Frequency - once
433616b9-37a0-5fc9-babf-a88b3701b8ee | note | Inspection Type (Visual, other) - Visual + Photographs + docket
5a4a5a9c-d9ee-50ff-80c9-c52bf7768719 | note | Inspection: Key - I
2b9d7c02-c307-56c8-b51d-d6b04fd83d38 | note | Inspection: By - IP
b5d3a9c7-0a9c-4166-b534-de6e869be29d | checkpoint | 4.2 - Isolating Valve Installation - Valve 3
68b2052b-9102-5d53-9956-3f0f7105ef60 | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 3
1f2c60c7-5d63-5627-9078-bbbc1b0d43cb | note | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
997daaf3-0c82-5ce0-a950-aece12fe823c | note | Verifying Document - As per drawings/Specifications & Best Practice
896d0b19-40e5-5c84-b3c8-15f43098ec07 | note | Frequency - once
fe22230e-e677-5a4f-88cd-0dddd6d1b82d | note | Inspection Type (Visual, other) - Visual + Photographs
003c3ebd-12c1-5a21-aa07-4ee830ded534 | note | Inspection: Key - I
52e06516-14da-55d9-9de3-8cc28cad8e19 | note | Inspection: By - IP
038092e1-dbbc-45fc-a009-bc213a744258 | checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 3
a436acc6-4115-5ace-9fbe-a3b2f50612fc | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 3
7901f8af-0f20-5ab7-bfd4-8770619a88db | note | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
919be829-c650-50b9-afe1-c14d68f984a2 | note | Verifying Document - Visual Assessment
2a47dfb4-2602-58cc-b358-87eb7c56e45c | note | Frequency - once
ea464883-1e59-545a-b2db-58020c2cd5f1 | note | Inspection Type (Visual, other) - Visual + Photographs
cade8814-7fc4-51d2-9591-e729c41e98d0 | note | Inspection: Key - I
95d9ca6d-04e4-5c4a-84b6-5765ba9ce17e | note | Inspection: By - IP
1f2317b9-bf33-40bc-ae3d-a1c004353923 | checkpoint | 4.4 - Isolating valve 3 - Off position
f163978e-8780-5169-8ea0-061c55107630 | note | Inspection Point: Quality Control Activity - Pressure test
d3b42480-565c-5e70-8c68-5be1f0362909 | note | Acceptance Criteria - Ensure all isolating valves are in the off position
71476cf3-c04f-5230-8a6f-dc2bc5550ec2 | note | Verifying Document - This ITP
16246bc8-0632-5d4a-b68f-6dcbd97d187a | note | Frequency - once
025beed3-dde4-53ef-a0e1-eaa61b5cd344 | note | Inspection Type (Visual, other) - Visual + Photographs
97f7b1ef-2677-58fe-a288-2d3d221cc7e0 | note | Inspection: Key - I
f12c875c-1c73-5e4c-bac4-9219373db8a6 | note | Inspection: By - IP/CR
80b3aa34-edce-4fa4-a10b-e67463038ff1 | checkpoint | 4.5 - Security
ac177204-a2e5-5566-8bd4-1e9439c7901e | note | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
51b3e03e-2ce5-5979-99d4-6a10324fa9ca | note | Acceptance Criteria - Valve covers are replaced and securely in position
b01ae284-d849-5d8d-b406-e0726744e836 | note | Verifying Document - This ITP
5e74f878-1463-5e50-b027-5a3a9e057601 | note | Frequency - once
b0a39538-936b-5fa4-9ad5-a6bed34297e3 | note | Inspection Type (Visual, other) - Visual + Photograph
f69711ea-a704-5c58-9545-f5d70268ddf0 | note | Inspection: Key - I
f5ec08ac-e679-5879-a3d4-ae6e05101062 | note | Inspection: By - IP
1dd40a82-c7f5-4518-b9a7-c184dfdd54d2 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
0656a83d-f950-4c69-aadc-bd8015dabb8d | checkpoint | 5.1 - Red pen Mark up
5f6b7369-2cf9-56b2-ba76-873d49821ecb | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
40a5b147-a927-5c36-99be-de56ecf7f7e7 | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 3 make & Model at each location
704372dd-2143-50f0-9b81-8462ea6cbb7f | note | Verifying Document - Red line mark up drawing / This ITP
365a33d8-383d-54f4-92ed-040f637000c4 | note | Frequency - once
43a135ed-1ed5-5605-b93a-fc6d8ed1a06a | note | Inspection Type (Visual, other) - Visual + Document + Photograph
dc894a41-d71f-5792-ba52-07bb60e32cac | note | Inspection: Key - I
e8b641e8-d9c8-5123-a645-a518aeba4af8 | note | Inspection: By - IP
bc846926-0690-4032-85c0-36568521eedf | checklist | 561483-ITP-001.4 - DRAFT - Installation of Stoney Knowe Air Valve4 - HOLD POINT | itp | 561483-ITP-001.4 - Air Valves - Delivery & Installation
c8416ae3-dd5c-4c31-9f0f-0b4781c09309 | section | SECTION 3 – RECEIVING INSPECTIONS
65d0eb6c-fbc3-4b80-88af-ff4c39535946 | checkpoint | 3.1 - Take delivery of air valve 4
f2a44281-df01-5ef7-bb17-af0e2b17c87d | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
8da5410e-8f65-5e68-883e-0cf26fb72570 | note | Acceptance Criteria - Matches Design Drawings/Documents
171df1e1-592f-5529-9e79-ae81c51a686a | note | Verifying Document - Drawings & Specifications
a33b9063-eb9e-504e-a951-a5f4cd4e134e | note | Frequency - Once
d8fbdfd2-7d8b-510f-85c5-861f51cf2eb0 | note | Inspection Type (Visual, other) - Visual + electronic
43f18b61-f2ac-51a0-aae6-0a009bb2ed54 | note | Inspection: Key - H
d2f624bb-e596-51a7-98ac-68c46ad39f25 | note | Inspection: By - IP/PM
85800ad6-e779-429d-a9ef-9449b75d2f31 | signoff | HOLD POINT
895c2cc3-b184-4c20-a057-fcb6f66bfae3 | checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
c6175afc-a8e2-5c1c-bd1b-d8b1570bfb4c | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
734748b5-afb8-57cb-a5df-ee8840859850 | note | Acceptance Criteria - No chips to protective coating or any mechanical damage
d56aa36d-01db-5f14-8fa3-cdf59184083b | note | Verifying Document - This ITP
60766cb8-a4ec-5b76-85af-ed54c2fa5f69 | note | Frequency - Once
3490a01b-ab73-538a-a2d1-4485c80cfa39 | note | Inspection Type (Visual, other) - Visual + Inspection
da925fbb-0a03-5f01-8614-33d5c70fdd7e | note | Inspection: Key - I
cde5ca79-a8aa-5e46-ba72-08784d3f19d4 | note | Inspection: By - IP
c7a0ef90-1606-4f29-bf69-dc9842456b67 | checkpoint | 3.3 - Fitment - Spatial constraints
41c6646f-1891-5c77-a010-7bf454c38f47 | note | Inspection Point: Quality Control Activity - Verify air valve will physically fit into existing locations
992ad0ed-f2a1-5f49-942d-a197d7201258 | note | Acceptance Criteria - Measure & Check
52675b28-741d-5681-8395-b7ff3958fd06 | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
54440c9a-f732-542f-8008-6e94fe3a8c53 | note | Frequency - Once
942883c3-5ce0-5eb6-96c9-70220c719016 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
ca0354a0-1005-5593-9465-43b73e801e87 | note | Inspection: Key - I
71559dd4-e21b-58ee-a584-872b970200f4 | note | Inspection: By - CR
fdd9d6cc-9222-44f9-a873-48b9130a9477 | checkpoint-no-value | Note:
5e97b019-2701-5ae9-bfc7-9b64e43232c3 | note | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
dbfb51a9-d69e-5773-a3aa-cd712f45a25f | note | Downer to notify Engineer once confirmed.
19a1be45-a639-4ffb-8d01-4bee1bd5c57d | section | SECTION 4 – IN-PROCESS INSPECTIONS
8b4902c5-a8a7-4ca5-879b-03e0ddbb3adf | checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 4
a2f207d9-5745-5d29-8c19-53496dc10421 | note | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
7d1acc35-bdd3-5782-89d5-a536020f5493 | note | Acceptance Criteria - Thread is in good condition
7ca26548-9a02-5515-95c3-cad3216d8181 | note | Verifying Document - Visual Assessment
15039535-194b-5e42-8124-71ceb7704d6b | note | Frequency - once
4809f7e0-1d0e-5ad0-8d98-a7f1f3f658e1 | note | Inspection Type (Visual, other) - Visual + Photographs + docket
74e2166c-3ce3-5b4b-af61-1f3ada2b522d | note | Inspection: Key - I
0520636b-f5b9-5d22-b97f-64add320aa70 | note | Inspection: By - IP
01cb2437-c23b-4b5a-b5bc-f234f9042541 | checkpoint | 4.2 - Isolating Valve Installation - Valve 4
c917a66b-3dc1-52d8-92e2-af65df2d9530 | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 4
c14125c7-4f75-58f1-9cc4-dcd4d0e7ebd2 | note | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
245086ee-35ef-52d4-8009-eea85c3089d8 | note | Verifying Document - As per drawings/Specifications & Best Practice
f6c53bb5-464d-5fbb-beb1-69d612d784a5 | note | Frequency - once
d11362f1-3223-527e-9720-40f07244839f | note | Inspection Type (Visual, other) - Visual + Photographs
981f6471-ec91-55f8-8280-59c8bf541ea3 | note | Inspection: Key - I
ed495d92-8c07-5a4a-bad7-16f0bb61b6d7 | note | Inspection: By - IP
82f9961b-1507-44cb-ad07-40aad447fe5c | checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 4
85e04e51-68e0-55d4-b3e9-43424d28df63 | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 4
7f3d72f5-3b9b-506a-8337-79ad2e8d4d15 | note | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
4b8d55e2-40ff-5445-a8a4-1c7427f1cbf1 | note | Verifying Document - Visual Assessment
4fe85e5a-405f-5a19-b39f-18ca224d9098 | note | Frequency - once
5d9fd3ce-60de-5379-b6ed-912c44b0e75a | note | Inspection Type (Visual, other) - Visual + Photographs
744ffdf3-9fb7-53d0-8dd4-1a434ce39fe2 | note | Inspection: Key - I
a50605d6-beba-5424-9ddc-afc151231d27 | note | Inspection: By - IP
3bd2fc70-7197-4ef1-a004-40d955911040 | checkpoint | 4.4 - Isolating valve 4 - Off position
8cac94c2-9c2f-5ef2-ad5b-91d9ad035bd2 | note | Inspection Point: Quality Control Activity - Pressure test
2e47ef7a-792f-5cb1-a8b7-3b80b6e07052 | note | Acceptance Criteria - Ensure all isolating valves are in the off position
4078c003-62a9-5c08-8f6a-afb9c78deadf | note | Verifying Document - This ITP
e3c4efe5-9c60-5ecf-8432-22c823b7c295 | note | Frequency - once
adbd184a-c99f-5265-8bd6-3adf0f041438 | note | Inspection Type (Visual, other) - Visual + Photographs
01246827-0654-59fa-ba53-cc053274db13 | note | Inspection: Key - I
12c0b403-3879-5202-b061-070c045c08f6 | note | Inspection: By - IP/CR
15afffe4-4acd-4914-aab1-76a1c4c7e206 | checkpoint | 4.5 - Security
145528d8-cff0-5304-ac62-b866caee26d8 | note | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
5c18f332-278e-532e-86c1-2bfe5684adc8 | note | Acceptance Criteria - Valve covers are replaced and securely in position
21a39ec8-c199-5b7f-8163-97acc6d9d8be | note | Verifying Document - This ITP
de4e1a72-3768-5721-a5ed-5ebe35329de9 | note | Frequency - once
6d6b340d-c1d7-5d38-9932-ea19a6c0d88d | note | Inspection Type (Visual, other) - Visual + Photograph
c6985806-6ade-54c4-9ff8-a6e5249659ba | note | Inspection: Key - I
430ecd7e-524f-5f18-8615-0e824b85b617 | note | Inspection: By - IP
5ed60f92-8c59-401a-afcc-6049d3fe6e54 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
fccb1405-ac54-4827-8e7e-807dcb3319cc | checkpoint | 5.1 - Red pen Mark up
517295cd-1bf3-5a74-9834-a64131fa4a7b | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
e57861e1-76b0-509b-8668-b627d164c533 | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 4 make & Model at each location
06523b83-0789-5713-a63f-e2c8c88711dc | note | Verifying Document - Red line mark up drawing / This ITP
11411f3b-580b-549e-9fbb-38a4f7a8d55d | note | Frequency - once
be8c09aa-df7d-500a-88f4-587d040dbd79 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
77672991-b093-54cd-b4d5-326e857b43fc | note | Inspection: Key - I
cbbeafd1-c336-5845-a37b-ac3520877782 | note | Inspection: By - IP
d63d22bd-9d38-4f9e-a786-d2b29fd164aa | checklist | 561483-ITP-001.5 - DRAFT - Installation of Stoney Knowe Air Valve5 - HOLD POINT | itp | 561483-ITP-001.5 - Air Valves - Delivery & Installation
cdeca2a6-4b16-45e6-9ffb-95e39f736ca3 | section | SECTION 3 – RECEIVING INSPECTIONS
ca3459d9-2eac-471d-b276-734e4e83eea6 | checkpoint | 3.1 - Take delivery of air valve 5
93d24d71-b176-534f-ac07-52f247b25567 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
e0636729-be7c-50cf-b256-aea633435d30 | note | Acceptance Criteria - Matches Design Drawings/Documents
0e1ecc1d-e1a4-568d-a46d-11bef80215f6 | note | Verifying Document - Drawings & Specifications
cf5cb172-499d-58cd-a255-95ae06c7a9a2 | note | Frequency - Once
522e72b9-54ff-5522-a4f7-913a7ac350cb | note | Inspection Type (Visual, other) - Visual + electronic
2ab51b74-61f4-5fb4-8926-5cdda261a039 | note | Inspection: Key - H
1c2f302e-35c7-565c-bd67-6330810d8f54 | note | Inspection: By - IP/PM
a462b0b9-8a4d-4b4d-a043-226cdd8428d3 | signoff | HOLD POINT
8c65a585-8a64-44d7-a5b9-ee0f784c6447 | checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
3edab98a-2517-555b-8664-3333b4ff389a | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
145de78e-a500-5d2f-bb0c-70bcbc5a1c24 | note | Acceptance Criteria - No chips to protective coating and any mechanical damage
d4be5c0f-0392-5e3f-b797-1bc9bcd6c21b | note | Verifying Document - This ITP
5215d70c-17a4-53dc-a059-4d236b6eb3e9 | note | Frequency - Once
4d6e9e63-1550-5333-8663-eaf39cc0fd89 | note | Inspection Type (Visual, other) - Visual + Inspection
4e01c76c-df10-5d62-9f95-c45ceb970818 | note | Inspection: Key - I
57560b49-263c-5666-a737-537d2ce01d16 | note | Inspection: By - IP
ef5d5c1e-5f45-4d0a-81d2-00413ef6138d | checkpoint | 3.3 - Fitment - Spatial constraints
6cda170d-fbc0-5212-b56a-c41c7453e67c | note | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
28a245b4-7db1-5001-ab44-04f973b3e39e | note | Acceptance Criteria - Measure & Check
23e2fde7-28f5-5647-8357-544a81f6078c | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
5eda169f-c129-516d-bfd0-453dcd89ce78 | note | Frequency - Once
0f0a0d4b-3944-5729-90e3-26d407def5bc | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
8df7242c-fcbe-5c35-9c3f-a53f66174968 | note | Inspection: Key - I
89d280dd-7f96-5de7-a5ef-450298af1676 | note | Inspection: By - CR
2ad02386-ae2d-425a-bd01-18ca041a3963 | checkpoint-no-value | Note:
f758c5c4-378c-5f28-b632-bac7c6c227d0 | note | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
7eaca80c-51e6-5462-ab74-8a4a5bec6dae | note | Downer to notify Engineer once confirmed.
48aad807-bc2b-4d89-86c3-1d50a8328f74 | section | SECTION 4 – IN-PROCESS INSPECTIONS
d35a94e9-0665-4501-8a37-90eaade5d614 | checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 5
2b06552d-220e-5301-a74f-00f07a879040 | note | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
4454be6c-18bb-5481-b49e-7a19b388b874 | note | Acceptance Criteria - Thread is in good condition
a00080d7-83ac-5a4a-bc01-5ce2c316925e | note | Verifying Document - Visual Assessment
987b68ba-2119-5209-9db6-ce3114e3de77 | note | Frequency - once
dcc1f271-6ce5-56d0-90ac-2e850c9a45c2 | note | Inspection Type (Visual, other) - Visual + Photographs + docket
01dcc081-bace-5145-837a-a88510f64646 | note | Inspection: Key - I
89c0564b-d5fa-5084-af4f-a9c4d5de6124 | note | Inspection: By - IP
158ba023-a306-456e-9a15-2e847a4bbe1b | checkpoint | 4.2 - Isolating Valve Installation - Valve 5
6c68d19e-b6c3-54eb-ae70-dee20fc961db | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 5
30d80023-fbc8-51fd-868c-a595ff498c0e | note | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
4ba5c176-bca8-5def-8a39-cd22ce4bb973 | note | Verifying Document - As per drawings/Specifications & Best Practice
e275f40c-4082-5d4b-9e5f-c1499ed588fd | note | Frequency - once
48374460-eec4-5058-a798-fe07b284bb5a | note | Inspection Type (Visual, other) - Visual + Photographs
82294234-62fc-513f-9300-b6a3c9dd8e2c | note | Inspection: Key - I
92553cd4-0acc-5a2a-a4b9-c98063ee3864 | note | Inspection: By - IP
70ac245b-6c5d-4fb9-9d9e-d5e7b26ac138 | checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 5
2381c1c4-c789-55c4-8e45-47d12708a147 | note | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 5
ca3a9f2a-95ab-5cf8-8f49-82934c63e4cc | note | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
efd6eeb5-5eb3-5c67-9ea1-6c9be3a4cae9 | note | Verifying Document - Visual Assessment
161df384-0279-54c6-b856-4546f21c3a83 | note | Frequency - once
3ea019da-0d51-58cf-be32-0c6566d12e71 | note | Inspection Type (Visual, other) - Visual + Photographs
420acf4e-49f0-579c-822e-7e89aa7056ea | note | Inspection: Key - I
345df81b-d259-562e-84a5-0f8079102b57 | note | Inspection: By - IP
ab86e995-5158-4d35-943b-76ec26eff8c8 | checkpoint | 4.4 - Isolating valve 5 - Off position
11decccd-aa4c-5e09-b0c3-2d871232a107 | note | Inspection Point: Quality Control Activity - Pressure test
7efde902-f888-5fd2-a02a-1f376a697cb9 | note | Acceptance Criteria - Ensure all isolating valves are in the off position
d947c407-5e39-5485-9520-c527938cb971 | note | Verifying Document - This ITP
90923969-dd1d-59a5-9f03-f1dd1eaec7b1 | note | Frequency - once
b7565936-69fe-5adf-bb1e-1a6d096227ad | note | Inspection Type (Visual, other) - Visual + Photographs
61b2dfc9-6e18-55a7-9315-3b5315091823 | note | Inspection: Key - I
1ca5d0c2-6fe2-5d34-81f3-508a711e6e62 | note | Inspection: By - IP/CR
1fcd6b04-b103-4c53-837c-013d5abb21d1 | checkpoint | 4.5 - Security
1e568a21-8056-5beb-96b2-db3687fa603e | note | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
91c5c33f-3f92-59c9-8370-f60a3ba514c5 | note | Acceptance Criteria - Valve covers are replaced and securely in position
379917a3-e195-53f7-851f-14e14589a299 | note | Verifying Document - This ITP
d014442d-51bc-5b2f-af3b-8fb4bc479817 | note | Frequency - once
ec2bd39c-82a9-52d9-916d-c2a1a49c8c7c | note | Inspection Type (Visual, other) - Visual + Photograph
af2cf836-daa0-503e-92c4-e6cd2c4ae564 | note | Inspection: Key - I
59a3a058-098f-5499-a959-65af620ef63f | note | Inspection: By - IP
3f8cccb1-69b2-4acf-8b68-881135b924dd | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
a444b3c2-5cf1-4aea-b10e-411ef9877adf | checkpoint | 5.1 - Red pen Mark up
d74721b2-4e35-5fc8-b7fc-86ca3dfe120e | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
a8713c96-9501-5ce2-af01-c4dc2b1e239a | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 5 make & Model at each location
88658f19-25d5-513a-8d70-430a3ae4e2da | note | Verifying Document - Red line mark up drawing / This ITP
c2b8f9a2-c221-5ae4-a85c-6e79203dfb94 | note | Frequency - once
dd05373a-063f-596a-9585-d7ec10628d1b | note | Inspection Type (Visual, other) - Visual + Document + Photograph
b198f0fb-0c55-57b8-ac91-62bcb649f88d | note | Inspection: Key - I
f02a948d-7ed7-53e2-baa4-0984bb3771c5 | note | Inspection: By - IP
83435f42-050c-44f5-b856-98639b8fb16b | checklist | 561483-ITP-001.6 - DRAFT - Installation of Wingatui Chamber Air Valve1 - HOLD POINT | itp | 561483-ITP-001.6 - Air Valve - Delivery & Installation
230d8e2d-1f46-4cc2-b913-031ec06f5094 | section | SECTION 3 – RECEIVING INSPECTIONS
2697f2b2-4ee8-4152-b8ef-020b7f9bf06f | checkpoint | 3.1 - Take delivery of air valve 1
781a8993-541d-5dda-9485-e87729734164 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
4d5ca385-1ae5-56f4-a6ea-4520abd94dda | note | Acceptance Criteria - Matches Design Drawings/Documents
99f0c9f1-f3d0-53b5-a385-df2f5701f255 | note | Verifying Document - Drawings & Specifications
795f4ed6-6eb9-5fc1-9b62-4748a83f5d8e | note | Frequency - Once
ddb886f4-77e2-51b0-acfd-94457a05b270 | note | Inspection Type (Visual, other) - Visual + electronic
49da9489-f68c-5d04-9f98-896361233fcc | note | Inspection: Key - H
74ff4ed8-44ed-5dab-83f9-3a4073e1d642 | note | Inspection: By - IP/PM
3e739b7d-7f44-439e-852b-5b83e79403fb | signoff | HOLD POINT
6eeb2977-a144-4271-a86a-e32bfa385456 | checkpoint | 3.2 - Take delivery of valve position inticator 1
287b1137-54cf-5c2f-82be-07789ead1315 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
67716f40-4c8f-5129-98f5-6754a29d3e64 | note | Acceptance Criteria - Matches Design Drawings/Documents
1f6d0a2a-1779-5425-bc8d-6f69cc033b3f | note | Verifying Document - Drawings & Specifications
5652bb4a-5cbc-51bd-b5d4-fa4731f2ce58 | note | Frequency - Once
558f3b7b-9845-55e8-8c2c-d338259ec53d | note | Inspection Type (Visual, other) - Visual + electronic
3eff7c37-c715-5d67-9637-426cc910bf39 | note | Inspection: Key - H
e1b78b95-241a-51c6-9f02-af0d30826dea | note | Inspection: By - IP/PM
a23722ed-348f-4604-9ab7-b0a4b84ce292 | signoff | HOLD POINT
6c441200-47f3-40b0-a3ca-acefec45fe61 | checkpoint | 3.3 - Inspection of Air valve for any sign of transit damage
f4c86e45-c576-50d3-9b66-b61259b30bd2 | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
79d49998-be60-59ce-ad56-5663b2a39991 | note | Acceptance Criteria - No chips to protective coating and any mechanical damage
7e681284-26ff-577b-bb17-0e3eb0b8c98b | note | Verifying Document - This ITP
e1ec2171-6463-523c-9934-ef8faa1e8c0b | note | Frequency - Once
c66f810c-3fb0-59ad-a1b8-358cb6c10976 | note | Inspection Type (Visual, other) - Visual + Inspection
633f9dce-a257-5335-ad30-b15bf1d1c033 | note | Inspection: Key - I
4db2cba0-ac0e-5e44-9cc9-214fb9032a62 | note | Inspection: By - IP
5433d675-e40f-4c1a-a89b-53e0346286a4 | checkpoint | 3.4 - Fitment - Spatial constraints
4259a7c7-367f-5ab9-9d38-eb4d0da817a6 | note | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
66499cec-c051-540c-8eab-b5acdc67e49b | note | Acceptance Criteria - Measure & Check
e84aab81-20f2-5d80-a977-551d95ca0ca5 | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
d57470da-efb2-5882-abe4-25422ad91295 | note | Frequency - Once
42267d70-4af2-5f93-8c8a-98fb7361343e | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
c2361271-1daf-52a7-a9f3-976287dec42e | note | Inspection: Key - I
d778b40e-5240-5e1a-b2e0-7a8241dec498 | note | Inspection: By - CR
7f992141-7d0b-4092-922e-890af2200569 | checkpoint-no-value | Note:
84f5214c-ec7c-5740-a87b-1778c3b0c8f4 | note | Air Valve 1 & Valve Position Indicator 1 are to be fitted to Control Valve 1 (200mm dia)
26635dfc-1ad8-44d9-917a-3de795bd5968 | section | SECTION 4 – IN-PROCESS INSPECTIONS
05afd9a7-5443-4df0-8c22-099fe08258e0 | checkpoint | 4.1 - Connection to Wingatui Valve Chamber - Valve 1
8babe567-53e2-5926-8dfd-8593424d7280 | note | Inspection Point: Quality Control Activity - Air Valve 1 is installed in vertical position
cd19e33a-5b4f-5777-b892-ee2c0719650d | note | Acceptance Criteria - Air Valve is installed leak free & free of obstruction. Installation as per Manufacturers instructions
decb9014-9c46-5042-a94b-3c55a980b492 | note | Verifying Document - Visual Assessment
270b36fb-79a5-548e-87f5-2c17453f699a | note | Frequency - once
2097807a-f3bc-59db-bbe8-a12e60b742ab | note | Inspection Type (Visual, other) - Visual + Photographs
0f8f2af0-cb59-5e71-a5bf-6cbcd2aa13f4 | note | Inspection: Key - I
b8818908-5bde-55b3-aebe-30c638545d54 | note | Inspection: By - IP
6af606c7-e8e9-446f-9e88-b6fab406c6cf | checkpoint | 4.2 - Connection to Wingatui Valve Chamber - Valve 1
191e4302-c2bc-5c26-bb0a-9e297050602f | note | Inspection Point: Quality Control Activity - Valve Position Indicator 1 is installed in vertical position
bcddc19c-f38e-56d4-9524-10738e0d43db | note | Acceptance Criteria - Valve position Indicator is installed leak free & free of obstruction. Installation as per Manufacturers instructions
f15c61f5-1550-5f26-84ae-63bcf75a3850 | note | Verifying Document - Visual Assessment
958be71d-8c4e-5d5c-9c2c-13ee5c5a6877 | note | Frequency - once
41f271b7-5d77-558a-83c2-42ba23e9644e | note | Inspection Type (Visual, other) - Visual + Photographs
b329c166-30ba-52b2-b49d-d1967e2a7057 | note | Inspection: Key - I
71bfbb82-1b7e-5fb3-b117-2c6e651a4362 | note | Inspection: By - IP
fcf8f8e5-70dc-41f7-9b07-576f7c5868c8 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
d4f51ad4-298c-41f6-9a39-ac24feb9aee8 | checkpoint | 5.1 - Red pen Mark up
63a8114b-494c-5112-b0c5-79116dce0ba8 | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
3a5ac0c5-7d19-5d0e-9f49-c4b80e1184d2 | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 1 make & Model at each location
ee19bb37-59e9-5cf6-be2a-450828412f24 | note | Verifying Document - Red line mark up drawing / This ITP
6bd05d28-d5c5-5425-b2a0-8f1511914e15 | note | Frequency - once
0267c222-e87b-5ba4-bf40-7ff413a57440 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
610d1082-10a0-59c4-91c0-690142f4fc1b | note | Inspection: Key - I
9255b036-50d4-533d-b922-6bb7ac17b684 | note | Inspection: By - IP
9a92f0a5-d641-4036-acf7-83109cc313fa | checkpoint | 5.2 - Red pen Mark up
2f7d0e77-4d07-5478-8e68-4889c383de4f | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
e00572e2-4af5-5a2a-b658-687da9a5cc13 | note | Acceptance Criteria - At completion of all items on this ITP identifying Valve Position Indicator 1 make & Model at each location
a2f083e2-2083-5337-9e97-3f276fdc8fdb | note | Verifying Document - Red line mark up drawing / This ITP
aa4e4007-4fb7-59c2-a79f-fd6eadc52f3f | note | Frequency - once
1bfac287-1397-57f9-b9b1-15416f61cab3 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
1b63eb07-8a72-56ab-8668-899bdba6dba9 | note | Inspection: Key - I
5d4a636a-bdb6-5d47-b516-96d040225321 | note | Inspection: By - IP
810d16bc-751a-4a9c-aa78-2caf84ad1151 | checkpoint-no-value | Air Release Valve / Valve position indicator
99be106a-254f-5340-a384-86700faf3f35 | textbox | Air Release Valve - Manufacturer:
8a90889d-a134-5dc4-90ed-1a9db1aa8847 | textbox | Air Release Valve - Model:
dcda955e-4ae3-506a-ac0a-0a0e5d48d4e7 | textbox | Air Release Valve - Serial:
e463d714-f921-5260-a1a3-a96816685856 | textbox | Valve position indicator - Manufacturer:
e237696b-4d41-5496-824c-10caa7b3cf6c | textbox | Valve position indicator - Model:
f7373633-6bf8-561d-8644-43e2d89a9b0a | textbox | Valve position indicator - Serial:
c12136a8-6743-46bc-bc67-a9c06c39bb0c | checklist | 561483-ITP-001.7 - DRAFT - Installation of Wingatui Chamber Air Valve2 - HOLD POINT | itp | 561483-ITP-001.7 - Air Valve - Delivery & Installation
bdd2860f-cf2b-4399-9c13-aaa7604bde3a | section | SECTION 3 – RECEIVING INSPECTIONS
c6336cd1-ffba-4a0d-ad74-b7fc2cc76ee1 | checkpoint | 3.1 - Take delivery of air valve 2
952b1d8a-3340-5eb1-a1ac-94fbed188143 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
c5c7e592-8938-521c-b26f-959be9e28fed | note | Acceptance Criteria - Matches Design Drawings/Documents
401a448e-7700-52f5-9376-9e8badde1e42 | note | Verifying Document - Drawings & Specifications
2b4411dc-bbab-5b32-9cdb-0298dbf2c271 | note | Frequency - Once
de0de80f-439c-5c82-858b-eccdb6541ff5 | note | Inspection Type (Visual, other) - Visual + electronic
88e91a37-46dd-581e-aa46-61f310b3e100 | note | Inspection: Key - H
d5b63885-32f0-5802-a505-cb166066800f | note | Inspection: By - IP/PM
99b8c4d6-b88b-4737-acd5-cc579d2d273c | signoff | HOLD POINT
2f9aeebe-8691-491b-aa38-dcef5ff54532 | checkpoint | 3.2 - Take delivery of valve position inticator 2
41247704-1bec-533c-98b7-4c0fda6d1312 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
b5c330a6-200d-514b-9878-954db81c37c6 | note | Acceptance Criteria - Matches Design Drawings/Documents
95014eb7-4ddb-598f-95cf-caf9ecc1c1c9 | note | Verifying Document - Drawings & Specifications
41e5b736-2075-5617-8e2d-461f74c9d027 | note | Frequency - Once
0948b1c9-ce3d-5c59-8fa5-44a0c9866de5 | note | Inspection Type (Visual, other) - Visual + electronic
56752f08-d7a4-51be-8bbd-cc27a945c0c4 | note | Inspection: Key - H
3b117fea-12ff-5424-861d-137d54cf6fb5 | note | Inspection: By - IP/PM
d55fcbca-58c9-4292-ad1c-537b6a0f2654 | signoff | HOLD POINT
b8fb1f16-410c-40cb-9b66-5a5a5b95eab0 | checkpoint | 3.3 - Inspection of Air valve for any sign of transit damage
968ff834-9368-5c7d-beb4-62a3fae3091d | note | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
b0067fc8-be74-524b-b849-418b972d2d78 | note | Acceptance Criteria - No chips to protective coating and any mechanical damage
0e9ee410-f83f-54ea-9655-92631b393f16 | note | Verifying Document - This ITP
e918c398-356a-5251-8f7e-b54770220c8d | note | Frequency - Once
e15285a7-f81d-5743-81fe-253b16dce9cd | note | Inspection Type (Visual, other) - Visual + Inspection
96da4d8d-2b92-5e20-ae25-a753c51ae828 | note | Inspection: Key - I
0a9e7270-0f98-53b7-b894-867c2ad25cbb | note | Inspection: By - IP
92cd3c0d-0299-4466-b6cb-814c113644a8 | checkpoint | 3.4 - Fitment - Spatial constraints
b358df0c-caba-5ff2-9fb0-e3be0d0b0b6a | note | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
a1d072a2-6e77-58f2-9fb3-7bf25e4a02f6 | note | Acceptance Criteria - Measure & Check
373dfb6a-7daa-5ac4-bfed-c204cea6312e | note | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
9d53e7cd-de93-577f-b9ad-ff5412333161 | note | Frequency - Once
aae45f37-5f37-5c73-b2bc-7dbefe027689 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
0e6d05c2-efbd-50c8-a34d-8bad256fb434 | note | Inspection: Key - I
14c7e548-e786-5060-a38f-eabdbb953bbf | note | Inspection: By - CR
b550f3bb-a7bc-4915-b46f-b5450fa22a50 | checkpoint-no-value | Note:
8fb1ec3b-a0fd-555c-867f-10d502ce8fb0 | note | Air Valve 2 & Valve Position Indicator 2 are to be fitted to Control Valve 2 (250mm dia)
cdd2e9a2-4afc-4d2a-8fc5-4194f0df7820 | section | SECTION 4 – IN-PROCESS INSPECTIONS
5a8f5d97-4ff3-4189-8c2e-e8b6d1063cdc | checkpoint | 4.1 - Connection to Wingatui Valve Chamber - Valve 2
0d94a15c-9743-55c1-9e2f-d682d97b140f | note | Inspection Point: Quality Control Activity - Air Valve 2 is installed in vertical position
34cf7b83-380b-526e-b874-13314ef56bea | note | Acceptance Criteria - Air Valve is installed leak free & free of obstruction. Installation as per Manufacturers instructions
a1774f21-0b62-55d0-bb51-dc51b7048514 | note | Verifying Document - Visual Assessment
b6f32524-3c4b-52d3-b055-2001d12ab8ac | note | Frequency - once
a7e15551-8d54-5b5f-b1c8-1ee3ab8c384b | note | Inspection Type (Visual, other) - Visual + Photographs
650ab13b-7043-5773-b204-319fb4862f00 | note | Inspection: Key - I
a022ff46-5dcf-5507-a7fb-8283b77f5515 | note | Inspection: By - IP
7e109999-2a71-420a-a5fe-cc1cb7f9a0a7 | checkpoint | 4.2 - Connection to Wingatui Valve Chamber - Valve 2
7809a827-d769-5ec2-93ff-5cb2fc7c659b | note | Inspection Point: Quality Control Activity - Valve Position Indicator 2 is installed in vertical position
1c724dbf-d75d-5f0d-b731-5a2447101e80 | note | Acceptance Criteria - Valve position Indicator is installed leak free & free of obstruction. Installation as per Manufacturers instructions
9186ba59-317c-5fa3-adbf-b84c64a25143 | note | Verifying Document - Visual Assessment
923f7ba6-e55f-5cfe-ab6b-2280ca216c6d | note | Frequency - once
1457324d-0044-5bf1-91c9-b8b405246f2e | note | Inspection Type (Visual, other) - Visual + Photographs
fd4d3a42-a5a6-517e-9802-3ff46490d2f7 | note | Inspection: Key - I
d3e9738e-f7a3-5dc1-9e15-a35191e38ca1 | note | Inspection: By - IP
86ad7d3d-4e09-45ff-b1a9-636d734e5ba2 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
8ca36610-ee60-4ecf-9f48-fe5b44d1492a | checkpoint | 5.1 - Red pen Mark up
5b1e14ac-6cd4-5877-af5e-040cabf79b91 | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
27a282b3-551c-53ee-bc30-d111cdf85395 | note | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 2 make & Model at each location
cb330d80-40cc-5a73-ba32-96dde09b5e58 | note | Verifying Document - Red line mark up drawing / This ITP
6c4cb8c3-a2d8-5225-9a25-2731e1df4f4d | note | Frequency - once
132f53eb-523d-538a-b5ab-22d94a933680 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
f1b08479-e73c-585e-9391-8d8191d498ae | note | Inspection: Key - I
4436406e-77cd-5e7c-a324-b5395a31d114 | note | Inspection: By - IP
7a435a57-cd88-4659-80e4-8ff9877a0fab | checkpoint | 5.2 - Red pen Mark up
da51d0ca-89b6-578e-9573-54d05c817c65 | note | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
eb6b815f-a243-5ef2-9439-096c0968165f | note | Acceptance Criteria - At completion of all items on this ITP identifying Valve Position Indicator 2 make & Model at each location
7e633487-07b5-526c-92cc-9f97e7cb5fe1 | note | Verifying Document - Red line mark up drawing / This ITP
7593fa9c-934a-5312-ba6e-23b085a8b94d | note | Frequency - once
253ebf23-b1ca-50d0-ba64-47b58f54a5e8 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
8979f251-de44-5ea5-ab8a-40e93189457f | note | Inspection: Key - I
73b82b46-ebf7-5975-99c1-f6c2311c29af | note | Inspection: By - IP
3d8f9274-d343-46d8-b9ca-4926fe69182c | checkpoint-no-value | Air Release Valve / Valve position indicator
e011b86a-0bf0-5c6b-8600-60c1c325e1c5 | textbox | Air Release Valve - Manufacturer:
f2155e94-4a17-559c-9c08-379ef0d55b49 | textbox | Air Release Valve - Model:
785497d2-7828-5ac8-9bcb-1f4e246f3714 | textbox | Air Release Valve - Serial:
488e5c3a-0b2b-519f-acc1-95b0496e5a25 | textbox | Valve position indicator - Manufacturer:
caf9788b-ea39-585e-9e0d-e8943b9ac780 | textbox | Valve position indicator - Model:
d3e0a3a7-45d4-57bf-9460-d5ed09d371ed | textbox | Valve position indicator - Serial:
15d120d0-1843-4302-83b1-aef999d1e512 | checklist | 561483-ITP-002.1 - DRAFT - Wingatui Valve 1 Valve installation - HOLD POINT | itp | 561483-ITP-002.1 - Valve - Delivery & Installation
6c284a97-a6ae-4875-9572-9f052492fb3d | section | SECTION 3 – RECEIVING INSPECTIONS
74cb1389-dca6-4c5b-aaff-d578eb3e1eb3 | checkpoint | 3.1 - Take delivery of valve 1 assembly
a754bca4-604d-5364-98f8-53e68974804e | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
99722d08-52c3-5b89-bb4b-1d5761b24655 | note | Acceptance Criteria - Matches Design Drawings/Documents
c9d45925-03e7-52f6-9e83-d036b5f86a1a | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
2415ea6c-be14-56b1-9805-e0b5d4cc9175 | note | Frequency - Once
5a13d09f-e588-55ad-9d38-5846bde80e80 | note | Inspection Type (Visual, other) - Visual + electronic
8ee6ee2c-5885-58d7-854e-748642828f66 | note | Inspection: Key - I
5b7123ff-853e-5408-b676-795b3e335cb0 | note | Inspection: By - IP/PM
9367f9f9-03da-4f46-896b-14c048ba3665 | checkpoint | 3.2 - Take Delivery of Valve position indicator
5c8a7544-55d9-5fc8-b540-eef6af49df98 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
d06abcc4-e274-5dfe-a81d-248e9a397a49 | note | Acceptance Criteria - Matches Design Drawings/Documents
fe9fe761-eac9-53bf-9176-ab68545d02ad | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
318d8635-e168-5c1e-acef-535d3a5226ff | note | Frequency - Once
6c64a722-1918-5f4e-821f-1d603460cab4 | note | Inspection Type (Visual, other) - Visual + electronic
dd255c9f-d09b-53a2-9573-55483461d3ab | note | Inspection: Key - I
be455c25-2039-5195-b342-b61366a5ec8b | note | Inspection: By - IP/PM
bf7f0564-096f-4f38-bfbb-9bef0ff69bdf | checkpoint | 3.3 - Take Delivery of Air Release Valve
e47b4e44-3c6d-53b0-9fd0-6af2f883254c | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
ad4f1c88-2e47-5355-9ffc-37427c1620f5 | note | Acceptance Criteria - Matches Design Drawings/Documents
c47caf85-f9dc-548a-93a9-aef41d4f2e41 | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
33c496db-a28b-5787-9659-79b3d6ab96fc | note | Frequency - Once
749dcbae-21f5-5671-ac69-c1e51d870366 | note | Inspection Type (Visual, other) - Visual + electronic
991a9743-7564-5dd4-a550-d2962825c783 | note | Inspection: Key - I
4c9158f0-317c-575c-96fd-a35ec1cd0f19 | note | Inspection: By - IP/PM
9da6bb14-18d8-49ec-abb0-5cdd208eb70c | checkpoint-no-value | Note:
7d424a36-fb3d-5c50-be60-8ebe8148446a | note | Downer HS&E to assess as to whether Valve chamber is Confined Space.
21a05088-22b3-4478-b2fe-7855068e78d3 | section | SECTION 4 – IN-PROCESS INSPECTIONS
d4864993-c668-4735-89f5-ee6f9a40ac6e | checkpoint | 4.1 - Shutdown preparation
42b81d1d-3763-5b86-bf6f-2c343ef2bccb | note | Inspection Point: Quality Control Activity - Arrange with Client & Engineer for shutdown
1b21c260-219c-527d-971f-6ff8c6341d0a | note | Acceptance Criteria - Acceptance from client & Engineer
17dffe77-f8ad-5c42-ab2c-4c91f852ff3d | note | Verifying Document - Written, via email or NTC
eac9909d-a9d4-5525-80ba-5d6efefa6d93 | note | Frequency - once
3e7f98a8-ff54-5796-8adb-0b4f1753aa04 | note | Inspection Type (Visual, other) - Written + Inspection
a697f33b-b5d8-598f-9f73-4f7818886ee5 | note | Inspection: Key - I
dd1f4a8f-d8b6-5674-95f3-a1e5a6cfc8c4 | note | Inspection: By - IP
3226a967-7ae2-42a8-8519-867c25825c8b | checkpoint | 4.2 - Valve position indicator
cecc772e-5a3c-597a-82f1-3515c599a14d | note | Inspection Point: Quality Control Activity - Correct installation of valve position indicator and fittings
21150c22-509a-5a09-889b-b90dd944456f | note | Acceptance Criteria - As per manufacturers installation instructions. No leaks and orientation is correct
f848fe54-35b5-50c7-893a-47523935fd5e | note | Verifying Document - This ITP
8f69048c-8a97-5023-8c6d-3e9af2878739 | note | Frequency - once
0ff93eed-2a50-5024-9cf5-5b8d91237d3e | note | Inspection Type (Visual, other) - Visual + Document + Photographs
df940c77-f5c5-52f2-a103-0763757d63e2 | note | Inspection: Key - I
295ce132-72ca-54fc-b0d2-ec98b98f1813 | note | Inspection: By - IP
91db1e03-1286-4d7a-abae-850ed0f66121 | checkpoint | 4.3 - Air Release Valve
f12ff636-f1dc-55b6-a8de-155cc00b7c69 | note | Inspection Point: Quality Control Activity - Correct installation of air release valve and fittings
78243f66-1b62-5627-9679-0dd14bee0a74 | note | Acceptance Criteria - As per ClaVal installation instructions
66cda006-6550-5790-8df1-40888ed4c4d3 | note | Verifying Document - This ITP
b6dd2d5c-56c7-5ccf-ad3b-96f5a8a5d24c | note | Frequency - once
225cf15d-0207-576e-a750-643fea0c94b9 | note | Inspection Type (Visual, other) - Visual + Document + Photographs
d3d2d3f0-29fb-52c6-8cca-2599496afbe3 | note | Inspection: Key - I
564d364c-ff4e-54ee-acd7-6519b29ed4db | note | Inspection: By - IP
e43d7d4d-0c00-408d-905a-317de8127652 | checkpoint | 4.4 - System reinstatement
fb0e356b-6e0c-50a9-bc32-a1713bc4ee4c | note | Inspection Point: Quality Control Activity - Open main valve to reinstate wate rsupply
f2173ee0-6079-5280-a663-962582fe0b5f | note | Acceptance Criteria - Completion of item 4.2
96457736-cf19-5fd2-92da-69a6da85a33b | note | Verifying Document - Inspection and this ITP
53ead742-8317-590b-99da-d0d04d1b02fa | note | Frequency - once
322f7bdb-e4e5-51be-ae74-d33ddafbb76d | note | Inspection Type (Visual, other) - Visual + Inspection + Photographs
90399eed-6912-5f51-b0a0-915764983b2e | note | Inspection: Key - I
1cd1c0f0-8a64-58ce-9ace-40ae0d12acc1 | note | Inspection: By - IP
b515c8a7-d959-4266-933c-5d93418c4460 | checkpoint | 4.5 - Adjust
94e9712a-18dd-5950-9536-3027f20298e9 | note | Inspection Point: Quality Control Activity - Adjust the pilot valve to obtain the correct flow 113m Head.
80075e70-daff-5be1-a623-ed86ba957767 | note | Acceptance Criteria - Obtain specified flow rate ClaVal technician
5fcdb5de-ad52-5a66-bc13-d5bca7e1d4c2 | note | Verifying Document - Specification flowrate
48514938-1de0-5414-9fd0-d8d000bfe9dd | note | Frequency - once
b5a6ac53-ae5b-524c-bdaf-775fbd39a399 | note | Inspection Type (Visual, other) - Visual + Document + Photographs
cb6d1d37-46fb-5858-be4a-b5111b404bb6 | note | Inspection: Key - I
60c2fc63-e2c1-5ab9-8d6a-cb768c87397b | note | Inspection: By - IP/CR
3f65708e-3ae6-4a00-81f7-4e50b361f3ac | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
481050d6-37c4-4f77-9d07-1c6c7489e09b | checkpoint | 5.1 - Red pen Mark up
c044c85d-8fba-5383-89cc-4ad33e86249f | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP. Document upgrade and record new flow rate & pilot valve position setting
848c67ec-bf91-5515-90ec-9cbccab8f6f4 | note | Acceptance Criteria - As per specified pressure & flow or client requirements
42a62691-8d61-58a5-88de-037cf64a6046 | note | Verifying Document - Red line mark up drawing. This ITP
4be22be4-aee1-53a0-8d69-745495880b5c | note | Frequency - once
aaf1e85c-62a4-558d-ad7e-8d7127a6574d | note | Inspection Type (Visual, other) - Visual + Document + Photograph
5cca9443-dece-5a55-b2a5-7b724d3ae543 | note | Inspection: Key - I
0260acec-1e90-5664-b534-234bc5273913 | note | Inspection: By - IP
80cd6809-b7c4-4970-8faa-2065cc3b7ff3 | checkpoint-no-value | Head / Flow
2c102d70-5949-51e2-919a-0ec96d511f7b | note | Head
418bd8bf-04fd-531f-b9e4-4c7ad835f311 | note | Head - Specified: 113m
0142d6b3-af85-567e-ae92-d160ed14edcf | textbox | Head - Recorded:
e6ab0923-5271-5dd3-919e-4108139d841f | note | Flow
ac414fd6-b9a5-517c-aa37-f23fbd35b56a | note | Flow - Specified: 130L/sec
eb32b414-3a46-5b2f-9815-56d558a9e6d6 | textbox | Flow - Recorded:
97459405-6f0d-4e77-8d44-f51c8db604ca | checklist | 561483-ITP-002.2 - DRAFT - Wingatui Valve 2 Pilot Valve installation - HOLD POINT | itp | 561483-ITP-002.2 - Pilot Valve - Delivery & Inatallation
fbf7ed58-3a12-49f7-ad9b-4ad4b3dea4d0 | section | SECTION 3 – RECEIVING INSPECTIONS
1b590d23-0db0-42bc-818c-0618995fc904 | checkpoint | 3.1 - Take delivery of pilot valve assembly
574871ce-7629-55a7-8956-c52a6db5316f | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
d015b7e8-a92f-590f-8519-f081b836fa5f | note | Acceptance Criteria - Matches Design Drawings/Documents
bea16070-9ea2-5c65-9962-89263dc1f231 | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
e093af6f-d6db-5326-8527-23a77a48d862 | note | Frequency - Once
ddf18716-ed75-5c0b-91b0-51efbaac3949 | note | Inspection Type (Visual, other) - Visual + electronic
b0a8b4b8-4ec3-5ac0-9b88-284a05d0fe68 | note | Inspection: Key - I
1978bb2f-d6f6-53a1-b364-a2690a621f07 | note | Inspection: By - IP/PM
4b4757c9-0449-48f3-a97d-a52e99c56490 | checkpoint | 3.2 - Take Delivery of Valve position indicator
75365fd0-e05e-5125-98f4-f2f257cff78d | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
e50ca593-1d90-5019-9b99-cc7ca6624a18 | note | Acceptance Criteria - Matches Design Drawings/Documents
4ce900a9-a5ca-5fee-a921-be414202afad | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
2edd579d-8b7f-53ab-8e23-7c47858ce553 | note | Frequency - Once
335fd206-a2f4-5e99-b2ca-c4aac6b8f166 | note | Inspection Type (Visual, other) - Visual + electronic
eb94d6a5-0fa9-528a-a7dd-11ec7c6c3da7 | note | Inspection: Key - I
bd49ba54-6828-565e-96d2-91a8d2f1b83e | note | Inspection: By - IP/PM
7cb91038-6c13-47a0-ae91-440480af61c4 | checkpoint | 3.3 - Take Delivery of Air Release Valve
cc241639-a6f1-51f0-b882-9aac72b813ef | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
f8f75b8c-1c15-5396-884f-bb8f1625987d | note | Acceptance Criteria - Matches Design Drawings/Documents
59f81923-1561-593f-8f50-977abb289d01 | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
64a470a9-47cf-517c-8507-8fd6b73d96d6 | note | Frequency - Once
530011dd-c552-571b-8082-588791c8d7ba | note | Inspection Type (Visual, other) - Visual + electronic
2b3e54f2-378e-5cff-82c4-7f7a09a7115f | note | Inspection: Key - I
792290aa-643c-51b3-98da-31bbb0f54a48 | note | Inspection: By - IP/PM
cb673aca-e483-4bf1-a70b-d0ac71105760 | checkpoint | 3.4 - Valve Assessment
c80a2d4d-e16b-56ef-be40-faca8939d9e4 | note | Inspection Point: Quality Control Activity - Internal valve component inspection
b4f18a20-852c-5ca3-8fdf-94729835abfe | note | Acceptance Criteria - ClaVal Assessment
b0efa869-ae04-51e1-927a-e49acc498371 | note | Verifying Document - Claval report and verification
303b2519-b42f-529f-ac63-d00c2e160497 | note | Frequency - Once
e77e22f2-47c6-5800-ac86-801f9adb7d14 | note | Inspection Type (Visual, other) - Visual + electronic
ed3fb432-812e-522b-8dad-7ad27db05551 | note | Inspection: Key - H
b8f9eb8d-62ee-5269-abda-0eeb95aaebea | note | Inspection: By - IP/PM
b3f4503e-3010-473b-ae70-6a08a441e1f4 | signoff | HOLD POINT
d95bbab3-ffcb-4593-995b-6633e79a069b | checkpoint-no-value | Note:
805a1b23-7613-523d-87a1-b8a94ed5da92 | note | Downer HS&E to assess as to whether Valve chamber is Confined Space.
84b23be5-2877-4181-81ff-b35394571eab | section | SECTION 4 – IN-PROCESS INSPECTIONS
f81d2aaa-bd15-4e9a-92a4-6ae90b5e3065 | checkpoint | 4.1 - Shutdown preparation
5815177f-4909-5d7a-814d-dcc223116693 | note | Inspection Point: Quality Control Activity - Arrange with Client & Engineer for shutdown
136c93b5-11a1-5f3c-9459-54dd7f1a0955 | note | Acceptance Criteria - Acceptance from client & Engineer
4d519c0d-94a1-5387-93f5-1d3587259aa4 | note | Verifying Document - Written, via email or NTC
4fbef022-58b1-50b8-9be3-f2961f73996c | note | Frequency - once
2292f447-9cca-54d4-9ddd-f63937a2dd0e | note | Inspection Type (Visual, other) - Written + Inspection
fcb29733-05c1-5766-b95d-25afab7953ff | note | Inspection: Key - I
67eec3ef-0c40-5439-823c-4fb4bcaa02b7 | note | Inspection: By - IP
6b832ca7-5ce9-4ad3-926f-76944da21894 | checkpoint | 4.2 - Pilot Valve
1e602d77-3f3e-5582-bf4c-7e3a9e1f47c4 | note | Inspection Point: Quality Control Activity - Install new pilot valve and ancillary items
66d54fa9-768a-5ada-947e-de5c5b4d1285 | note | Acceptance Criteria - As per manufacturers installation instructions. ClaVal technician
dcd7fe6e-79d8-5720-ae20-614eb085d82f | note | Verifying Document - ClaVal Technician sign off
01c87ec4-709d-5c2a-8a61-06a85477e89c | note | Frequency - once
c3a5831e-e976-5075-9308-7a7403b0a61d | note | Inspection Type (Visual, other) - Visual + Document + Photographs
4e969203-8a46-55f0-8584-0c05ea027092 | note | Inspection: Key - I
a6ed8f5b-a9b9-5ce0-bd23-9c6b27885486 | note | Inspection: By - IP
6cb8096f-63bd-45d5-b21a-d3ed1e1f755b | checkpoint | 4.3 - Valve Position indicator
2e585262-c0c6-5ecd-837e-b76f60a0f196 | note | Inspection Point: Quality Control Activity - Correct installation of valve position indicator and fittings
f111cb5a-9099-5cba-a92d-efbdb9c58234 | note | Acceptance Criteria - As per manufacturers installation instructions. No leaks and orientation is correct
cb7719ca-4a3a-52e8-8623-78ee79941dbd | note | Verifying Document - This ITP
00355771-5525-5684-84fa-5fc8c8a77cfe | note | Frequency - once
95c6398a-6f81-5a47-a398-48593dc68b1d | note | Inspection Type (Visual, other) - Visual + Document + Photographs
65d98585-871b-5733-81f3-a568fd6a3bbd | note | Inspection: Key - I
97980f15-99cf-5b87-bbe8-8282bc47b461 | note | Inspection: By - IP
c9ca4939-be89-498b-ae76-62c5a7200dd1 | checkpoint | 4.4 - Air Release Valve
d702ef61-0f4a-5679-b43a-1f7b3bcd7180 | note | Inspection Point: Quality Control Activity - Correct installation of air release valve and fittings
c58aba3e-b6c3-58b4-b5c6-eaf45d2a7fdc | note | Acceptance Criteria - As per ClaVal installation instructions
6f3c371d-5048-5ec4-9cdc-9f8ffbaa3061 | note | Verifying Document - This ITP
0808cebe-5c4e-547f-b052-b774d1ca8be2 | note | Frequency - once
b6aad1ad-9bbd-578e-948a-59cc907f5022 | note | Inspection Type (Visual, other) - Visual + Document + Photographs
a9b599e7-0c6e-50d2-a596-268e4462bdf4 | note | Inspection: Key - I
0187a5e7-0977-5efb-a8de-b8bcf6c05b64 | note | Inspection: By - IP
892677fd-e69d-4915-a8ec-e43eeb403e13 | checkpoint | 4.5 - System reinstatement
03aa99d0-cbca-5331-b3b5-4263d430f651 | note | Inspection Point: Quality Control Activity - Open main valve to reinstate water supply
0843504c-877c-54f3-9a28-023dd3e7c16f | note | Acceptance Criteria - Completion of item 4.2
08ffda99-f2b4-5be6-8c09-10889bd96953 | note | Verifying Document - Inspection and this ITP
dce78344-9821-57cf-9c94-7c88645d5871 | note | Frequency - once
5b8e82c1-a027-503d-9ade-0464480b338f | note | Inspection Type (Visual, other) - Visual + Inspection + Photographs
295cc54d-f5fb-538c-86b7-2872ad30db2f | note | Inspection: Key - I
91dce1c0-15fe-5aca-bb80-6493e7307989 | note | Inspection: By - IP
b3bee91b-72f4-456b-b805-5e450c2a7467 | checkpoint | 4.6 - Adjust
ca03bf6a-5437-5df2-9651-1a2969a0c74a | note | Inspection Point: Quality Control Activity - Adjust the pilot valve to obtain the correct flow 8.5m Head & 130L/sec
19140afa-f320-5c35-8090-cce05f17f823 | note | Acceptance Criteria - Obtain specified flow rate ClaVal technician
bc0b5c34-674c-55eb-9522-3a2149ce7868 | note | Verifying Document - Specification flowrate
093e631f-30fa-599a-9706-c76405de2d57 | note | Frequency - once
87c9ba88-10a6-5db4-907f-ac3304086acb | note | Inspection Type (Visual, other) - Visual + Document + Photographs
3dc21f11-2522-5573-a7f8-0f0392863af9 | note | Inspection: Key - I
1a676197-efad-522d-b8e8-d9f664550938 | note | Inspection: By - IP/CR
b6eefcfc-a2ea-41de-9201-ca2e6c516eaa | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
3fd93837-5bde-4508-8873-e83a2dd832d0 | checkpoint | 5.1 - Red pen Mark up
186230ae-c0ed-5c40-b43b-cf5a8db2b0dd | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP. Document upgrade and recored new flow rate & pilot valve position setting
b3edc26c-33ba-5beb-997b-9890fce3b6bd | note | Acceptance Criteria - As per specified pressure & flow or client requirements
cd89aba3-3518-563e-b195-a010643f67bf | note | Verifying Document - Red line mark up drawing. This ITP
b5ebfdc5-5d0a-5788-a632-6f68ad171b3d | note | Frequency - once
2ba4e2d6-adb3-560b-923a-c63683f95ab2 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
6c23abbd-1e17-50c6-9284-da43ca09ed8d | note | Inspection: Key - I
ec3f4a49-72d4-582d-9a80-acb71cb5540a | note | Inspection: By - IP
51c9ae36-b466-4c34-9c3c-cbdc445c3502 | checkpoint-no-value | Head / Flow
5fdcb0d7-c7e7-5977-95f9-05705b252504 | note | Head
3ba65a5c-9740-5014-94a0-ae3bffa52633 | note | Head - Specified: 8.5m
211ef67b-c6b9-5e61-ba39-8dba24abd88f | textbox | Head - Recorded:
97da3c26-db27-59b2-b75e-5964894749aa | note | Flow
c57ad829-56d2-54ce-aca7-cacf544c67a2 | note | Flow - Specified: 130L/sec
c465f9f7-3ebc-597f-b6e5-080be6d5cc56 | textbox | Flow - Recorded:
450965bc-3e51-482a-a313-10df076ce112 | checklist | 561483-ITP-002.3 - DRAFT - Stoney Knowe Valve Pilot Valve installation - HOLD POINT | itp | 561483-ITP-002.3 - Pilot Valve - Delivery & Inatallation
28792a71-a32c-4aef-8130-acdb00c1c21c | section | SECTION 3 – RECEIVING INSPECTIONS
d4c2c12e-1c2e-4f88-95bb-d44d399ec056 | checkpoint | 3.1 - Take delivery of pilot valve assembly
b969c5eb-f84a-58b3-a0ab-17de55e74d70 | note | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
3de9ba34-7e55-5112-84bd-7520cc01ae4c | note | Acceptance Criteria - Matches Design Drawings/Documents
0ee13e74-38e5-54aa-918d-5ed081c45847 | note | Verifying Document - Drawings & Specifications. Advice from ClaVal
76a4ca26-9198-539b-9383-d8120403d3d4 | note | Frequency - Once
bf02e03a-4fcb-5d1c-9a95-e6cb509f87cd | note | Inspection Type (Visual, other) - Visual + electronic
c8b5bd9a-12d7-5eb0-906a-b141a805bcd6 | note | Inspection: Key - I
222ac60d-9fac-5689-8633-6b2af8976161 | note | Inspection: By - IP/PM
04722113-9324-4ea2-ab91-aff18fefd0b1 | checkpoint | 3.2 - Valve Assessment
ee719de5-5710-5acf-be45-dd23078f559b | note | Inspection Point: Quality Control Activity - Internal valve component inspection
d00a0911-cbca-5369-85ed-cc58c3caa23b | note | Acceptance Criteria - ClaVal Assessment
9298ad1a-0094-568d-a116-6f636d694979 | note | Verifying Document - Claval report and verification
327986a1-2780-5f70-ac05-33b5fbea567c | note | Frequency - Once
6bdcd7fd-1a13-5d1b-9a93-b654cd0f7dc4 | note | Inspection Type (Visual, other) - Visual + electronic
102cb497-91fc-543e-bc10-285d77a427e9 | note | Inspection: Key - H
73be1ae3-6a1e-5d3c-b306-fafa89411bbb | note | Inspection: By - IP/PM
9435e041-bb87-4326-b731-0f5814b46412 | signoff | HOLD POINT
48831c34-c12c-429e-b23e-5f12505674e5 | checkpoint-no-value | Note:
b5a3b9a1-33d9-5487-9f60-e38af55d5444 | note | Note: Valve chamber is Confined Space.
13d86b4f-3877-4b9d-9cb1-940eb1e303ef | section | SECTION 4 – IN-PROCESS INSPECTIONS
3b9f47f0-9846-4d01-8e01-402e0fd7e71c | checkpoint | 4.2 - Pilot Valve
56f10a81-42ad-5b92-892d-5cc7f81063e1 | note | Inspection Point: Quality Control Activity - Install new pilot valve and ancillary items
420c2fdb-b02b-5cc5-a9d3-569c33f7b775 | note | Acceptance Criteria - As per manufacturers installation instructions. ClaVal technician
2e822100-892e-53bf-8cc1-a36f4fc2cd27 | note | Verifying Document - ClaVal Technician sign off
c47ce127-a659-5e13-b27d-8868446d9ac9 | note | Frequency - once
fc392516-68a8-56e2-8987-5351b514f537 | note | Inspection Type (Visual, other) - Visual + Document + Photographs
82aaf47c-34a1-5a68-998a-0928716fe7e1 | note | Inspection: Key - I
bcc7dc62-c302-5650-b55b-224e5228fc26 | note | Inspection: By - IP
1fdcee8f-5fc4-47fc-a57b-6ebc1cc9b77f | checkpoint | 4.5 - System reinstatement
cfee7fd5-7283-52a3-aab0-a7fe16b8920d | note | Inspection Point: Quality Control Activity - Open main valve to reinstate water supply
e64fd4a0-086b-5a22-a74b-5c0bf7a3afc1 | note | Acceptance Criteria - Completion of item 4.2
872d7c30-06eb-5625-b396-84d662f4d443 | note | Verifying Document - Inspection and this ITP
49a1b4dc-57de-5278-8224-bc101102792c | note | Frequency - once
99ca5709-7d81-5570-97e7-5f0ffd707f4a | note | Inspection Type (Visual, other) - Visual + Inspection + Photographs
6e3f2a87-a43f-5ba5-bd70-4dddf7dedc6f | note | Inspection: Key - I
7bb39780-0e46-5904-9651-d1c607561ae7 | note | Inspection: By - IP
27eaa1fc-0c13-4967-aa70-e091fcb2c134 | checkpoint | 4.6 - Adjust
937aae61-d85e-597b-8333-81a1c3c3b5fc | note | Inspection Point: Quality Control Activity - Adjust the pilot valve to obtain the correct flow 8.5m Head & 70L/sec
98786324-2d81-5181-9d90-fbbbd3b0cc49 | note | Acceptance Criteria - Obtain specified flow rate ClaVal technician
668ea1a3-d16d-5a59-82c1-fc45e163f933 | note | Verifying Document - Specification flowrate
f207cebd-9ad8-5f70-ac88-96c8ce0a098d | note | Frequency - once
a9a36ca3-e629-5ed6-ba1f-9a427ae3dd20 | note | Inspection Type (Visual, other) - Visual + Document + Photographs
67477776-2d52-51c3-8071-b61c7ec9fbe3 | note | Inspection: Key - I
3d0462fc-cb53-5625-9571-60dd891de01b | note | Inspection: By - IP/CR
8f09947f-1001-4b48-9047-cc09a780aecd | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
f537d7fb-09e0-45ce-90ec-489ac474c5ae | checkpoint | 5.1 - Red pen Mark up
33381892-fa62-5f59-9330-64c53f5fc714 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP. Document upgrade and recored new flow rate & pilot valve position setting
a9acfa5f-00b5-5546-9334-2520ad60d63c | note | Acceptance Criteria - As per specified pressure & flow or client requirements
59f8de42-a60b-5f42-a167-6c11372e658b | note | Verifying Document - Red line mark up drawing. This ITP
d4af4d9b-9c56-523f-bde1-456cb26928bc | note | Frequency - once
7d659409-f41d-5cc7-b3b7-7579b21c419c | note | Inspection Type (Visual, other) - Visual + Document + Photograph
e4d09829-0258-5076-8fc8-70f62d359eb6 | note | Inspection: Key - I
5650f71a-34c0-56c5-82f8-d97cf6cbd931 | note | Inspection: By - IP
73faa5c2-4012-4afb-907a-9c649a4e558f | checkpoint-no-value | Head / Flow
301112ba-b60b-5549-acfc-fe3f10438781 | note | Head
ca11412a-4b86-5d8d-9b49-d164d0a60609 | note | Head - Specified: 8.5m
813fc29f-4c76-562a-a81a-1a8a2ad89a24 | textbox | Head - Recorded:
8a4aa354-077c-5f85-a1d6-8e9d9c58a0df | note | Flow
0946d323-66c4-5f0f-b801-907885622938 | note | Flow - Specified: 70L/sec
53a81906-de4a-50a0-a48f-66d871f55ea9 | textbox | Flow - Recorded:
ad7bf8f3-06a8-4a7a-b463-ce8ccd7f7472 | checklist | 561483-ITP-003 - DRAFT - Stoney Knowe Pipeline Flushing | itp | 561483-ITP-003 - Pipeline Flushing
49cb0c97-f526-4858-ac82-29000cc6db06 | section | SECTION 3 – RECEIVING INSPECTIONS
12bacd05-f037-4ab6-95a4-87ac259f7f35 | checkpoint | 3.1 - Adaptor to pipeline
ac6d7ada-731e-5401-be1a-f8726724f3ef | note | Inspection Point: Quality Control Activity - Manufacture adapter spool to connect Downer pumping equipment onto pipe
9460a8ef-d60f-5f76-aaa7-133e8fb1ce32 | note | Acceptance Criteria - All air valves installed and isolating valves on off position
9bab015a-b464-5a81-b3df-a16d0ad436ae | note | Verifying Document - None
7353a28d-4d05-5954-b79e-6d679701128f | note | Frequency - Once
265c60d6-94fb-5dae-bbce-4add1053e88c | note | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
175a0e47-ce8c-5717-8be8-10b35eb05daf | note | Inspection: Key - I
68dbd886-28a8-5ce8-b586-ef63330e77ba | note | Inspection: By - IP
d86b44a2-5b5c-452e-8d20-b87425b82e66 | checkpoint | 3.2 - Excavate to expose
37b5a7ce-6828-54fa-a06c-a6f37bd0f18a | note | Inspection Point: Quality Control Activity - Break existing flange and connect temporary spool
5eb5ee0b-d2b7-5846-be88-5d0d52053bfe | note | Acceptance Criteria - HS&E documentation. Traffic Management Plan. Shoring (if applicable). Ground disturbance.
9e0e26ea-8947-5d02-bd8d-7c63d3e8f228 | note | Verifying Document - Downer HS&E Documentation
a3d54162-b8c0-594e-95ae-d902b588ffb6 | note | Frequency - Once
2886164d-d66e-597c-96ab-c615c3a78c81 | note | Inspection Type (Visual, other) - Permit issuer
70981168-3dca-52b4-886f-69b22bc58d5d | note | Inspection: Key - I
1efbcadb-c39c-58ad-8ea6-d305270ae347 | note | Inspection: By - IP
10f81e02-ceed-4feb-ae5d-2db0a3b46862 | section | SECTION 4 – IN-PROCESS INSPECTIONS
5b40086d-1dd9-4ad7-a6cc-08e94e349a1e | checkpoint | 4.1 - Flushing
72b04f19-fd16-59d3-b240-e411e57ec110 | note | Inspection Point: Quality Control Activity - Flush pipeline to remove any loose material
d2c40264-3b03-5dfa-97af-f4c1a5ad2b9f | note | Acceptance Criteria - Flush line until water runs clean
99aebaab-c8e4-560a-8b60-a1f6bda78ce9 | note | Verifying Document - This ITP. Client Engineer witness.
f531c54a-0074-5c0b-8b5c-002a9dbb28e3 | note | Frequency - once
3b111de4-d942-5767-bd33-29a456555d27 | note | Inspection Type (Visual, other) - Visual - monitor any excess debris
24cc2d00-7424-53a0-bffb-6c1ed1207068 | note | Inspection: Key - A / E / I
7deeb495-c21b-51d1-a353-c1862d790030 | note | Inspection: By - SP / PM / CR
c57312ea-68c2-4491-8eb2-1d8091a99afa | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
dae62d1b-7dff-46e2-b4e1-4bfa2b1c5165 | checkpoint | 5.1 - Pipeline Flushed to Engineer approval
8b7b4e75-c4a0-57d7-af45-3d781e29f9a6 | note | Inspection Point: Quality Control Activity - Pipeline Flush - Pass
11cd0cde-2624-55e0-9bf1-dfcfefed6a74 | note | Acceptance Criteria - Engineer / Client Approval
b841dbbe-0ca6-5f64-8b5a-e6f5c83c9c64 | note | Verifying Document - This ITP
74fd5e08-7c13-5e09-b2c9-2f7ac49f7353 | note | Frequency - once
a1d5c176-e36f-5be2-888e-00428c0f9709 | note | Inspection Type (Visual, other) - Action/Visual/Issued document containing results/ Photograph
5eab1d7f-465e-5510-9315-4c460818138d | note | Inspection: Key - O
ee245520-87b6-520c-8bd5-668772204d1e | note | Inspection: By - IP / CR
94669eea-9724-4271-b668-3618d33887ee | checkpoint | Timestamped photographs of flushing & short video clip as evidence - Engineer to Approve
773c3ec1-74f4-4bf1-bda2-16daf311cdc2 | checkpoint | 5.2 - reinstatement
4e6b0860-e103-5af2-a152-9f4ac55c1494 | note | Inspection Point: Quality Control Activity - Disconnect Temporary Flushing Spool
03d57c2f-e1d5-502b-860c-a379ef3f85a9 | note | Acceptance Criteria - Flushing acceptance. Engineer / Client Approval
c0082bd0-4531-5558-b396-3ace1b575620 | note | Verifying Document - This ITP
fd894c81-d43c-5c47-bb6d-056f41c14792 | note | Frequency - once
b4ac9bed-1777-5a49-be8c-b08a0506d4e7 | note | Inspection Type (Visual, other) - Verbal / Visual
e0975be7-180e-5a0b-8ed5-9745b24aea15 | note | Inspection: Key - O
5e6518ad-ba11-5cb7-b87b-771d3c83c151 | note | Inspection: By - IP / CR
a50eaa1b-ae89-447c-a68c-f5c8a5585a12 | checklist | 561483-ITP-004 - DRAFT - Stoney Knowe pressure test - HOLD POINT | itp | 561483-ITP-004 - Pressure testing to re-commissioned water main
edc1b45f-0b78-45a2-971b-471958919a29 | section | SECTION 3 – RECEIVING INSPECTIONS
90696dd3-4303-408c-b2ac-5ac7679ad858 | checkpoint | 3.1 - System Primary Flush
fd0c8960-9b07-5ea7-a565-be02d4f2a0a4 | note | Inspection Point: Quality Control Activity - Completion of system flush
11d8414e-c542-5d51-adce-63310eb9d22d | note | Acceptance Criteria - Completion of ITP 3
6132eabe-ab38-510e-a3fc-f9a83feddf15 | note | Verifying Document - ITP3
f08fa868-71c7-5beb-882d-63987a83c32d | note | Frequency - once
e7fa3379-40c6-555e-a2b6-63e22d9e2081 | note | Inspection Type (Visual, other) - Visual + Photo + Document
866b232b-782f-5b59-88be-e3cb57d4aaec | note | Inspection: Key - I
b16682d8-34ba-556f-89ba-b4dff8c5fce5 | note | Inspection: By - IP
366133c9-2f08-49ab-a576-426903fd07c8 | checkpoint | 3.2 - System Pressure Pre -Test
16dd8a3f-b72b-5253-9ce4-f9adcb144786 | note | Inspection Point: Quality Control Activity - Ball valves to air vents are in the closed position
83757f4d-dda0-5834-a208-8f14c22f669d | note | Acceptance Criteria - 4.6.6 of Specification
fb54069c-6eb6-5bd6-a315-70854bf05985 | note | Verifying Document - Appendix E Specification
b2fedec9-025c-59b5-bfb5-6ba79e9f5c7c | note | Frequency - Once
4d1fee01-62da-520e-a39e-6a3610cfac26 | note | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
8ac6cd03-99d9-5bf2-8156-5ccaf27948b5 | note | Inspection: Key - I
e2a3415e-d3db-5a1f-8823-fcb162774eb9 | note | Inspection: By - IP / CR
60d400c8-b152-47d9-bfeb-cdb29a79c6c3 | checkpoint | 3.3 - System Pressure Test
d13b998a-800c-5e30-8fd0-d665a072c6d3 | note | Inspection Point: Quality Control Activity - Ball valves to air vents are in the closed position
9602d3cb-060b-56ee-a0f9-060481134871 | note | Acceptance Criteria - 4.6.6 of Specification
5ab68e59-1298-5100-a38b-61351c025418 | note | Verifying Document - Appendix E Specification
967f8d3f-8294-5bee-a654-2d4fc7be1f1e | note | Frequency - Once
29e1c551-cd39-51c5-a0c4-4a7f8eaa766b | note | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
a7e0209b-d8c8-54bd-863a-8eb10ccbeb48 | note | Inspection: Key - I
e97a1bb7-9dce-5f29-9c92-0313d0dfeb03 | note | Inspection: By - IP / CR
31e0865f-d9db-4839-9350-2ece77530fb9 | section | SECTION 4 – IN-PROCESS INSPECTIONS
d2bff430-1b41-44aa-89f4-56939ff480db | checkpoint | 4.1 - System Pre- test
ae95b24a-ab75-578d-a8f0-da29650810bd | note | Inspection Point: Quality Control Activity - Pre pressure test
bdce159a-3675-53ba-bfbb-2f946ddc43a1 | note | Acceptance Criteria - Pressure test - Pass.
f6b1e7cb-2463-53d6-8d02-725d9a252b5c | note | ○ Pressure test value be determined by Engineer.
8abb4f2f-a810-59f7-9235-fa6e461ccba5 | note | ○ Use method as outlined in specification section 4.6.6.1
2cdb9de3-d556-5c3b-91a9-68d705a87a99 | note | Verifying Document - Watermain Pressure test record - Attached
c311f08d-53d4-5c03-bb34-4229d2ca0030 | note | Frequency - once
4c98d707-1c46-51cc-9841-c9c98f279454 | note | Inspection Type (Visual, other) - Visual - monitor any pressure drop/time. Report any issues or concerns to Engineer
c66e3979-dd99-5288-b013-75d4b815953e | note | Inspection: Key - A
7743e571-0838-55db-9a71-d0de0cf4cb54 | note | Inspection: By - PS / CR
f429ee6c-39e2-49d8-98d4-4b404661569c | checkpoint | 4.2 - System Pressure Test
97d127ca-ecfc-5dd1-8730-cb900cfd5231 | note | Inspection Point: Quality Control Activity - Pressure test
3be87d26-1140-565e-bd5e-9703cbfd098f | note | Acceptance Criteria - Pressure test - Pass.
02352249-0228-56e1-b776-3bb7f61ea5f0 | note | ○ Pressure test value be determined by Engineer.
be5faff7-4f25-5ff7-b3bc-03d77857e169 | note | ○ Use method as outlined in specification section 4.6.6.1
3a29aaf4-c4e6-5e66-ad59-dc81c1cc1c14 | note | Verifying Document - Watermain Pressure test record - Attached
fae4e37d-829f-5006-a6c1-22c1ca3ce912 | note | Frequency - once
4a79792a-8c68-53f0-a917-6e1774c922a2 | note | Inspection Type (Visual, other) - Visual - monitor any pressure drop/time
a57ae079-f8a7-5189-ad1a-1ca22d185bb1 | note | Inspection: Key - A
37521e5f-81bd-5d6f-bdfc-37e5872ae121 | note | Inspection: By - PS / CR
76a67b2a-478e-4345-86d4-56d66f80a912 | checkpoint-no-value | Note:
42c5a31e-26dc-56d8-ba43-08a194c5906c | note | Client or Clients Representative to be present to witness pressure testing. Test pressure to be confirmed by the Engineer
abacc261-02e3-4b2a-a058-ed123ced8c98 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
60b3b40e-a07a-4d44-b93b-a1645934c1e9 | checkpoint | 5.1 - System Pressure Testing
fdfe0b0b-25de-592d-bb6d-bc80de8c8b85 | note | Inspection Point: Quality Control Activity - System Pressure Test - Pass
5ff0e8ee-d545-5e5c-bc5d-0b08b9246118 | note | Acceptance Criteria - Pressure drop is less than specified value
cabef224-1511-58a9-99fe-3500d49d9234 | note | Verifying Document - Watermain Pressure Test Record - Submitted
54a67d17-e990-5ce0-a720-fc783031bc10 | note | Frequency - once
d552e335-87e8-5b2f-824b-0743581ce9c6 | note | Inspection Type (Visual, other) - Action/Visual/Issued document containing results/ Photograph
03e1a6f6-7800-55f3-81f9-2b5e2f960647 | note | Inspection: Key - A
8e8e30a2-0529-555e-b8f7-bb81f63c2817 | note | Inspection: By - IP / QE / CR
009d11b6-ca19-4905-990d-2990accfce01 | checkpoint | Timestamped photographs of pressure gauge at critical stages to be submitted as evidence - Engineer to Approve
3eb7986c-d122-4e36-8501-300e02f3aff0 | checklist | 561483-ITP-005 - DRAFT - Pipeline disinfection - HOLD POINT | itp | 561483-ITP-005 - Re-Commissioned Water Main Disinfection
04064343-c697-48d5-9538-933d21bc41de | section | SECTION 3 – RECEIVING INSPECTIONS
f3e4e4a8-f8fe-4daa-9be2-d3bd7a2ea32d | checkpoint | 3.1 - System Pressure Test
0f0fcea0-7d4e-5478-8795-9af0a31faeb2 | note | Inspection Point: Quality Control Activity - Completed installation Check all unions & Fittings are tight and leak free
8a759a44-edda-5afd-b472-fee4b2b86c45 | note | Acceptance Criteria - 4.6.7 of Specification
bf43abce-d20c-5785-bc1f-0765f50023d8 | note | Verifying Document - Appendix E Specification
6e1c24a7-feca-5a01-a7da-7bcc62d08c6d | note | Frequency - Once - After Pre system commission checks have been observed
f1d4401c-5561-57a5-bbd4-0040e2133297 | note | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
9f212e66-913f-5a93-a86d-0976dbf0b4c0 | note | Inspection: Key - I
89f6d7a2-27db-589f-80cc-75fcbb671e61 | note | Inspection: By - IP
56e16960-71cd-490f-a0cc-2f8bf7136b3c | checkpoint | 3.2 - Drain pipeline of pressure test water
b3ef9db7-c957-5801-a7f2-c2ac1ad9f6cd | note | Inspection Point: Quality Control Activity - Upon completion of pressure test
fb8c7d91-17cf-51f0-972a-5a19d3eacbab | note | Acceptance Criteria - 4.6.7 of Specification
9e91dae4-618b-5c12-85f1-80bcd4190462 | note | Verifying Document - Appendix E Specification
5231759f-e4e2-5829-b744-89cb02143d71 | note | Frequency - Post Pressure testing
e362cef3-b653-5ed2-82b7-b2b3db25702a | note | Inspection Type (Visual, other) - Visual + Photograph
ee198ab8-b6ef-5132-9552-f1d67fa323da | note | Inspection: Key - I
1d9ee6bd-e6c9-512c-a6b7-a960a9384249 | note | Inspection: By - IP
ec4877ec-67a8-4207-bb52-f2daf07c08d5 | checkpoint | 3.3 - Arrange for client attendance/witness
5d9bd22d-0c50-583c-b9ab-6a179869dbe7 | note | Inspection Point: Quality Control Activity - During Disinfection process
e2280e4f-d11f-58ca-a90e-a9101f34067d | note | Acceptance Criteria - Client representative availability
84108e41-2b51-57b5-b56e-3d1bfc73bb35 | note | Verifying Document - DCC Approved Flushing & Disinfection of Water Mains - Document
822671db-54bc-59bb-9c41-3562665de267 | note | Frequency - Once - After completed checks
df55c826-de64-56ab-a503-c46d1a2bd4e6 | note | Inspection Type (Visual, other) - Attached Flushing & Disinfection Document
91db7fab-70d4-529a-ba1b-9422b78f5fcb | note | Inspection: Key - I
05bdc53f-2282-5a3a-b3df-f9a943cb7d53 | note | Inspection: By - IP
302b2404-cae9-47a7-90a7-56d8d1e065d2 | section | SECTION 4 – IN-PROCESS INSPECTIONS
dd842c7e-07b3-46cd-b45f-3cad50a59445 | checkpoint | 4.1 - Ensure all pipe fittings, valves & other connections are tight and leak free (as per pressure test)
c2bbb1cd-f87e-5bcb-8121-1bc06714f654 | note | Inspection Point: Quality Control Activity - At completiion of installation and prior to pressure testing
48b48abf-f1ee-593f-998e-15afbc0507f8 | note | Acceptance Criteria - Installation complete
c5d23895-eea4-5b8e-b2b3-e4898cda81bc | note | Verifying Document - Check list. Initial & Verification on the Schematic drawing
87c6e4b2-0da0-57e9-b4cd-16ad76c750d1 | note | Frequency - once
b43e7f40-a827-57e0-ad90-9ebb481a86cd | note | Inspection Type (Visual, other) - Visual - monitor any pressure drop/time
13b9d568-a70a-52f7-a9ad-0b2251a69f98 | note | Inspection: Key - A
abee4954-cf4c-5dd9-aeea-d4b1a494bdc8 | note | Inspection: By - IP / SP
16bb6a7d-9f70-4612-8337-42b0258e8e85 | checkpoint | 4.2 - Prepare to flush and disinfect new pipe, Fittings & pump
9588bb14-98e2-599b-a11a-e24ac2dc54a2 | note | Inspection Point: Quality Control Activity - Post pressure testing
de765cdf-4dc4-5225-b0bd-2860a8cfb7b5 | note | Acceptance Criteria - Pressure test - Pass
68dff7b2-b947-5f71-8cbe-2d78b76e30c3 | note | Verifying Document - Pressure test - Pass
e6e0b785-9cb8-5503-b0f4-0fab05557624 | note | ○ Flushing & Disinfection of Water Mains Document
93c76a98-fe96-5a0d-b575-e02a25f8dd5f | note | Frequency - once
ba4912b0-9259-5a70-829c-dcd4f217e07f | note | Inspection Type (Visual, other) - Closed loop circulation as installed by Bruce Allan
b62c0d54-67b8-502a-a6a1-5e60d9e63d04 | note | Inspection: Key - A
a668fc10-b65a-5258-8299-b3cbf1e74a1c | note | Inspection: By - IP / SP
dc19e10e-5045-4f4b-bfb5-c106af056ad1 | checkpoint | 4.3 - Calculate system volume to determine required chemical quantity.
c0b0156a-aa13-5238-84d7-041d7f45bf3b | note | Inspection Point: Quality Control Activity - Pre-disinfect process
ea8e43da-89f5-5646-bb24-5225044b74a6 | note | Acceptance Criteria - Watermeter or calculation
ad675cbf-b0d6-5b68-a125-9d91c1f48301 | note | Verifying Document - NZS4404:2010
87aba881-ffd0-55d2-8501-3f4da2cbd4d4 | note | Frequency - once
ab26b28f-ba3a-5af4-b725-da15a7424823 | note | Inspection Type (Visual, other) - Visual - Document volumes on client provided tdocumentation
9139bac0-3d2d-5554-a816-c58c875e5693 | note | Inspection: Key - A
71688500-82b1-53c0-ba4f-c1a67d2c9eaf | note | Inspection: By - IP / SP
9f8704cd-f0c3-44f1-bd0f-5d5f03664f93 | checkpoint | 4.4 - Undertake disinfection process
82143328-5e34-5266-a133-ba5ab4169c04 | note | Inspection Point: Quality Control Activity - Monitor circulation
e10bf091-abec-5f37-bdb7-ffcd1051cdfc | note | Acceptance Criteria - Monitor values (this may need done more than once due to age) to achieve acceptable level
62573dd3-f273-5a89-8b07-73020543cabf | note | Verifying Document - Client FLUSHING & DISINFECTION OF WATERMAIN DOCUMENT
44f3bbd7-6e31-5e33-89b9-e174e4f77768 | note | Frequency - once - or more as required
a1124022-ad08-5c31-a428-88e0ab160537 | note | Inspection Type (Visual, other) - Visual, Document and photograph
a582d003-37a5-5e45-8f51-d214c7662381 | note | Inspection: Key - A
c330b492-916a-507b-ab61-4d248ad6863a | note | Inspection: By - IP / SP
66dc2076-5f2a-47eb-9cf9-e951c3cc2c08 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
288d7215-6872-4c82-ba7a-5dea8273a936 | checkpoint | 5.1 - System Flush & Disinfect
f5dab8bb-4daf-5556-9d90-4a7267a79f28 | note | Inspection Point: Quality Control Activity - Upon successful pressure test
c9867933-5021-5c9d-b96f-4362e7904f0a | note | Acceptance Criteria - NZS4404:2010
ea38245b-8029-50af-a8a8-5619775a9f48 | note | Verifying Document - DCC Standard Flushing & Disinfection of Watermain document
419cbead-4fac-5ec2-99de-c20cb07e91d0 | note | Frequency - once
c992bae5-7840-51e5-b508-1f51b6bcf398 | note | Inspection Type (Visual, other) - Action/ Visual/ Time/ Photograph
a7336b39-7e9a-5559-9aae-b7df773cee47 | note | Inspection: Key - O
6e80c3ce-536d-5af3-875c-4d646996b7a6 | note | Inspection: By - QE / CR
effb413d-a877-419a-8ba5-780ba3ca0932 | checkpoint | Video footage of pump and disinfection process in action - Engineer to Approve
a725a18a-4132-45d4-b79f-11678e064d38 | checklist | 561483-ITP-007.1 - Pump 1 Isolation Valves Delivery & Installation | itp | 561483-ITP-007.1 - Installation of Pump 1 isolating valves - Inspection Test Plan
7240be40-8a0b-4fb2-b6d4-f70e3aa6e978 | section | SECTION 3 – RECEIVING INSPECTIONS
4287f4ec-90c1-468f-a45e-bbc779026240 | checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 1
9ab83190-2b4c-5d5d-99f8-007d21ab664c | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
96909bae-8d7a-5718-b358-48a94a6128e2 | note | Acceptance Criteria - Must be on the Approved Products list
b42bb903-3a72-57d8-8bd8-be4fd5cb6d34 | note | Verifying Document - Specification - Approved Materials list
24abc5c0-31a5-5262-bb34-6ca8d1dc03d6 | note | Frequency - Once
ed060350-266a-515a-a0c1-afef1d218f12 | note | Inspection Type (Visual, other) - Visual
664c125a-ba0a-5930-b0b5-cfe6d0394514 | note | Inspection: Key - C
3900062c-b628-5fdd-8a44-e95826d81fb1 | note | Inspection: By - IP
4df53388-7e7d-4b29-b05a-4e05aaee6c3a | checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 1
7cb2d7a1-298e-5fc5-804e-951321901c78 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
9d911c54-6b15-51a4-9f03-2df30457a090 | note | Acceptance Criteria - Must be on the Approved Products list
0ea9b710-7e67-5256-9117-5b3c273b1282 | note | Verifying Document - Specification - Approved Materials list
340ed704-20e7-5ca5-bbaf-53c7289b54ba | note | Frequency - Once
4b2ca555-d0c8-56c5-bf82-c7ed0b66bbb1 | note | Inspection Type (Visual, other) - Visual
040bcce1-b2c6-51b5-b60a-9f9b887aec78 | note | Inspection: Key - C
5eafdf78-6c0c-5b8e-aaf6-a62db37373f5 | note | Inspection: By - IP
48f644f3-54b1-463f-808f-721c9f3175db | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
93440355-411f-5b90-a3b0-12d7903ba537 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
cd810160-36f5-5835-b32f-7690afe978d3 | note | Acceptance Criteria - Upon approval from Client & Engineering team
cbf8b11c-97fe-50c0-87a2-abdc124d9c10 | note | Verifying Document - Written approval
7023e227-dc38-5503-b263-b11a979bc687 | note | Frequency - Once
ee8e679b-432d-50c1-a538-e8ab7f1dc895 | note | Inspection Type (Visual, other) - other
1d46fb3f-dccb-5091-8f67-fd273485c063 | note | Inspection: Key - R
b6bd46c3-daaf-5b3c-baf5-23e31f58b1b7 | note | Inspection: By - CR
c21bc7b9-bd00-49d4-b02d-6a38b26dfcaa | section | SECTION 4 – IN-PROCESS INSPECTIONS
4e9b3db8-4695-4fee-b90b-23dd0b5db02f | checkpoint | 4.1 - Shutdown the pumping system (all pumps)
3f7ce2ef-13c0-5834-861f-7a3ea9a33aa2 | note | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
9885c64a-855e-50b0-925c-3f5180f7cd57 | note | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
b076f65c-5b3a-5db2-b90c-e2d2271e04d0 | note | Verifying Document - Advice from DCC Operations
8efb2005-48e2-52c4-8951-5a7d4f483401 | note | Frequency - Once
333ac6e0-9ebb-5d45-ad7c-f5b26d3e71e7 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
24878586-2565-5940-bd64-3f3d31c315c2 | note | Inspection: Key - C
46f5db00-b4a8-5291-a834-04d2ee4c374b | note | Inspection: By - CR
5f19b6bb-ca51-4cd4-9fff-102167f95242 | checkpoint | 4.2 - Removal of suction side isolation valve to pump 1 (wafer type). Inspect pump flange and valve flange
6b08a4dc-f5ce-54f6-aa4a-4acee493d33a | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
e2ab32ca-fff2-525a-8db2-94f651aeb166 | note | Acceptance Criteria - Surfaces are clean
ceea978d-6d7f-5ee5-83c5-36271e31c012 | note | Verifying Document - Visual
9d271d8e-f479-5c5f-99fd-2d704150f4fe | note | Frequency - Once
6a831f1a-264f-5ec6-aa1d-4df749c60d50 | note | Inspection Type (Visual, other) - Visual + Document
045cee70-a768-55e6-bcd5-43c9af1a0eb7 | note | Inspection: Key - A
74a27094-a6c6-560f-b96b-1121380f0087 | note | Inspection: By - QE
5fd462ef-568d-4772-8e86-ffb2c274dd99 | checkpoint | 4.3 - Removal of discharge side isolation valve to pump 1 (wafer type). Inspect pump flange and valve flange
e1131cea-c069-572f-8a79-6dacfb5e4329 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
5eb9eee4-db83-5a4f-8576-49656eb79b6b | note | Acceptance Criteria - Surfaces are clean
8c2958dd-e6b3-5d9c-b237-92cceea3350b | note | Verifying Document - Visual
e643e66b-fa52-5bf8-b35c-e16f316c2010 | note | Frequency - Once
cd02faf4-9ef3-5871-bcb1-0962601e7326 | note | Inspection Type (Visual, other) - Visual + Document
958795d3-0bc3-5ca7-97ab-f90e8acb0d60 | note | Inspection: Key - A
95387fb0-9417-5e44-8a3f-0666da9a0db6 | note | Inspection: By - QE
5e6166d6-0da8-440c-aa3d-70bc25fa5912 | checkpoint | 4.4 - Suction side valve installation
04521bd8-fa32-5d25-a78d-d09e65e056d6 | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
68b851c5-8dd0-54e1-820d-1dc9ad9c137b | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
b97fc25c-a60d-55ab-aee0-6734008f4bab | note | Verifying Document - This ITP
855f42b5-e937-5f8c-b8a9-4025b6bfa9e0 | note | Frequency - Once
f9953c04-82f7-51b6-b15f-eba453d260f4 | note | Inspection Type (Visual, other) - Visual + Photograph
5f51cba4-3134-5d47-88e7-1737e084369a | note | Inspection: Key - I
aedf2363-8386-5bfd-8f52-1414c3cec717 | note | Inspection: By - IP
e1394320-37b5-415d-a828-29a8f49f4daf | checkpoint | 4.5 - Discharge side valve installation
5b05e16d-9cdb-54c5-9712-61907afdc5ce | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
e3a14752-0b2f-57f1-9aa7-75d7fd24ebc3 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
47cfa507-9029-567a-8636-4bada0fccca9 | note | Verifying Document - This ITP
a213ff68-4f85-5f86-bf7c-6304fc53e984 | note | Frequency - Once
487ce33b-84b9-5ada-833f-e397cfa7a3fa | note | Inspection Type (Visual, other) - Visual + Photograph
731be64b-5449-5e1d-bc42-00a6786ddfed | note | Inspection: Key - I
016fde07-4a00-5e06-b5f7-be0f56572897 | note | Inspection: By - IP
4907a575-e30a-4ace-bea9-991bbe6fda1e | checkpoint-no-value | Note:
973d7ce1-bd13-54cb-b9e0-7041f7128792 | note | All valves to be left in closed position
b4264cf1-ded1-4c9f-9ee6-3ba674c7135e | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
739f61ff-1a5b-4775-adf7-56492492e8fa | checkpoint | 5.1 - Returning existing pump 1 for duty
12b71e7c-55df-5219-80c9-922dacc41472 | note | Inspection Point: Quality Control Activity - Purge pump 1 of any entrained air
caae31ce-2ae0-56c9-9457-f152a7465cab | note | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
c374efc9-d33e-50aa-b1c1-d79582fff662 | note | Verifying Document - Visual
2c10cf2e-a6f0-5536-8e64-573876eb3c88 | note | Frequency - once
bc9b7185-bec1-5460-8512-dad487db6570 | note | Inspection Type (Visual, other) - Visual + Document
42842aa3-a17e-5868-8f7d-50835178adc0 | note | Inspection: Key - I
b441dd56-7150-5cc3-9ffb-9a6f70085590 | note | Inspection: By - IP
5dc39c5b-d6ab-405c-8f28-b0be5f0ebf19 | checkpoint | 5.2 - Power reinstatement to pump 1
18586112-8576-5b07-9e60-236a33469ff6 | note | Inspection Point: Quality Control Activity - Remove lock out tag pump 1
80b54854-835c-5c11-8d54-b94a9a979755 | note | Acceptance Criteria - Completion of 5.1 above
9c712809-ca64-540e-98b9-9e9adc1a3fba | note | Verifying Document - This ITP
3254e160-f89a-5327-af1a-0b31b149217a | note | Frequency - once
50c8be6a-40c4-5aaf-aaaf-999c27f09bc3 | note | Inspection Type (Visual, other) - Visual + Document
74c07ac7-768d-5028-9c75-9ccdc9b3e978 | note | Inspection: Key - I
e890c284-2e59-5a54-aed5-371c33a304c6 | note | Inspection: By - IP
dd0200b9-4f70-4081-bd0f-f86b043230a0 | checklist | 561483-ITP-007.2 - Pump 2 Isolation Valves Delivery & Installation | itp | 561483-ITP-007.2 - Installation of Pump 2 isolating valves - Inspection Test Plan
d308f0f1-24df-4091-87f4-9bb175de651e | section | SECTION 3 – RECEIVING INSPECTIONS
10c930ee-7503-4ff2-9e36-fd733a8c01b7 | checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 2
13b3e304-b8c3-5242-91f6-920adc5fc556 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
9b9236b8-e033-5707-ada3-451db4369819 | note | Acceptance Criteria - Must be on the Approved Products list
fdb218ea-e092-5038-81a9-5020112f446d | note | Verifying Document - Specification - Approved Materials list
3038f229-1ff7-5294-8241-0c3a5c225992 | note | Frequency - Once
5692bf63-0c24-59a4-87e6-1d0eaade60f5 | note | Inspection Type (Visual, other) - Visual
fb7a5aa0-f6b0-50ea-bffb-1c2a02102ded | note | Inspection: Key - C
bd8112b8-3fa6-5195-a9d6-96b78f5e4294 | note | Inspection: By - IP
632b590e-63c8-431e-a96f-7a7ffaa88b67 | checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 2
06f7c1cb-7309-5aa9-8a7e-a4b7e3f2c412 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
9a058f39-473c-57fa-be66-90812c9b010c | note | Acceptance Criteria - Must be on the Approved Products list
842bd88f-5b51-5b4c-8e31-694438e395fb | note | Verifying Document - Specification - Approved Materials list
6a006bf8-e0f5-556d-9855-6022afc2c575 | note | Frequency - Once
e58ba47a-c7d4-5cc8-9fb6-01187da86952 | note | Inspection Type (Visual, other) - Visual
f93d657a-b89a-5b1b-98ee-926be3f75106 | note | Inspection: Key - C
8570fb84-43ce-5c51-9df0-bbaaaf439ddb | note | Inspection: By - IP
f93d94d1-ce1d-45a4-8572-84ffe31d411f | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
a11a2767-8527-51eb-90d0-0f300217dd53 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
3de2c7be-4aeb-5e49-a41a-d0c7edf715d6 | note | Acceptance Criteria - Upon approval from Client & Engineering team
3e2ff67a-f027-5ee0-9b26-b9be93995e41 | note | Verifying Document - Written approval
521d1e5e-0c76-56a6-ac36-40599cdeb0f9 | note | Frequency - Once
dbf93169-9354-5f7b-a56d-f8117fc840a1 | note | Inspection Type (Visual, other) - other
c188940e-b5ac-53a5-9e13-c8a98d5658b0 | note | Inspection: Key - R
4d7fc016-ba41-5b03-8e82-517285d9672b | note | Inspection: By - CR
36e7f2e3-24b4-4796-aed2-d14db72b101d | section | SECTION 4 – IN-PROCESS INSPECTIONS
de834767-0316-4281-9d75-8155c9a41002 | checkpoint | 4.1 - Shutdown the pumping system (all pumps)
62d30aa5-9e01-54cf-8544-800646cbef1c | note | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
d8160516-c270-524c-9f3c-8438bc210f61 | note | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
066d2a9c-98b3-5c7a-9cbf-cd6af5775eea | note | Verifying Document - Advice from DCC Operations
81ac5c1a-b609-55bb-9dde-dfd23008a3b9 | note | Frequency - Once
6f4f17e6-1d23-5031-860b-90dde0e5756f | note | Inspection Type (Visual, other) - Visual + Written + Verbal
1ea74681-af06-5f14-9e26-f606b511e7a3 | note | Inspection: Key - C
9f178950-edc4-5968-a4b6-5091970a45e6 | note | Inspection: By - CR
059ebfdd-a239-4677-be48-fad0d5610ad3 | checkpoint | 4.2 - Removal of suction side isolation valve to pump 2 (wafer type). Inspect pump flange and valve flange
a14f28b1-5ea0-5ce1-93ce-487e2ad6ca7a | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
ee2bb876-9356-5133-b40d-701f4ddd52d2 | note | Acceptance Criteria - Surfaces are clean
f8e15775-1732-5ef4-9595-1394f4d09d9c | note | Verifying Document - Visual
86b72935-6a12-5980-98c5-b6bc2704b5e4 | note | Frequency - Once
6f375ddf-7b92-5ce7-9f49-a52931c0435d | note | Inspection Type (Visual, other) - Visual + Document
f3105129-7820-534d-8ffa-a27168748008 | note | Inspection: Key - A
c03269b7-89f7-5c7a-96cd-c5849ddfb1f3 | note | Inspection: By - QE
a0a05efb-1778-4d05-98eb-7c3053d5a603 | checkpoint | 4.3 - Removal of discharge side isolation valve to pump 2 (wafer type). Inspect pump flange and valve flange
8b001796-124d-5ce2-b8bd-49a7e97b2fce | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
5171d022-5be3-5a39-848e-8bb379a74729 | note | Acceptance Criteria - Surfaces are clean
b6dfb755-5a1f-5cfb-8fd5-b92e705f39b9 | note | Verifying Document - Visual
72d067c3-3cf8-5462-8e18-070cde9111d6 | note | Frequency - Once
5a16bf5f-a5f5-5f57-bb20-9aba8fe41e94 | note | Inspection Type (Visual, other) - Visual + Document
d9fd0aaf-117f-580e-862e-1739544b3b26 | note | Inspection: Key - A
6da19413-1a3a-54e1-8329-dfd6e8dcb260 | note | Inspection: By - QE
5442ad1f-3aaf-4838-9cf0-c63a373e1680 | checkpoint | 4.4 - Suction side valve installation
b991fab3-8e79-561b-8121-a1d552abc411 | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
b0628067-0c1d-5afa-bdcc-defef038b9e3 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
6538218e-375b-5af1-a1c5-4e170fd220d4 | note | Verifying Document - This ITP
56575d9e-14dc-5de5-9265-17ca44b70fbb | note | Frequency - Once
a413acb5-c980-54dc-91e5-25f27f7d7b80 | note | Inspection Type (Visual, other) - Visual + Photograph
be4c726a-f3c7-5043-bc28-8bbb98f5c4fd | note | Inspection: Key - I
d8674ebe-c190-538b-9afe-945148b20e28 | note | Inspection: By - IP
16b3197e-92b2-4c8e-850c-4e2200dd2891 | checkpoint | 4.5 - Discharge side valve installation
65e66453-63ba-57d0-a094-704bd33405b2 | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
bf8be1df-e178-5566-a9fb-b152cc3b50f3 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
7fcc3328-60ad-5a32-b40c-cc6402ad0825 | note | Verifying Document - This ITP
3555debd-6370-509b-ac47-d22534f9be59 | note | Frequency - Once
f7ee203d-49f7-5633-a0cb-f88d24af5c5b | note | Inspection Type (Visual, other) - Visual + Photograph
155e1481-09bf-51b7-982b-bf01c056f8e9 | note | Inspection: Key - I
d65a58d4-e6ed-52e1-8551-366097ec27d8 | note | Inspection: By - IP
7c6279ee-adad-4cfa-89fa-ae4e6743d40d | checkpoint-no-value | Note:
dcad5b5b-5ac2-5e0a-8aa1-249bec9295c5 | note | All valves to be left in closed position
d13054d4-d87c-40a1-b093-8c7a11ce1496 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
bb9113b4-8a3c-4a02-8976-1fbba017ad96 | checkpoint | 5.1 - Returning existing pump 2 for duty
86a91d00-e0d1-5331-9de1-a3d42a3ba60c | note | Inspection Point: Quality Control Activity - Purge pump 2 of any entrained air
26c8554b-6947-5e70-ab74-e067fc9348c0 | note | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
4c174537-fbfd-5bf4-ad35-d1b92cedeae2 | note | Verifying Document - Visual
e6be96d6-3d01-5993-b4ca-f6971aadecd9 | note | Frequency - once
32c5231b-5f62-548c-9c0d-eb324d64f76b | note | Inspection Type (Visual, other) - Visual + Document
13100e12-d489-54ec-80b0-f1f18cf00d5e | note | Inspection: Key - I
8b93ea10-a594-534f-a4b0-1a467011c6da | note | Inspection: By - IP
4bfc2507-0bc8-4187-9261-949ad2040e44 | checkpoint | 5.2 - Power reinstatement to pump 2
9904263f-d9f7-5fef-a241-bd852631c0e4 | note | Inspection Point: Quality Control Activity - Remove lock out tag pump 2
c82d661b-fd9e-595b-8730-7849521a139b | note | Acceptance Criteria - Completion of 5.1 above
0157b64c-9ad7-5e68-8d09-e5035544657b | note | Verifying Document - This ITP
e6331f8b-27d2-59e9-b74f-46382fce72fa | note | Frequency - once
c87a0852-5d7a-535b-8c66-7c5c5f6522e7 | note | Inspection Type (Visual, other) - Visual + Document
1ed0f52e-5b9c-5c66-b3d1-10ea728cf157 | note | Inspection: Key - I
2507b40f-3f26-5658-93af-c88cbdd11de4 | note | Inspection: By - IP
7cc4d55a-5d75-491b-82af-b73184f053c6 | checklist | 561483-ITP-007.3 - Pump 3 Isolation Valves Delivery & Installation | itp | 561483-ITP-007.4 - Installation of Pump 3 isolating valves - Inspection Test Plan
fc15476b-6a60-49a3-910e-36ec548540b2 | section | SECTION 3 – RECEIVING INSPECTIONS
5cd1a71f-8761-4065-b3e4-763230a31c73 | checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 3
c2a763c0-3bcb-5567-95bd-1f8d1697399e | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
5fa41931-2ed4-536d-8ea1-4773ad093cbf | note | Acceptance Criteria - Must be on the Approved Products list
4045e317-685a-5a35-8768-d3836c9fb030 | note | Verifying Document - Specification - Approved Materials list
bdb0a9aa-67b7-516a-9493-ef1f8c683c27 | note | Frequency - Once
f659dc10-8eec-5595-815e-85e26c599df1 | note | Inspection Type (Visual, other) - Visual
e5c78bbc-af95-555d-895f-348b883a1eeb | note | Inspection: Key - C
4ca2af3b-2fb7-57a8-9a8b-3254627ec330 | note | Inspection: By - IP
b46a35d2-6ac4-4591-8e92-c6a2e8b3b072 | checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 3
a1cc5892-57ab-5539-a5b5-ef0bc35e9afa | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
c604cd47-0de6-5a78-b8fe-d7e2b7388924 | note | Acceptance Criteria - Must be on the Approved Products list
3bb8d8c9-4240-5b3d-bdb8-9039aad8d1db | note | Verifying Document - Specification - Approved Materials list
937e84ec-2332-59b2-a702-83e23f632c48 | note | Frequency - Once
7589abb5-a0df-5d33-a132-b7310bdad547 | note | Inspection Type (Visual, other) - Visual
7fbed0fd-0c17-5498-9536-301946b7d68d | note | Inspection: Key - C
9c633336-7aa8-5ecc-afa4-33170d0d35db | note | Inspection: By - IP
5d962e7b-211c-46e6-8cdf-05638cd079d9 | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
57e8bacb-9870-585c-92a5-4b410e0d0d56 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
8ec411e6-1b1a-5ea0-b1da-1a0f736084bb | note | Acceptance Criteria - Upon approval from Client & Engineering team
a8536d08-3d0f-5096-a21a-a87f658a5434 | note | Verifying Document - Written approval
5e479fb0-5e94-586a-9ef1-8ac591b7174b | note | Frequency - Once
e271aa36-b7ec-563f-9a25-50583861609f | note | Inspection Type (Visual, other) - other
09005c26-4f82-5254-9263-320b5cfadd38 | note | Inspection: Key - R
ab6b673e-b517-547d-ab75-ffd00f86ff4d | note | Inspection: By - CR
da64b150-c169-41e3-995f-c3ce3e9e3042 | section | SECTION 4 – IN-PROCESS INSPECTIONS
c8cf94ff-ff87-4223-9ac1-d8bf3ace5c1e | checkpoint | 4.1 - Shutdown the pumping system (all pumps)
de4267a7-cd40-5973-acd2-390ee7349508 | note | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
835c4ddf-1f30-5349-a57e-79cabdf10789 | note | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
0e735415-b1be-5370-b0c0-67340d3c646b | note | Verifying Document - Advice from DCC Operations
a821ac0f-354a-5857-9c36-e4e523f922ee | note | Frequency - Once
519a0201-09f3-53ff-86ee-3033474207c5 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
392f4178-3bd7-57b6-b3b9-9bbdc259cfe5 | note | Inspection: Key - C
cdf1ffe6-ee02-58f3-8920-6bfec7fb63b4 | note | Inspection: By - CR
d2458f77-3531-4901-857d-d8c0d8be7168 | checkpoint | 4.2 - Removal of suction side isolation valve to pump 3 (wafer type). Inspect pump flange and valve flange
cf2cf843-8cfd-51b1-aadc-4b8ad1ccac74 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
0cbb1ef6-a066-5ba2-b266-12466ab4e76c | note | Acceptance Criteria - Surfaces are clean
f342b0c7-e1cc-5d20-8870-fbe6b1a934ce | note | Verifying Document - Visual
a2904b82-8567-593d-8ff6-4da04df3f781 | note | Frequency - Once
28428061-d95b-5df3-9e0d-c1b32c2cabe7 | note | Inspection Type (Visual, other) - Visual + Document
f3c07fb5-78bb-5fef-b466-e46ce3140d1a | note | Inspection: Key - A
0661cc67-69c4-5714-9c15-277677f17676 | note | Inspection: By - QE
7db0cefa-aa1a-4280-84dd-60055966f232 | checkpoint | 4.3 - Removal of discharge side isolation valve to pump 3 (wafer type). Inspect pump flange and valve flange
421e60fd-32cd-520d-bdc4-e6f909add2e3 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
32195782-25f3-5b8a-ac07-58061df2ecf5 | note | Acceptance Criteria - Surfaces are clean
0194da17-ab05-5d51-b4c4-655b9709907e | note | Verifying Document - Visual
e276f2ef-af65-57fd-b00f-e47f3583270d | note | Frequency - Once
65aaef8a-6cdb-5d57-a2b2-b9aeea362170 | note | Inspection Type (Visual, other) - Visual + Document
6a7ab054-5f04-5a12-b025-620286919438 | note | Inspection: Key - A
dd2fdef7-b6b2-5a71-b93d-b57d01f0973a | note | Inspection: By - QE
063bba4a-5675-48de-bbe9-1a0dbcc0da0c | checkpoint | 4.4 - Suction side valve installation
2e645923-0391-546d-b72e-f5762dba87ce | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
caba25ba-f3eb-5279-926b-6e94b2601d6f | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
5ee6289c-5106-5522-9c00-a1427c6fad70 | note | Verifying Document - This ITP
3d25661f-3b49-5659-9b87-8ec480044931 | note | Frequency - Once
5d1e95e3-c0e9-5557-9672-49dfac23ca0d | note | Inspection Type (Visual, other) - Visual + Photograph
eb4d1ea9-7596-539d-8e03-a6c7b19ce197 | note | Inspection: Key - I
9a54b13c-21ba-5a69-8381-615906e2e5e8 | note | Inspection: By - IP
0018efd3-5d1d-4eec-a5eb-d510d2b124d9 | checkpoint | 4.5 - Discharge side valve installation
3e73dd6f-facc-5652-a0c0-06d91599c23a | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
0346c7cd-3178-50bf-b1da-902bcc7593a9 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
f0763492-ab91-5a41-96a9-e6d9dad534c8 | note | Verifying Document - This ITP
973cec15-c4c0-5eec-9fbf-9cfa95df7ad6 | note | Frequency - Once
ad9c7cc8-47f1-5a65-b5c8-3a85eeda9e63 | note | Inspection Type (Visual, other) - Visual + Photograph
d2cc3807-bff1-5189-a0a0-f6b03ee49631 | note | Inspection: Key - I
607b29a8-60dc-5885-9514-35163c54de9d | note | Inspection: By - IP
315e6ac4-edc5-4473-bd1c-32d7776300a9 | checkpoint-no-value | Note:
f3b59762-ff3b-5ece-9621-cfdaf598e17f | note | All valves to be left in closed position
c5178992-e407-4974-9171-e33128799520 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
51df1423-d5e8-4c66-b11f-961222f4b9aa | checkpoint | 5.1 - Returning existing pump 3 for duty
bb96e04d-467a-55ed-ab4b-902b4d43f30c | note | Inspection Point: Quality Control Activity - Purge pump 3 of any entrained air
d7191a69-8c4f-5634-80cf-1e63a052f572 | note | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
66585a8c-3ac8-5bd9-8e8b-fe8616833d96 | note | Verifying Document - Visual
aa760710-fefe-5f94-9555-f5c66b8ac7fc | note | Frequency - once
082ea7a5-b1c6-5f25-96d0-de43454e663d | note | Inspection Type (Visual, other) - Visual + Document
cb0d27f2-ded1-54b1-b917-b9e46f0d7984 | note | Inspection: Key - I
eb733b4d-b73b-50be-be11-137a7e9b766b | note | Inspection: By - IP
a376c839-463d-4675-8aec-83cff30a9ad7 | checkpoint | 5.2 - Power reinstatement to pump 3
a7a4695e-7bb2-56e5-b5bc-da20155b60ae | note | Inspection Point: Quality Control Activity - Remove lock out tag pump 3
dbc90990-b24e-5565-82da-516ce9773173 | note | Acceptance Criteria - Completion of 5.1 above
95ebfe52-ed93-5c70-ab42-b22cd635fb8d | note | Verifying Document - This ITP
705b5f7f-6552-5713-a6e2-3bb4ca09e4d9 | note | Frequency - once
56a3f76a-8f01-58e3-b5a5-848b59c4b052 | note | Inspection Type (Visual, other) - Visual + Document
16541de8-aab2-567f-be87-161e2aa7051b | note | Inspection: Key - I
65a495ba-d9ff-59e8-a96f-cabc202c775f | note | Inspection: By - IP
53ae3811-1715-4ae2-a0b4-136c90956919 | checklist | 561483-ITP-007.4 - Pump 4 Isolation Valves Delivery & Installation | itp | 561483-ITP-007.4 - Installation of Pump 4 isolating valves - Inspection Test Plan
ad56c593-1b09-4c22-a49d-d1eb790abd8f | section | SECTION 3 – RECEIVING INSPECTIONS
6fec4778-9adf-44e8-b5dc-dd122e58cb79 | checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 4
04050b69-c6dc-5b01-b376-3ea077310d3a | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
6300fa47-6f9d-5422-a568-07092266d4eb | note | Acceptance Criteria - Must be on the Approved Products list
5dbd1823-4e74-5566-a7ea-b14c520f461b | note | Verifying Document - Specification - Approved Materials list
154e02c4-506b-526b-9226-e4d6371a4614 | note | Frequency - Once
57418fb2-cbbb-5f84-910b-60810f66bc6f | note | Inspection Type (Visual, other) - Visual
8cfa9e49-1b24-5e74-8bda-5be4c8c63486 | note | Inspection: Key - C
5abc989b-7192-5664-b2fc-f79138a3f4b0 | note | Inspection: By - IP
f270929f-dc96-4ea9-82de-822e97e11997 | checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 4
db9da2e6-311d-5e6d-90db-509c38f4dcb5 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
184fa0e3-7715-510d-93ab-10904ff92424 | note | Acceptance Criteria - Must be on the Approved Products list
85336bcd-3e05-5f7c-a6f0-aca426c73275 | note | Verifying Document - Specification - Approved Materials list
e0b1391a-9386-5da0-b314-4fc3ba97b7da | note | Frequency - Once
60373b3c-93c1-533b-b103-99d6f7376f21 | note | Inspection Type (Visual, other) - Visual
0b9a67d3-3d0b-5e64-b114-76c749c5a549 | note | Inspection: Key - C
5791ed0d-2ed3-5889-9442-c43d6c254699 | note | Inspection: By - IP
c3893e25-5e1d-40c1-a0f3-a461095e1a9d | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
d56320da-329d-5349-b2f3-63bb9151565f | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
8535932a-ba40-51b4-aa5c-f3aff7027d24 | note | Acceptance Criteria - Upon approval from Client & Engineering team
9b79c7fe-0b0b-5c74-956d-2742db475ae9 | note | Verifying Document - Written approval
20f5dbbb-6196-5a6d-b1c2-a546a886588a | note | Frequency - Once
dd06e6a2-67d0-5d4d-91ac-8ddbffb1246f | note | Inspection Type (Visual, other) - other
184a6541-40b3-52ee-9618-8e00b51283f7 | note | Inspection: Key - R
a59623f2-96b4-51cb-99f3-4cb8bbf610d0 | note | Inspection: By - CR
42e32fb4-781f-4770-a94e-95a1e27653b9 | section | SECTION 4 – IN-PROCESS INSPECTIONS
58159c57-6e96-4ea0-a175-024e058bfae2 | checkpoint | 4.1 - Shutdown the pumping system (all pumps)
97b7a496-67b5-528e-8930-92f40aa29ee3 | note | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
aa932abc-4427-5e4b-8e5e-6f33d1e96b5d | note | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
f2168552-c2db-5800-8a94-c8528e2e0d15 | note | Verifying Document - Advice from DCC Operations
15b6bcff-b6b6-5e89-9d32-baa536008048 | note | Frequency - Once
ed762ef9-f414-5019-9582-031823061794 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
32f6f252-3fed-54e9-aaab-1c4e8f24ba38 | note | Inspection: Key - C
693f7a23-75b1-5bbb-ad53-a875cefa48ab | note | Inspection: By - CR
4d377edc-c3c6-41a4-a69f-083f849bbb18 | checkpoint | 4.2 - Removal of suction side isolation valve to pump 4 (wafer type). Inspect pump flange and valve flange
c383d4a7-3c07-55a2-bd5a-91b667f8ffa9 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
afe221a4-91a3-5a68-a9c8-1ca78dacca3d | note | Acceptance Criteria - Surfaces are clean
d53b1301-d3e6-5a47-9122-84a8122e74bb | note | Verifying Document - Visual
2463fb92-aeda-5028-ab55-8a8b2e3a56c3 | note | Frequency - Once
4417da7b-091c-505a-83cf-c203c48af3de | note | Inspection Type (Visual, other) - Visual + Document
8fb0c008-9149-5536-88a9-143911adde74 | note | Inspection: Key - A
c9ff231d-6d64-5dd5-a676-ccf940a7d219 | note | Inspection: By - QE
94930da9-6363-4ed3-95f8-3c9f0894f6d1 | checkpoint | 4.3 - Removal of discharge side isolation valve to pump 4 (wafer type). Inspect pump flange and valve flange
ee34b6ed-e802-5593-8436-2bf43d2e9b5a | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
637831a9-db80-550a-8b06-976e930aed9e | note | Acceptance Criteria - Surfaces are clean
69ee0207-3b6b-5d68-b0c2-84ad7ce1878f | note | Verifying Document - Visual
f5064af1-2b17-52d5-b279-afc361119eaf | note | Frequency - Once
4507bcd4-d698-5873-88a5-8e0e60e56d48 | note | Inspection Type (Visual, other) - Visual + Document
814c96d9-55e9-5f9e-bb39-de968eab9226 | note | Inspection: Key - A
29740774-1245-56b6-9b96-64b52d08c28e | note | Inspection: By - QE
71053b8c-05d7-4269-ab97-944e919c88a8 | checkpoint | 4.4 - Suction side valve installation
21cc7bcf-5c85-545a-ba79-e5fb1d42328e | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
ca8ea24f-e02f-5626-9b96-4886db0ce519 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
a8bc6c89-1e61-59a3-ab83-eb3616be218f | note | Verifying Document - This ITP
de1372d4-a622-586f-a427-ea23f845ab3c | note | Frequency - Once
f711984f-ebcf-5a63-bfd2-5089dc0e20c1 | note | Inspection Type (Visual, other) - Visual + Photograph
4f35eb1c-2f05-516c-ad73-31697bc1e182 | note | Inspection: Key - I
7cf557e0-a48f-5dd2-bfed-7ddfd9a778e2 | note | Inspection: By - IP
b2345d55-2c97-485c-9c04-b74eced69c9d | checkpoint | 4.5 - Discharge side valve installation
83d9a831-9c2b-56aa-8da9-4c5a77b74272 | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
cf3eab24-158b-5bd5-ab34-baf7967796bb | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
508f5a60-ff36-5593-a9ce-86200c9aa7ac | note | Verifying Document - This ITP
e2cb585a-23de-5382-a9d9-ea86f041923f | note | Frequency - Once
78de70a9-6504-5d39-a38b-b1275737a0e5 | note | Inspection Type (Visual, other) - Visual + Photograph
80242719-a942-596b-ac71-655b6c111f84 | note | Inspection: Key - I
0ed7ab6c-e4ae-5f76-8160-5641798958c6 | note | Inspection: By - IP
dcb26779-2799-44dd-a4d3-ebe3c52e225b | checkpoint-no-value | Note:
330d3ecc-ec29-588e-b26b-fba8264f6ba9 | note | All valves to be left in closed position
d5a53e6c-e2d4-41e2-a00f-37803c9ee9ab | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
204ac309-213c-4945-a764-f97884d8b853 | checkpoint | 5.1 - Returning existing pump 4 for duty
7228afc0-a883-57fd-8ceb-95214ca5a4e0 | note | Inspection Point: Quality Control Activity - Purge pump 4 of any entrained air
0384484b-2235-59ae-89e5-99d52076f199 | note | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
07df838b-d234-553c-88be-ccfe6ee1f282 | note | Verifying Document - Visual
0a25be7e-fffc-589c-8f1c-240da0a05b9b | note | Frequency - once
3c6db1c8-89cb-5e48-bf51-c365e6adab26 | note | Inspection Type (Visual, other) - Visual + Document
2e30bcfc-a2dc-5395-a01f-1283fe9992d9 | note | Inspection: Key - I
80da3f66-655a-52ac-9c89-1c48650dd591 | note | Inspection: By - IP
9f8187c0-be2e-492a-bae7-6b2805af2932 | checkpoint | 5.2 - Power reinstatement to pump 4
8b821183-9056-5f48-bb8b-18532549b1b6 | note | Inspection Point: Quality Control Activity - Remove lock out tag pump 4
9a201bde-cebb-59da-8200-fc6b62a7d721 | note | Acceptance Criteria - Completion of 5.1 above
291dc1df-b7f4-5c3e-ae75-5557a2e7f13a | note | Verifying Document - This ITP
f79409f0-ed11-57ab-b862-5b71325857ec | note | Frequency - once
7afebc63-9f2b-5585-98a7-d32b79a4c650 | note | Inspection Type (Visual, other) - Visual + Document
2b05417c-638c-557b-9e1c-cd7595799e0b | note | Inspection: Key - I
effb871f-b0c2-5596-b1a1-543763b83b26 | note | Inspection: By - IP
8d9b6896-3294-4fb4-9449-7e180f0e21f3 | checklist | 561483-ITP-007.5 - Pump 5 Isolation Valves Delivery & Installation | itp | 561483-ITP-007.5 - Installation of Pump 5 isolating valves - Inspection Test Plan
d5cd41d2-4764-4538-b977-f943ab007e3d | section | SECTION 3 – RECEIVING INSPECTIONS
95257f7b-eba6-4450-9a36-252005964ca3 | checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 5
faa09a19-ecee-5785-8d18-a0cf8374e506 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
6edee207-9d4a-537b-b2a7-83270dcbc88c | note | Acceptance Criteria - Must be on the Approved Products list
34a31755-f554-5aee-8310-d44d1312f8d6 | note | Verifying Document - Specification - Approved Materials list
cb000a32-4559-5b46-80e4-6a8bd4738761 | note | Frequency - Once
caada997-39a6-5085-a31a-b6875d05e00f | note | Inspection Type (Visual, other) - Visual
1c6bb5a6-a105-522a-82d9-306c23280ae1 | note | Inspection: Key - C
726ad9bf-c864-5db3-82a3-b63917dc01a0 | note | Inspection: By - IP
3bba793b-6920-4333-a6a9-fd9722d56d82 | checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 5
46de5574-cbff-52d4-b02a-d16b2016b574 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
c5c73f6e-f4a2-5dff-93d8-f194081533e1 | note | Acceptance Criteria - Must be on the Approved Products list
78f0ee4a-ee3d-5ed2-a2e4-13d1117059cd | note | Verifying Document - Specification - Approved Materials list
05570bd2-8152-532d-9db0-6763fdc946b0 | note | Frequency - Once
9f40cbdf-9b54-5407-b6e7-85ac7cd06e55 | note | Inspection Type (Visual, other) - Visual
dc63e2c5-c716-5437-9900-0ed5455de0e9 | note | Inspection: Key - C
9df2e791-8595-538d-8f4e-555145461fc6 | note | Inspection: By - IP
766737f2-0f0c-4f48-a096-23336900cabf | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
8fb6247a-6b5d-570e-a343-478b5d850fe7 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
4cfbafa5-c1a4-58e4-a914-b8b10d7c2f97 | note | Acceptance Criteria - Upon approval from Client & Engineering team
459285a0-14f6-5df3-8b8b-d651639c730d | note | Verifying Document - Written approval
a6639da2-1538-5c14-8e76-d5584a818e37 | note | Frequency - Once
0b3b6c22-ac88-5286-bc39-9759bcb42dee | note | Inspection Type (Visual, other) - other
9f19f03d-45de-5668-9e64-bdeaa1287f22 | note | Inspection: Key - R
01cdf0ea-bb84-56e2-b41a-ee69fe422ceb | note | Inspection: By - CR
6e4715a4-4b58-43f9-ab9b-81aef24ad767 | section | SECTION 4 – IN-PROCESS INSPECTIONS
7007e095-8fdd-4526-9868-e04741f4a880 | checkpoint | 4.1 - Shutdown the pumping system (all pumps)
0dcb667b-eda1-5591-866d-73e073223ea7 | note | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
dbaaba3e-fc11-5198-8543-6fe29a8c6416 | note | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
9a4910cc-513e-5dfc-a2e9-7031cc8ede5d | note | Verifying Document - Advice from DCC Operations
9ea2bc31-a6bc-50eb-8de0-a1e8f19792ef | note | Frequency - Once
89b76f09-7fc2-592c-a426-c68cff46a731 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
f470d018-1f73-55c5-b4af-10c3738e0cce | note | Inspection: Key - C
b24fea03-727d-5c7f-9add-6fe2b2cc0641 | note | Inspection: By - CR
3759ab1c-a0f5-450f-87f6-324f7aaec30a | checkpoint | 4.2 - Removal of suction side isolation valve to pump 5 (wafer type). Inspect pump flange and valve flange
f7f21842-b690-5ced-bd8e-1e9282d7cdc6 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
babfff78-4c51-58b6-ada1-1ab9f0e65592 | note | Acceptance Criteria - Surfaces are clean
7f0bb6bf-5778-5dc3-99a1-5dd6849b89ae | note | Verifying Document - Visual
2a26e47f-5589-5416-b6c4-b9d2061e15a1 | note | Frequency - Once
0d9abb12-a23b-5958-9869-7fc6e9344c80 | note | Inspection Type (Visual, other) - Visual + Document
80b7d3aa-437e-5ce7-ad02-d281c9f03c24 | note | Inspection: Key - A
1b20e1da-21de-5709-a1ec-2bc07a3ec5ce | note | Inspection: By - QE
d8b430c2-efcd-4ef9-b91e-93b62bcce6c2 | checkpoint | 4.3 - Removal of discharge side isolation valve to pump 5 (wafer type). Inspect pump flange and valve flange
5fb71c5d-2230-5aa1-96e5-bac58a2864c3 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
6c8b80f6-322b-5628-b15d-a88d34fb1b1c | note | Acceptance Criteria - Surfaces are clean
e8c6d6b4-1f4f-58b6-af55-49ba33460427 | note | Verifying Document - Visual
80302c0d-4f01-5e6b-841f-8796cf6dd536 | note | Frequency - Once
91610cf7-4c23-5f7c-baa0-75a3c934fffa | note | Inspection Type (Visual, other) - Visual + Document
2a8d5b45-cae3-58c5-b092-99d84b6123f8 | note | Inspection: Key - A
0ac2b196-76cf-5585-aca0-33cb1fac268f | note | Inspection: By - QE
ff84c1c6-8861-40bf-880c-b160c79bbb58 | checkpoint | 4.4 - Suction side valve installation
2c095f8e-6471-5a42-ae67-e52f1d49bb94 | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
cad02e78-ca39-5b0a-91ca-af54f3cf07d8 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
f3a9c5d0-4f44-5d2a-9739-d656db7d518c | note | Verifying Document - This ITP
5f5d76ad-e409-5028-8e53-f0f0a6166004 | note | Frequency - Once
75c87af9-fa5f-51ad-88cd-51f5fa3d584c | note | Inspection Type (Visual, other) - Visual + Photograph
bb30c354-4164-5794-83ce-227a178be1ff | note | Inspection: Key - I
168d7abe-2d2f-5394-b97f-c38603c4a0c2 | note | Inspection: By - IP
c88292b9-3c15-4623-81b3-2d24a329470c | checkpoint | 4.5 - Discharge side valve installation
4e711870-3a7b-5662-bcab-32ef9dc9d901 | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
5316cd9d-b3d8-512e-a06c-abf01b9322e5 | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
24dd2947-e813-5994-b406-24b60f138e70 | note | Verifying Document - This ITP
647b5a8a-f911-50e3-93ad-b5e385fb9b9f | note | Frequency - Once
d5e9d942-d601-5d66-90ff-40098012bc31 | note | Inspection Type (Visual, other) - Visual + Photograph
ba43d9fc-2e13-5007-8d66-cf7763c7ada5 | note | Inspection: Key - I
52704237-b4a0-58fe-bd88-ddf966490e27 | note | Inspection: By - IP
42730c59-eb7e-4da1-a91c-96f8fcd6e86a | checkpoint-no-value | Note:
6ad9747c-5f98-5b2c-9991-49d965cb79dc | note | All valves to be left in closed position
4038789e-bdb0-4daa-9636-1ae361f43a88 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
dad87f7a-e5a1-4ded-90ca-584cf829e3a8 | checkpoint | 5.1 - Returning existing pump 5 for duty
d3ffd854-0179-5854-a1e3-4282ba15dd23 | note | Inspection Point: Quality Control Activity - Purge pump 5 of any entrained air
b7996de8-fc17-5942-8719-872195afa1fa | note | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
e692eee0-88c0-52fc-8db8-57237489ac27 | note | Verifying Document - Visual
a3dd8b63-eee7-5ab5-90c4-ce560c17fa2d | note | Frequency - once
76e58e82-4544-53bd-a263-b77668969240 | note | Inspection Type (Visual, other) - Visual + Document
9e77b388-375d-57a8-8efe-47711da1468f | note | Inspection: Key - I
905e4658-7c1c-5c33-a741-fc1a99536292 | note | Inspection: By - IP
76e13132-db22-4f54-b720-d7fa1ad1d670 | checkpoint | 5.2 - Power reinstatement to pump 5
68459864-05c9-589e-b79b-fa2a91785be1 | note | Inspection Point: Quality Control Activity - Remove lock out tag pump 5
4b3b075a-74b8-5ca1-acce-8dc1f6120fa6 | note | Acceptance Criteria - Completion of 5.1 above
1002198c-5ca8-54c4-8603-dfbf07fa2b76 | note | Verifying Document - This ITP
7cda4f73-6dbb-58e6-8297-55b2762a3507 | note | Frequency - once
46573eb6-0d1b-5175-ae11-9fceaa5a37cf | note | Inspection Type (Visual, other) - Visual + Document
ce13b43a-2993-5da5-b986-c1f1c530cc92 | note | Inspection: Key - I
c7547a75-f798-50a8-8e1e-23f5352946d5 | note | Inspection: By - IP
a691b783-719a-4f34-ab21-dc98599544f5 | checklist | 561483-ITP-007.6 - Pump 6 Isolation Valves Delivery & Installation | itp | 561483-ITP-007.6 - Installation of Pump 6 isolating valves - Inspection Test Plan
f7ea2815-48ca-45cb-9669-190ba11115c2 | section | SECTION 3 – RECEIVING INSPECTIONS
b7cde502-d1a5-4ad9-8a54-0ba1a37cefb4 | checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 6
3ec0ea8d-d5c0-5ee3-bfd6-11499c7537bf | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
62946520-bdb1-5704-a77d-35a5c8d272d4 | note | Acceptance Criteria - Must be on the Approved Products list
4117eab0-61a7-5b4b-9058-40b693049cb3 | note | Verifying Document - Specification - Approved Materials list
01fa799b-1862-5dfd-b7a2-c70e1dc80438 | note | Frequency - Once
bfb7786c-addb-57ab-b3fc-5b7f6e3ffc7d | note | Inspection Type (Visual, other) - Visual
49dd6a6a-a3f6-5338-82a8-b82130e6b5be | note | Inspection: Key - C
46172f05-8e20-56d5-9d6e-42633e1c0e9f | note | Inspection: By - IP
85bf015f-bf76-4cb4-9a72-b6fb5207c7f6 | checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 6
53e444a5-4bdb-5950-8a81-9b3c77eb6c72 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
53b23f1c-c37c-5d08-ba58-0eaa49270ca7 | note | Acceptance Criteria - Must be on the Approved Products list
d3488d13-3696-5e2a-ac29-7a3111c39977 | note | Verifying Document - Specification - Approved Materials list
0917baec-7946-535a-98d8-1106198e15ee | note | Frequency - Once
83c66062-c0f7-527c-8036-df693b16959a | note | Inspection Type (Visual, other) - Visual
cf240a0e-bba5-564a-a853-73b425d8d071 | note | Inspection: Key - C
38ff1059-6642-5da2-8771-4b5119df24a9 | note | Inspection: By - IP
7e6e8464-5bdc-4712-aa7a-477999c0bdab | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
275ba96e-8366-5e51-97ea-92ec6242a9d2 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
16d0bc50-5cbc-560f-a458-2f8f43ad002e | note | Acceptance Criteria - Upon approval from Client & Engineering team
cd4e783b-1c60-5871-a068-eed6c80cf873 | note | Verifying Document - Written approval
aace337b-c176-584b-adca-26d13198db7d | note | Frequency - Once
056ad4f4-f790-5849-94fd-7118a1c36280 | note | Inspection Type (Visual, other) - other
622b6296-c666-5730-a766-706f38643220 | note | Inspection: Key - R
fd46ae12-8b2e-50e8-9dca-ed38c871d4a7 | note | Inspection: By - CR
f07a4a50-363f-4b94-baa0-4ce355691305 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f0f887d9-6d48-404a-be87-00314c020267 | checkpoint | 4.1 - Shutdown the pumping system (all pumps)
ca42f85b-f236-5bf0-9977-b55f975820e4 | note | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
fff9e09e-3704-5398-adf2-74cba7b5fbdf | note | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
f96d08cc-9dd6-5f1f-a6d8-4bd5da458b02 | note | Verifying Document - Advice from DCC Operations
878e7ce7-80f7-57a2-967b-62774a3c13da | note | Frequency - Once
1ba762b4-ae0e-5064-93a7-e262ba9d6bbe | note | Inspection Type (Visual, other) - Visual + Written + Verbal
213ec5bd-d9fb-5fee-85bc-432f3d891e65 | note | Inspection: Key - C
1a90a669-0ea5-596b-81c7-ddf84a296cd0 | note | Inspection: By - CR
6ec9ba70-8362-426e-8fe7-1155f8078ad5 | checkpoint | 4.2 - Removal of suction side isolation valve to pump 6 (wafer type). Inspect pump flange and valve flange
91c612b7-f3cc-59a7-a98e-e15d666a2401 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
82568804-a5f1-5dec-bb48-054178157fe9 | note | Acceptance Criteria - Surfaces are clean
53d26c53-a6a9-56d5-a2fd-96c03ae7dc18 | note | Verifying Document - Visual
009a35d7-9587-5e76-97c2-22396c3e14db | note | Frequency - Once
67cbba28-d2a7-5ee7-9164-034c48c57e42 | note | Inspection Type (Visual, other) - Visual + Document
27914785-4139-57d4-bfa7-c6381d6471dd | note | Inspection: Key - A
58cea32b-34f4-5485-ab23-171a254a7724 | note | Inspection: By - QE
34df065e-b4d8-4a07-937f-e1d68a85b422 | checkpoint | 4.3 - Removal of discharge side isolation valve to pump 6 (wafer type). Inspect pump flange and valve flange
4e5b4511-9f81-5331-b594-1fb5fe803d33 | note | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
158d3bb4-5caf-576d-bd47-f76fc4f91dc4 | note | Acceptance Criteria - Surfaces are clean
718a0a52-e561-50d6-870f-3f9993e06935 | note | Verifying Document - Visual
f5ddcd84-5a09-5bff-9773-92402c729ea3 | note | Frequency - Once
94c04269-bfe5-5365-86f4-8e7780934f26 | note | Inspection Type (Visual, other) - Visual + Document
80b771e7-4fd1-5620-923d-df836461bfae | note | Inspection: Key - A
7e3084d1-b721-597a-bbf4-9096ddf3d8ce | note | Inspection: By - QE
1cba6772-f9bb-4cfc-a1d9-0877658d47ea | checkpoint | 4.4 - Suction side valve installation
e1e9e30c-0a50-5774-ae64-ba6059a9ef5f | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
d0423d21-3580-5109-9329-b285434f691c | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
e3c7f410-23c9-56ef-8145-00be3a821f8a | note | Verifying Document - This ITP
69b35f77-d517-5b11-aa96-5625a88ea230 | note | Frequency - Once
125cb525-5cb5-518a-a197-e8263deee961 | note | Inspection Type (Visual, other) - Visual + Photograph
fd20527c-03b3-5592-a97e-d644ca8654cc | note | Inspection: Key - I
bf2d9738-9192-5443-ac87-671acc42c340 | note | Inspection: By - IP
a6ebb3d1-c10f-4bd7-abe6-85983e68ed41 | checkpoint | 4.5 - Discharge side valve installation
f73c8b21-376c-5d24-a90b-dcd40dd50a4e | note | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
34ebef5a-ea58-542d-bb54-a4e31ac911af | note | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
04c3ed13-9c88-5657-9de2-c7738337a53e | note | Verifying Document - This ITP
5337444c-d580-58d4-bdbd-78c0420b4c53 | note | Frequency - Once
8c370f43-d31a-5e5d-b4b2-4c76ac6a970f | note | Inspection Type (Visual, other) - Visual + Photograph
50d63fee-abee-597b-9b45-e863b5e508b3 | note | Inspection: Key - I
34b3e968-5dfb-576c-9a0e-2de4a70620ec | note | Inspection: By - IP
ac239cae-0ec8-4c78-9cf3-ad473084af42 | checkpoint-no-value | Note:
5a92ae90-2bde-5a36-9703-d3f6584b153e | note | All valves to be left in closed position
7df4b5fb-7e3b-47a6-8e41-7b67a96b0365 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
bab1e950-da7e-42b3-a6d8-92f4d7b9d804 | checkpoint | 5.1 - Returning existing pump 6 for duty
169dc1ef-335b-5903-8716-1ec892ab7d85 | note | Inspection Point: Quality Control Activity - Purge pump 6 of any entrained air
4b7b7df6-927c-5952-bc2a-b09937f441d2 | note | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
f1a119f8-36a0-5e24-934c-5e3075dfd5ef | note | Verifying Document - Visual
24d49cf2-b6b2-5fe0-bcef-4637fd85b0ea | note | Frequency - once
15ebd05a-044c-58c6-aaaa-4dc6017b3cd7 | note | Inspection Type (Visual, other) - Visual + Document
7745138e-0d92-5f45-a15f-3f6abf8e8834 | note | Inspection: Key - I
9046aabe-69fd-5aef-9148-474c98bfc9bf | note | Inspection: By - IP
eac69eda-6da2-4b87-8afa-8e8d96624f26 | checkpoint | 5.2 - Power reinstatement to pump 6
4b5894e2-3a04-52a1-b534-171ccafd5995 | note | Inspection Point: Quality Control Activity - Remove lock out tag pump 6
063c0074-fb8e-5922-a0c1-be4c6e7786e6 | note | Acceptance Criteria - Completion of 5.1 above
ad896127-2838-5634-951d-4078c41f70fe | note | Verifying Document - This ITP
2bca7c46-df5b-56c2-9bc7-85209ed60fd7 | note | Frequency - once
e95721cd-7434-53ce-8239-2af7e9a3b66e | note | Inspection Type (Visual, other) - Visual + Document
3f454cd2-b6d3-539f-a604-813fcc8613f1 | note | Inspection: Key - I
029ff456-3f02-560c-a588-85444a1a7c18 | note | Inspection: By - IP
603cf8ea-2044-4b0d-8c19-33f8d4141965 | checklist | 561483-ITP-008.1 - Pump 1 Delivery & Installation | itp | 561483-ITP-008.1 - Delivery & Installation of Pump 1
d1a9a446-4e8d-4594-ae4f-242ab304e8b3 | section | SECTION 3 – RECEIVING INSPECTIONS
0e0f6983-b268-4420-9f4e-2b570dd82e38 | checkpoint | 3.1 - Delivery of Pump 1 to site from Downer storage facility
8ace37a3-bbd8-592d-874d-63ea5eb4a2f9 | note | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
4a51284d-c736-5ad7-9b56-95bbc80916f1 | note | Acceptance Criteria - Pumps are damage free
75fa932a-973a-533b-ba7a-c92075228e34 | note | Verifying Document - 1. Pump delivery docket.
7411318a-fb7b-5fae-a0e6-8ca5a53a5a0b | note | 2. Pump storage ITP
c03b7228-ed7c-5fc7-aef8-8636d6389235 | note | Frequency - Once
8aa67a8b-27d4-54a2-b76e-c5b09dd3bde2 | note | Inspection Type (Visual, other) - Visual
54106bd6-c387-540e-a77e-c7896f526aa9 | note | Inspection: Key - C
83f26ea7-0615-5668-8128-370d62d350e0 | note | Inspection: By - IP
f18318fe-8c40-40b8-8eb9-05ccd9509ec9 | checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 1
8c1885f1-fd43-5188-ac5b-a885c4157b1d | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
1d7fe2a0-e68c-5cbc-935a-55b8f78d2e40 | note | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
90f467b3-df32-58c8-b369-eeefe0c4d50d | note | Verifying Document - Written approval
9e13d554-ac71-5af9-b2f1-91c6c475ff23 | note | Frequency - Once
2d53652b-9742-5d55-9b76-2c35a23d56b4 | note | Inspection Type (Visual, other) - other
f9a1f8d2-98d3-5ac7-98e5-fa1a879ce30d | note | Inspection: Key - R
3ce8303f-a27f-58ec-8542-718a4dfc5526 | note | Inspection: By - CR
d897ddf1-1bf4-4ff1-8f87-bbf4074b959f | section | SECTION 4 – IN-PROCESS INSPECTIONS
0b7e8cdb-d5a2-4c52-bb1e-e6dc035ecf42 | checkpoint | 4.1 - Shutdown Pump 1
b2d9f9a1-0482-58c7-9cfe-2fa89a6e044f | note | Inspection Point: Quality Control Activity - Isolate Pump 1 Electrically & Mechanically and release any residual pressure.
bdf7592e-34fd-556e-9844-ea952d721316 | note | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
8d877213-2f7b-5282-8da9-8c79d7999888 | note | Verifying Document - Advice from DCC Operations
c7ce594b-8a18-5cff-bbc4-63e2742b9742 | note | Frequency - Once
0325c8a6-ab98-55e4-884b-714885503a40 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
23ff6afa-140a-5f73-bd44-d15e227c6f21 | note | Inspection: Key - C
f10d6b5e-0aa5-5175-85e0-fda500c8774c | note | Inspection: By - CR
a37dc98d-e759-43c8-9993-124e24cc18ed | checkpoint | 4.2 - Remove Pump 1 base plate - This may have to be cut into individual sections to accommodate each pump
16dece17-8ff0-546b-86e9-2dd08b551819 | note | Inspection Point: Quality Control Activity - Remove fixings from floor
67fdddc7-88ba-504c-954c-93ad606827c4 | note | Acceptance Criteria - Pump 1 is removed
98872fb1-b94b-5f25-a5cb-821e52b00364 | note | Verifying Document - This ITP
f575daa5-d900-5d0f-a58d-259838a5b0e4 | note | Frequency - Once
cfeed9e1-f64a-5291-9bfb-b857c57dab3a | note | Inspection Type (Visual, other) - Visual
e0e358df-ceb1-5d77-ba86-c583f2c6f06b | note | Inspection: Key - I
7b954090-fbf7-5d20-8225-f68480424059 | note | Inspection: By - IP
42f04f33-d2d9-452b-a625-ce78257206a9 | checkpoint | 4.3 - Install New Proprietary baseplate for Pump 1 - This may have to be cut into individual sections to accommodate each pump
e254bd7e-1264-5f3d-a6ab-c9c2b5e7ae31 | note | Inspection Point: Quality Control Activity - Check dimensions
88bf0377-d958-51f2-b78f-5b101484ce1e | note | Acceptance Criteria - Plinth is in suitable condition
34d09d05-e944-527a-aa85-df419a812b93 | note | Verifying Document - 1.Grundfos documentation.
e4a08411-b9b8-5559-a7f0-d4abb265033e | note | 2. Project Drawings
9f6fec41-6fee-5cb5-95ad-6c4dde71ddfe | note | Frequency - Once
3508f984-99a0-58c9-9f1a-355c4aa7d5d1 | note | Inspection Type (Visual, other) - Visual
5baae137-d1ef-5ecc-82ef-0178a044adff | note | Inspection: Key - I
b5f05fde-a980-5514-bb81-419f568df3b4 | note | Inspection: By - IP
9cd07485-68d0-490b-8247-1b31881e24ae | checkpoint | 4.4 - Pump 1 Installation
1e1fe52e-e7ab-508a-b16d-d2a0f403af91 | note | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 1 into position & bolt down
355ff1ab-0440-54fb-8d6a-66c9a5a0343d | note | Acceptance Criteria - Pump base plate mounted in correct position
489caa62-fb33-55a8-93fd-da237a93588c | note | Verifying Document - 1.Grundfos documentation.
61871af4-2b61-5f36-ab3e-8d4d68d5492f | note | 2. Project Drawings
ecb0e023-77e9-56f6-a3cd-3f1cf1fee74e | note | Frequency - Once
677f47b4-fb6f-59fd-8d61-2a87c2f3ab70 | note | Inspection Type (Visual, other) - Visual
b14af4ec-b29c-52e2-8f2b-e3dd705bbbc4 | note | Inspection: Key - I
7548ce9d-28b8-5913-aad6-7e5caefb79a1 | note | Inspection: By - IP
56bb69cb-f1d4-4855-8624-43b81f747a73 | checkpoint | 4.5 - Install gaskets & dress sets
568c4115-e2d7-5f26-ae84-70f400117e22 | note | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
20066116-a325-5b39-bb5c-6114666828c2 | note | Acceptance Criteria - Torque to 80N.m
cb449016-4864-5196-9371-4feaec36b58d | note | Verifying Document - NZ Water Standards
8d65d479-e4db-5cf9-9985-4484f2149975 | note | Frequency - Once per bolt
020ca8c5-4e4a-56ce-af56-35f8b340a08e | note | Inspection Type (Visual, other) - Visual
7e053ac2-5f42-5cb3-9e82-cef05122bdfe | note | Inspection: Key - I
72a27c26-9c8b-54a8-b928-25b8dde51c85 | note | Inspection: By - IP
63df39cb-32a1-436e-86ae-209951bc1a37 | checkpoint | 4.6 - Preparation to run Pump 1
8a01ceba-ea89-5ae1-913b-b5e61af16b03 | note | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
af5df3c7-10cd-5769-9ef5-92e26ac36848 | note | Acceptance Criteria - Water visible from purging valve
809bf152-0090-55e5-8e0f-0bdc66e08d13 | note | Verifying Document - This ITP
bc85bd40-fe91-5434-aa76-cc9ae9523424 | note | Frequency - Once/per pump
5d5d96af-98f4-5ca9-8c0b-e09e78a2754f | note | Inspection Type (Visual, other) - Visual
f2e55fa3-ba45-5fd3-850f-5a8d9db950c0 | note | Inspection: Key - I
802be0ea-e9ee-5856-9401-515b6edac850 | note | Inspection: By - IP
c32ecd5b-4c93-470c-ba2c-17567bc8bea8 | checkpoint-no-value | Note:
06f5de23-1807-578b-a50e-88d0470139b0 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
4a76137f-8e5c-4427-9ca7-e937529271d3 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
b5c75657-ac5a-49d4-a64d-772c58eedbd6 | checkpoint | 5.1 - Pump 1 Changeover Complete (Mechanical)
1bea8454-8b9e-5724-a792-99e78384915b | note | Inspection Point: Quality Control Activity - Check for any leaks
24443d79-f076-5eb8-be8b-ab9d0c7536de | note | Acceptance Criteria - No visible leaks
8d5a1b36-82e9-5579-9e26-c0bc32ebefd4 | note | Verifying Document - As per methodology
096a2544-ed3d-50fa-9b8c-7a9956a74908 | note | Frequency - once
db356d69-46dd-5a61-a548-1157cee46307 | note | Inspection Type (Visual, other) - Visual + Document
80a65b69-36cf-53a8-84e4-4879dee275fb | note | Inspection: Key - I
874f15d4-8bed-514c-a9c8-bf1e08d0d83b | note | Inspection: By - IP
57bb239d-2c13-48fc-b97a-c479d31dba48 | checkpoint | 5.2 - VFD 1 Changeover Complete (Electrical)
7edf10ae-0d91-585b-a5bf-7a2da2c5ab11 | note | Inspection Point: Quality Control Activity - Power to VFD1
ca3f7645-59a1-5d7e-adf9-45bd7c1c0af3 | note | Acceptance Criteria - Completion of VFD1 ITP
e0913bf1-2111-5573-95b8-b722a744ac07 | note | Verifying Document - 561483-ITP-009.1
bae9490a-766c-52b1-b5ea-753a24d44983 | note | Frequency - once
850e1d02-caff-5907-9dab-3a56d39ec98f | note | Inspection Type (Visual, other) - Visual + Document
d13b2425-1ae7-5ded-8e32-0e412f2b587c | note | Inspection: Key - I
a016e8a8-de0a-5f7f-9423-2e542c35e99b | note | Inspection: By - IP
a3f9da4f-cfc2-46a5-ac63-b67e418133ca | checklist | 561483-ITP-008.2 - Pump 2 Delivery & Installation | itp | 561483-ITP-008.2 - Delivery & Installation of Pump 2
3366af5d-e3d7-4e91-8683-c41b1c7259f8 | section | SECTION 3 – RECEIVING INSPECTIONS
967d1a9d-ecdc-42ca-a768-c9af9d11712b | checkpoint | 3.1 - Delivery of Pump 2 to site from Downer storage facility
ea34810d-cc06-50e1-bd91-3d7b96a36c53 | note | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
4dff2a4a-1bb1-5452-a08d-e5defb22373f | note | Acceptance Criteria - Pump is damage free
077fbf54-1058-534d-83f3-77da4c17647a | note | Verifying Document - 1. Pump delivery docket.
9c66b99f-0aa7-5d58-851b-977cb33b9333 | note | 2. Pump storage ITP
98eec331-93fa-59b0-b067-1965a43b17c3 | note | Frequency - Once
bce5eca6-7480-59bf-8b69-51e2b59acd95 | note | Inspection Type (Visual, other) - Visual
f7c22f99-39cb-56b8-9b0d-e5c767e560e4 | note | Inspection: Key - C
448602ef-c09a-5c42-b408-1baadcf061d4 | note | Inspection: By - IP
2e7db7c3-4f09-42af-9f6a-cd20fecf271c | checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 2
4c52acab-0eb5-5b14-b20d-bf2908e729e1 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
afb93611-aaa1-5a86-8eff-f16826c62127 | note | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
5fe497fb-4a3f-58e1-bc6c-a43a818ee393 | note | Verifying Document - Written approval
553d2315-a7ea-56d3-a563-7c3c3e3a5f62 | note | Frequency - Once
4486b30c-0778-5465-8c74-6dea1d54538e | note | Inspection Type (Visual, other) - other
818b45a0-5bbf-536d-a0ec-14ff5c273dc7 | note | Inspection: Key - R
df7eeeb2-f2cb-5673-9289-eee174098aba | note | Inspection: By - CR
b7fab91d-1f99-450e-93a5-870365c4853a | section | SECTION 4 – IN-PROCESS INSPECTIONS
39d38d00-034f-47c6-ada1-48b00389cb0e | checkpoint | 4.1 - Shutdown Pump 2
d4ce4a6b-0914-5d9e-8320-f3864fb79262 | note | Inspection Point: Quality Control Activity - Isolate Pump 2 Electrically & Mechanically and release any residual pressure.
24073f79-1848-5739-833c-e03f82e37bbe | note | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
ff3059df-5bec-5097-9e31-6052736db695 | note | Verifying Document - Advice from DCC Operations
392565c4-0a57-5e08-ae6c-9aee75cd788f | note | Frequency - Once
5947cb13-ecbb-5abd-ae8b-1917a17b7e0e | note | Inspection Type (Visual, other) - Visual + Written + Verbal
197a0a89-7e8c-50ac-ac47-55c41da97234 | note | Inspection: Key - C
ed87cdcb-f477-5675-b982-9bc764d5beae | note | Inspection: By - CR
290c7ce4-6437-41e6-9b2c-e7ca1e40677d | checkpoint | 4.2 - Remove Pump 2 base plate - This may have to be cut into individual sections to accommodate each pump
f628d5fd-9c9d-555c-b7f0-e72c1ccd7ea4 | note | Inspection Point: Quality Control Activity - Remove fixings from floor
5f687cc2-9f95-5475-a771-f0bdcad0fbbd | note | Acceptance Criteria - Pump 2 is removed
2c12bedb-1ae2-585e-bbe0-69cae2debb8a | note | Verifying Document - This ITP
a8c01482-0e37-5864-8f27-1ccab382b63b | note | Frequency - Once
66b583f1-0cd3-5af6-8fb4-5ae0c102435d | note | Inspection Type (Visual, other) - Visual
7e7ee49c-a4b7-5e69-b6e8-37e4307af188 | note | Inspection: Key - I
9a757057-6502-5542-9279-e6045c50d3a6 | note | Inspection: By - IP
295c635d-dade-48e7-9955-c13567de880c | checkpoint | 4.3 - Install New Proprietary baseplate for Pump 2 - This may have to be cut into individual sections to accommodate each pump
f3772d8b-8032-5f72-864a-c99280c553a0 | note | Inspection Point: Quality Control Activity - Check dimensions
8e168094-c89d-5016-adec-8da35972086a | note | Acceptance Criteria - Plinth is in suitable condition
6162bd40-3062-50ec-a636-f1ac60734521 | note | Verifying Document - 1.Grundfos documentation.
4b804039-502e-5533-87a2-94a6bc71c1f2 | note | 2. Project Drawings
f007641e-615b-58f9-8306-20a864a5f0ad | note | Frequency - Once
e0a79166-9715-5aa7-947a-242b59002914 | note | Inspection Type (Visual, other) - Visual
503fb16e-751c-550f-8c47-db0a1aafc1ab | note | Inspection: Key - I
07969259-92b1-5c25-8335-89b582f26c3e | note | Inspection: By - IP
befd292d-9d64-4c4c-9cc7-8f5fb098dc59 | checkpoint | 4.4 - Pump 2 Installation
20f53c64-e157-5485-bd23-61942c6d251a | note | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 2 into position & bolt down
262e96f2-5114-5a10-9821-86d35e0f779f | note | Acceptance Criteria - Pump base plate mounted in correct position
0fe30eaf-c91f-59d2-b099-fa7c6ec64876 | note | Verifying Document - 1.Grundfos documentation.
852a484f-31e2-5c82-9178-03cb1ed7f015 | note | 2. Project Drawings
8e25059c-f055-5c1c-8da1-ee711ab9909f | note | Frequency - Once
52db8ee8-6205-5738-82b3-526fe5dc4574 | note | Inspection Type (Visual, other) - Visual
2e1c67cc-698b-5352-a394-1598190d66fc | note | Inspection: Key - I
55179ecd-208e-5ff2-9d1d-5bc9f217d014 | note | Inspection: By - IP
539953c9-2c91-4893-9f84-a737b9a41744 | checkpoint | 4.5 - Install gaskets & dress sets
f807fb1c-e7ca-5a15-b8b5-7f75aaf08726 | note | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
f3b47ec5-95a6-5fe5-8ac4-dce99dcd0ff4 | note | Acceptance Criteria - Torque to 80N.m
4a7e2cd4-d8ad-554f-a0f7-00a4a4ee8058 | note | Verifying Document - NZ Water Standards
078641f8-ae7d-5c19-bb0d-a3227a7075df | note | Frequency - Once per bolt
e72a9102-5c59-51db-8a36-80e271ff7d4a | note | Inspection Type (Visual, other) - Visual
4ee3c010-0087-5449-ae39-ba20f0313b71 | note | Inspection: Key - I
821e8a96-2cfa-54f9-9b82-d705b9296404 | note | Inspection: By - IP
52f3fca7-d845-460a-9871-07a754f0d5a6 | checkpoint | 4.6 - Preparation to run Pump 2
4a52d896-8ec1-57b7-8951-220b32e90c26 | note | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
31068939-1b4a-5b0f-b89e-c001daee96a2 | note | Acceptance Criteria - Water visible from purging valve
23b56370-1757-5080-9646-47f199322605 | note | Verifying Document - This ITP
bc53833f-b1f7-5ff7-a7d8-6e09c4eb7d53 | note | Frequency - Once/per pump
2bdb151f-5c09-587b-a858-0d113d65467c | note | Inspection Type (Visual, other) - Visual
af36fe65-8eaf-537d-b20d-ded3f1f1a2e4 | note | Inspection: Key - I
6ab495f2-0b40-5214-9721-c784e19bbd30 | note | Inspection: By - IP
60024802-8157-48aa-9405-bbcb2e30e108 | checkpoint-no-value | Note:
19c76f77-faf6-5212-a141-6d4e526e3e78 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
3e6dbdc1-9db2-4992-a56d-fcb5203ee094 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
e15449ae-36c6-4d10-9df3-d4e15039f19e | checkpoint | 5.1 - Pump 2 Changeover Complete (Mechanical)
3616d52a-3f21-523a-b34f-f1264e88a7a4 | note | Inspection Point: Quality Control Activity - Check for any leaks
3acf6028-cf0d-50d3-98d6-d7fa5e1a2953 | note | Acceptance Criteria - No visible leaks
da140245-1cca-5c8b-91b8-57c7acac8e86 | note | Verifying Document - As per methodology
56dda179-0b64-5610-92fc-fb05b4d2b3f5 | note | Frequency - once
e523f54e-fe37-59df-ac75-d2c9cdc62409 | note | Inspection Type (Visual, other) - Visual + Document
cc6c9413-3768-592a-9145-5e99c936e35a | note | Inspection: Key - I
e68fd06f-a88c-5cd8-abc9-7edafff7b8ee | note | Inspection: By - IP
bae0bf11-7318-43ac-9f2c-7bb3f696769d | checkpoint | 5.2 - VFD 2 Changeover Complete (Electrical)
6d3c35cd-d399-5d52-8007-9787ad9743b9 | note | Inspection Point: Quality Control Activity - Power to VFD2
a9bda529-20b0-52cc-8a12-867f88ca99f3 | note | Acceptance Criteria - Completion of VFD2 ITP
8ce8c699-df46-5971-912c-8b3d85a8c364 | note | Verifying Document - 561483-ITP-009.2
1a28c591-fd84-5dd7-89ce-c17bcd10799c | note | Frequency - once
6a27ab29-c81e-5bac-be1f-5fda43df2cc5 | note | Inspection Type (Visual, other) - Visual + Document
22f4cd6b-d14f-5c85-86c5-cbb1d7f76668 | note | Inspection: Key - I
dc0e8b8e-c29b-5b4b-9e6d-85f285e32fbb | note | Inspection: By - IP
f92b12c5-8ae0-4bee-b457-8e25f3393933 | checklist | 561483-ITP-008.3 - Pump 3 Delivery & Installation | itp | 561483-ITP-008.3 - Delivery & Installation of Pump 3
459bf4ff-c849-47cf-9540-19bab3bb8249 | section | SECTION 3 – RECEIVING INSPECTIONS
a0222b86-7e24-4577-91bb-133b6cef1547 | checkpoint | 3.1 - Delivery of Pump 3 to site from Downer storage facility
7523df42-e9bd-515f-9bcb-d7eda71e9ac4 | note | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
6cf5d7d0-1808-5551-abde-14d32b8e6417 | note | Acceptance Criteria - Pump is damage free
d0e6931e-a8f2-535d-9c41-bceaacf1b030 | note | Verifying Document - 1. Pump delivery docket.
d1c77113-fbd2-57ae-8c7d-442b510214ea | note | 2. Pump storage ITP
984b92ba-daa6-51a0-a31b-815d68fbc614 | note | Frequency - Once
33e5b818-b0ff-5553-a504-477c50da0941 | note | Inspection Type (Visual, other) - Visual
8e78853a-831d-5d2b-b42d-f13f52f8785c | note | Inspection: Key - C
df197e8f-c965-55f3-869e-1252181bf586 | note | Inspection: By - IP
7ef4e2df-0d49-467c-96a1-c6aa1bae6703 | checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 3
69438673-1e2e-5251-b7f6-5b8f2db191c8 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
b6022932-a2b3-5187-974a-7ce658a327db | note | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
0fc0a225-230f-5e16-b11b-26a92884afa1 | note | Verifying Document - Written approval
e7c92b6a-d5e0-5276-a7f0-8c1900754d63 | note | Frequency - Once
b1730a60-24a8-5dea-afad-8a13cab98410 | note | Inspection Type (Visual, other) - other
88589625-e134-5f91-beaa-41ca39754d4e | note | Inspection: Key - R
aa3a277c-781f-5af6-a181-6cc863e6c93f | note | Inspection: By - CR
4a753321-9c3a-4ab4-b02f-51bed46e5b63 | section | SECTION 4 – IN-PROCESS INSPECTIONS
b8e7032b-8609-42bf-8e4a-b193c2a29a12 | checkpoint | 4.1 - Shutdown Pump 3
052a085a-bd49-5854-bf41-1ede17a722f1 | note | Inspection Point: Quality Control Activity - Isolate Pump 3 Electrically & Mechanically and release any residual pressure.
5e238ff3-ec13-511f-9e26-d3d3f580606c | note | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
e2e24847-8085-55cf-b744-f0bda2ce774b | note | Verifying Document - Advice from DCC Operations
662b76ff-2400-5c43-91fb-6e7638b07bf1 | note | Frequency - Once
85a4c9c0-d1ad-58d4-b666-94f22b8cb016 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
5332433d-a095-53b4-bf7e-2e225fd0724d | note | Inspection: Key - C
81d4dd9b-8d47-572d-aca3-d53f6fe204d9 | note | Inspection: By - CR
10d679fd-1cfb-4ea9-9894-6cfd0e733608 | checkpoint | 4.2 - Remove Pump 3 base plate - This may have to be cut into individual sections to accommodate each pump
2dc0408b-917e-55ea-925a-c73b60338fd8 | note | Inspection Point: Quality Control Activity - Remove fixings from floor
9c43d2ac-1da3-557a-a627-c772d53bfe63 | note | Acceptance Criteria - Pump 3 is removed
bad3f9bd-5f7a-50fb-bfde-34aaca43ae2b | note | Verifying Document - This ITP
03995856-2015-559f-86ea-9bb0218ad945 | note | Frequency - Once
b4c7c6c5-3b1c-598c-bb98-9430c92fc049 | note | Inspection Type (Visual, other) - Visual
438da8aa-04df-568e-8568-a4ecda8322e9 | note | Inspection: Key - I
2c883d6d-d6dd-5610-9068-8040c5cac272 | note | Inspection: By - IP
eef7859f-9865-491c-8118-52f334f522ca | checkpoint | 4.3 - Install New Proprietary baseplate for Pump 3 - This may have to be cut into individual sections to accommodate each pump
1065ab9b-3796-528f-94a6-c8af65bf6608 | note | Inspection Point: Quality Control Activity - Check dimensions
9516d5a8-fc91-53d0-a37c-8af4f332e99b | note | Acceptance Criteria - Plinth is in suitable condition
f65b2000-b713-5cf3-8aa1-6195aeca126b | note | Verifying Document - 1.Grundfos documentation.
0c9ed681-7156-54c4-8b16-8aff91d9c5e9 | note | 2. Project Drawings
888256ff-1005-59e2-ba5e-2563dd3c6c94 | note | Frequency - Once
ab4b62af-6e45-5c0e-93f1-18615ca6ee9b | note | Inspection Type (Visual, other) - Visual
2f5b7dac-a9a2-5a6d-9afd-37559929d5bc | note | Inspection: Key - I
25cc39d3-b643-5e64-a47a-634bb3ba718f | note | Inspection: By - IP
afad957a-62df-453d-b28d-c684b508909e | checkpoint | 4.4 - Pump 3 Installation
00a41be2-4cbe-56fb-bb76-88a3eb5203be | note | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 3 into position & bolt down
ac0190fb-81b1-5424-ab66-80622b2ca85a | note | Acceptance Criteria - Pump base plate mounted in correct position
14b0821d-f4d3-55c5-a297-93cb8f2f2cca | note | Verifying Document - 1.Grundfos documentation.
1479b3f3-f5da-501f-90d2-b518e621878b | note | 2. Project Drawings
925f061c-7f6c-5da9-a98a-ef08a73335ad | note | Frequency - Once
9b01b7e8-0321-5f8c-bc63-b7f06b911b76 | note | Inspection Type (Visual, other) - Visual
cfe8d01c-f985-5113-82f5-2ab01d8abf7e | note | Inspection: Key - I
9c4827e4-f7ab-5ca7-aa2d-3bfcfb5a3897 | note | Inspection: By - IP
4d29235f-5559-4d93-a50b-961263327a62 | checkpoint | 4.5 - Install gaskets & dress sets
e5206c4d-a18e-5ccb-af08-623b963196bb | note | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
d5b99219-dab9-539a-94ad-d1931eb8044a | note | Acceptance Criteria - Torque to 80N.m
99268bb4-eb11-5b6a-8f82-c92b74646ed1 | note | Verifying Document - NZ Water Standards
cd9a8bde-f05a-5314-bec1-324422085ebc | note | Frequency - Once per bolt
4e3c566a-e000-58fc-b925-93ab3fee4dc6 | note | Inspection Type (Visual, other) - Visual
f8127304-f7da-5dfd-b9d5-07e42dc56bb1 | note | Inspection: Key - I
7e8d5eb9-5a2c-51b0-8a17-170a0e88180b | note | Inspection: By - IP
ab55f726-4c39-4700-9205-c8c8ffc199cb | checkpoint | 4.6 - Preparation to run Pump 3
05f967a8-cb54-5b27-954b-6879c7c22872 | note | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
cd155303-68d0-53d5-a202-076af8adb990 | note | Acceptance Criteria - Water visible from purging valve
611bb9dc-b5ae-59e9-9266-308296b6e28e | note | Verifying Document - This ITP
5ceead39-b3d5-5c8e-aabe-463e8b86bbc0 | note | Frequency - Once/per pump
647df02b-7141-5b99-9fe3-85f8d9b3b00e | note | Inspection Type (Visual, other) - Visual
c487c8a5-5fbc-5c68-b8fd-bcf312434ed4 | note | Inspection: Key - I
673519a8-02a2-570a-995e-86f84dbfdbe8 | note | Inspection: By - IP
36b5f4bc-2cab-49e7-b3af-f1763cfc27bd | checkpoint-no-value | Note:
565cef8f-d09e-5ce2-80aa-82d9ed0ae1bf | note | Electrical connection of pumps and commissioning are covered in separate ITP's
aaabc3e9-1326-4c62-a820-5c18dd3acee8 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
0db55340-7610-4680-a50e-73c88eaf7f74 | checkpoint | 5.1 - Pump 3 Changeover Complete (Mechanical)
a8610f2f-6a03-5ce1-8d3f-7454b8b67987 | note | Inspection Point: Quality Control Activity - Check for any leaks
294f9a4d-62ab-553b-8626-6c301b7f892d | note | Acceptance Criteria - No visible leaks
874ec555-ed36-5588-ad00-45871076afcf | note | Verifying Document - As per methodology
96bbef1e-46d4-57e0-9b3e-e34102699292 | note | Frequency - once
e7983a51-a517-5d6a-a410-2f52b087a351 | note | Inspection Type (Visual, other) - Visual + Document
bdce9d2c-59ed-5d7f-90f5-6ea6baa1e021 | note | Inspection: Key - I
4054d3ee-cb74-5161-9d31-ae83350eec4b | note | Inspection: By - IP
134d9fd4-9e67-42c6-930c-89a57b17c020 | checkpoint | 5.2 - VFD 3 Changeover Complete (Electrical)
1522356d-b4f8-5a52-81af-686c7f1d71ef | note | Inspection Point: Quality Control Activity - Power to VFD3
89873b2d-a91d-552b-8c64-85fcb390f5b2 | note | Acceptance Criteria - Completion of VFD3 ITP
7f7dea2b-07b5-5e08-a135-4d6286f37fce | note | Verifying Document - 561483-ITP-009.3
bd54fb2d-39c9-5036-90cb-a140df9ae9b9 | note | Frequency - once
d627a4a2-488a-5067-8e4b-39c74697095e | note | Inspection Type (Visual, other) - Visual + Document
aa3404a6-c6b2-5e0a-addf-77b0c680ca03 | note | Inspection: Key - I
1042fcc9-5dca-556f-a0ff-627c36105981 | note | Inspection: By - IP
4d343cfb-3878-47e9-b919-d5b62c5857f3 | checklist | 561483-ITP-008.4 - Pump 4 Delivery & Installation | itp | 561483-ITP-008.4 - Delivery & Installation of Pump 4
18df8656-665a-453a-9d31-5ac7cd9d7f9e | section | SECTION 3 – RECEIVING INSPECTIONS
155ea097-0203-4e77-8820-859a2e18f75a | checkpoint | 3.1 - Delivery of Pump 4 to site from Downer storage facility
7e0d3dad-4f07-53f0-88dd-816f873110d1 | note | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
2da7ea23-359d-5c23-950a-786c70850ec4 | note | Acceptance Criteria - Pump is damage free
5a28f98c-dbf7-5a6a-b52f-cf6eb4b5d1df | note | Verifying Document - 1. Pump delivery docket.
a4f32de4-02d0-58cd-b139-47ebe4326662 | note | 2. Pump storage ITP
2fa68e9c-b91b-5b7b-b8c3-68d6232705f2 | note | Frequency - Once
4a6c2e0f-3a8d-5ab1-9b69-a88e9e4f6ce6 | note | Inspection Type (Visual, other) - Visual
571b0f7e-b35a-51a2-afb8-78dc442663a8 | note | Inspection: Key - C
06d00b04-86e5-57c2-9d3a-9418f558e242 | note | Inspection: By - IP
f2eef10e-a192-495b-82dc-edb4341cf330 | checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 4
bec41e21-1565-52b3-940d-bd5a21a52477 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
370aef8e-ae37-549d-b72a-a47f6e96a386 | note | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
21611394-23a1-5758-b4bf-0a7de5c192e5 | note | Verifying Document - Written approval
be15a09c-3aac-5a44-8037-7e96abd366ec | note | Frequency - Once
450e468f-1a85-53b8-9822-ed0437e9502d | note | Inspection Type (Visual, other) - other
05d8ec96-7cb9-5ce4-85a3-058e8b1091bf | note | Inspection: Key - R
d13c4d8f-a74b-5d6c-9173-2c367878a891 | note | Inspection: By - CR
7886a614-df1b-4396-a362-50ba50e1bfcd | section | SECTION 4 – IN-PROCESS INSPECTIONS
1981e1e9-bfca-4c5d-9afc-660611e11ad2 | checkpoint | 4.1 - Shutdown Pump 4
ff245dcc-be94-51bc-859e-702da9e16806 | note | Inspection Point: Quality Control Activity - Isolate Pump 4 Electrically & Mechanically and release any residual pressure.
9f00f97d-b5ce-541b-b0c4-af0c5f276496 | note | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
4832ed76-4694-5830-a3ca-0366237e41fc | note | Verifying Document - Advice from DCC Operations
7e493aa2-6745-5056-80e3-821b3d8ca3bc | note | Frequency - Once
9ebe625a-4490-5694-9107-c7d0807cf1f0 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
681c2045-bc4a-54fa-8303-d58cb30f83b5 | note | Inspection: Key - C
f751c61b-a1ae-50d6-9ef2-5da359df8606 | note | Inspection: By - CR
af964c71-047c-45f7-b405-4cf8565f1c60 | checkpoint | 4.2 - Remove Pump 4 base plate - This may have to be cut into individual sections to accommodate each pump
99f2cf24-fb48-520e-9ffa-73ffc20149b3 | note | Inspection Point: Quality Control Activity - Remove fixings from floor
9d6ff32c-9a02-50be-9354-a1b8693f3680 | note | Acceptance Criteria - Pump 4 is removed
dd13b3b1-1095-56e5-8159-df5e338fccf1 | note | Verifying Document - This ITP
31d4ee74-9566-52a4-9205-3257c230c30d | note | Frequency - Once
c298abb1-3495-5f95-a40f-0c1e263584eb | note | Inspection Type (Visual, other) - Visual
3d2688fa-a663-52ce-a8a5-5e75eedba233 | note | Inspection: Key - I
69bd76bf-b337-56fe-93a2-7ce864ecb75e | note | Inspection: By - IP
4abbc79f-de6f-4ec2-9edc-6803587adb81 | checkpoint | 4.3 - Install New Proprietary baseplate for Pump 4 - This may have to be cut into individual sections to accommodate each pump
cdd15203-77d1-5663-8b2e-2b525e125c27 | note | Inspection Point: Quality Control Activity - Check dimensions
af9dfb88-1dc4-58a4-be22-ed090ac9f089 | note | Acceptance Criteria - Plinth is in suitable condition
324604e3-8b5d-5ad1-8857-f9192143a273 | note | Verifying Document - 1.Grundfos documentation.
0f16855c-ca6c-5f32-8d50-2035aedd0ac6 | note | 2. Project Drawings
5082118d-b524-5e65-aba1-eca307905516 | note | Frequency - Once
0d23b1b8-5853-5b16-96d1-643e6e03ce19 | note | Inspection Type (Visual, other) - Visual
be7ae0dc-c7ba-5642-b585-4cdf72df3e1e | note | Inspection: Key - I
9be51044-8354-51d2-84ea-9468edfd369c | note | Inspection: By - IP
eb5cc1be-55d3-462d-b11a-2732f51b6650 | checkpoint | 4.4 - Pump 4 Installation
4ed7ce1d-bee9-5191-8b7c-54a7e99f29e8 | note | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 4 into position & bolt down
b99f1ef4-1836-554e-b8d0-360934987ae1 | note | Acceptance Criteria - Pump base plate mounted in correct position
e46ad62d-8508-5269-a40d-804f1abbee34 | note | Verifying Document - 1.Grundfos documentation.
479627a8-c2bb-5f90-b4f0-431a974d32ff | note | 2. Project Drawings
fb9dfbbb-f765-5a61-b032-5df640b4fc14 | note | Frequency - Once
d869119b-aa67-5c56-a90a-d2619bfbe043 | note | Inspection Type (Visual, other) - Visual
80dcad7e-da46-5255-8a9b-0f77f89c0f30 | note | Inspection: Key - I
f50ebd6c-7e03-5c56-961f-5d2bccf19a5a | note | Inspection: By - IP
dfcd351d-f3bc-46de-8675-d4eeaa23ec68 | checkpoint | 4.5 - Install gaskets & dress sets
53c666f7-e9f4-5158-a366-21b1f777f8fd | note | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
cbac96cf-0b87-51c7-ae6c-b5698329c275 | note | Acceptance Criteria - Torque to 80N.m
c76bd839-1a23-5e25-893e-d2c4843fc6ef | note | Verifying Document - NZ Water Standards
e3981f8b-3f1b-546e-8611-5f26546697f9 | note | Frequency - Once per bolt
dc1636a9-d77e-5271-89ec-3fd0abaa1f67 | note | Inspection Type (Visual, other) - Visual
5bfcd2ce-fd48-5d9f-866b-f46441e5e663 | note | Inspection: Key - I
3650e55c-4588-5ed6-b889-0854a69fad68 | note | Inspection: By - IP
957a9bfd-c01d-449c-925b-acb5bba5a319 | checkpoint | 4.6 - Preparation to run Pump 4
a89fdcc3-08ba-54d6-bc24-06c3b37d1837 | note | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
5118ae56-759e-55a9-9bb8-31c6ba961550 | note | Acceptance Criteria - Water visible from purging valve
704e2f01-ca7d-530f-b5c5-8576b7607261 | note | Verifying Document - This ITP
9faf94d9-7ba2-5dec-aa38-239c1b9e5007 | note | Frequency - Once/per pump
158c97dd-80b4-549b-820e-d48de51c86d9 | note | Inspection Type (Visual, other) - Visual
de4dae17-0aa0-52a2-ab50-df588d8aacd5 | note | Inspection: Key - I
7f0c48a1-74b0-5e97-a6c7-ec5ff1c1b582 | note | Inspection: By - IP
f181440f-51ce-4d54-99fe-029e6c174179 | checkpoint-no-value | Note:
2e3f3ec1-9a23-535f-98f4-9aa7bd084bfd | note | Electrical connection of pumps and commissioning are covered in separate ITP's
bdb6209f-fd73-48c7-b730-74aa72de0984 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
9b86c755-b348-4e48-b2c6-10adc6514f6e | checkpoint | 5.1 - Pump 4 Changeover Complete (Mechanical)
ddec7c04-b958-5c21-b029-ed09bb57367f | note | Inspection Point: Quality Control Activity - Check for any leaks
be0d986f-05ca-5b14-b454-0b6f906e3cb8 | note | Acceptance Criteria - No visible leaks
39920f65-34d3-54ee-8fbb-58d7cd691edb | note | Verifying Document - As per methodology
f583b24d-b4fc-5f00-a0b3-b389a3639e9f | note | Frequency - once
532559f5-1708-5245-a3cc-a46a7ad6325d | note | Inspection Type (Visual, other) - Visual + Document
6c3b7b02-b53c-56a4-8889-8242a6e82047 | note | Inspection: Key - I
b3521020-574a-5106-9fb4-511649747fd6 | note | Inspection: By - IP
35fc928a-565a-4881-87a3-7885386685a2 | checkpoint | 5.2 - VFD 4 Changeover Complete (Electrical)
24b7206a-4fd0-57e2-a994-5646bbd81942 | note | Inspection Point: Quality Control Activity - Power to VFD4
ee551a4a-d7c1-5b80-b128-c24d95c391b2 | note | Acceptance Criteria - Completion of VFD4 ITP
f00b377c-9fb0-514f-a1c9-b42368257f3f | note | Verifying Document - 561483-ITP-009.4
a563411e-1fcd-5154-9fd1-73245134869c | note | Frequency - once
509a2ea5-880d-5fcc-9eef-9a35bff1b5d0 | note | Inspection Type (Visual, other) - Visual + Document
59ce6842-3c1f-5332-9788-428ce6638245 | note | Inspection: Key - I
02ec3eb7-bc5b-55a9-b809-2af279ab18eb | note | Inspection: By - IP
ba547a2e-4d5c-4e7e-9d0e-ffd460a75201 | checklist | 561483-ITP-008.5 - Pump 5 Delivery & Installation | itp | 561483-ITP-008.5 - Delivery & Installation of Pump 5
a4a254d0-64a4-44c2-affa-42cc9d94b307 | section | SECTION 3 – RECEIVING INSPECTIONS
24097cf8-342b-41d8-a174-61adabb2cc98 | checkpoint | 3.1 - Delivery of Pump 5 to site from Downer storage facility
76995106-adad-52e4-a6c1-36a838755ea0 | note | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
25abd283-021a-5b62-ab20-92c31b7b5bb8 | note | Acceptance Criteria - Pump is damage free
ad7ebdbe-7367-5343-9663-f3b6bc77864d | note | Verifying Document - 1. Pump delivery docket.
cede8d73-33ed-577a-82a8-85dad6b2d1dd | note | 2. Pump storage ITP
10e9aaa2-7f33-5e05-9780-c54b6e418074 | note | Frequency - Once
f6d94bdb-2d76-5763-b325-971429ccac8b | note | Inspection Type (Visual, other) - Visual
54ac1953-c423-5caf-93c6-868d7b8ab5fa | note | Inspection: Key - C
69985a66-8d5a-599a-8868-22539a559707 | note | Inspection: By - IP
fd7b36e2-6088-4f22-a52b-417c39a37268 | checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 5
d3463047-583f-5b90-803c-330219e3f0f9 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
b2ab4b4f-f4c2-5988-9db4-c595048bb7a4 | note | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
d240532c-506b-5018-a940-893bc2426363 | note | Verifying Document - Written approval
a899247a-2d5f-5d95-8d76-c41b90c94831 | note | Frequency - Once
02f347dd-f241-5d13-b750-7f9f6a21111d | note | Inspection Type (Visual, other) - other
b065f21b-b2e8-52a8-9276-0b4fc44fe40f | note | Inspection: Key - R
6bac6cf8-aa87-5f2d-a996-7c87082a11e2 | note | Inspection: By - CR
3ff75e75-90d2-4a12-a2e1-c0205d18d2ac | section | SECTION 4 – IN-PROCESS INSPECTIONS
cdff47c5-9d16-49cc-93d4-455fb6aea6bb | checkpoint | 4.1 - Shutdown Pump 5
1323871f-e64b-5673-87f5-1f46031d12ad | note | Inspection Point: Quality Control Activity - Isolate Pump 5 Electrically & Mechanically and release any residual pressure.
dc2c6d9d-0def-5ff1-84ac-13408076d27a | note | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
ae052af7-3db8-5099-a44a-6f64ea45ce1d | note | Verifying Document - Advice from DCC Operations
1b69715b-bb91-5690-8c1c-b08582646c6a | note | Frequency - Once
2ab6964b-5a0b-57f9-9da9-1c21c603e3d3 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
ba0de72e-ee17-58d1-ba35-7497f3769c67 | note | Inspection: Key - C
2121d1a0-fef5-513b-9703-29f1ad417ef6 | note | Inspection: By - CR
8e31e1ef-7ef4-49b2-9d07-bd58def3a67d | checkpoint | 4.2 - Remove Pump 5 base plate - This may have to be cut into individual sections to accommodate each pump
9b7ffb00-373a-5431-b97f-686706df9ad7 | note | Inspection Point: Quality Control Activity - Remove fixings from floor
27a77b57-4547-57e4-b597-fc87e8e34087 | note | Acceptance Criteria - Pump 5 is removed
c4a66dba-8825-5bd2-81da-e9853e13d630 | note | Verifying Document - This ITP
7449fb96-3f7e-580f-b2d5-825d1a2ef283 | note | Frequency - Once
73b105c2-0279-58ef-9ef8-cbc33ae0ceb5 | note | Inspection Type (Visual, other) - Visual
ee8dcc05-968b-5604-92fb-383da1756054 | note | Inspection: Key - I
4343ec6b-6832-5eac-816a-40f4b47038e1 | note | Inspection: By - IP
3084e52b-a713-42e5-9fd0-62299df32205 | checkpoint | 4.3 - Install New Proprietary baseplate for Pump 5 - This may have to be cut into individual sections to accommodate each pump
b73b26ea-b0cf-5b53-b06d-d9cc239bc2af | note | Inspection Point: Quality Control Activity - Check dimensions
a1a26f0d-917f-5396-b6cb-724f5c2f615e | note | Acceptance Criteria - Plinth is in suitable condition
5294ddb3-a81d-5c36-a1fe-e55126d6cd0e | note | Verifying Document - 1.Grundfos documentation.
d1563f19-a667-51f0-90b3-1973cc6b37b3 | note | 2. Project Drawings
16055b56-c826-5b24-b2e3-5e26513f7a64 | note | Frequency - Once
2f5dc9c5-32fd-59ce-8284-3e985b010fa4 | note | Inspection Type (Visual, other) - Visual
90a0d007-028e-550c-a441-fdbd685d9ba5 | note | Inspection: Key - I
a08cb046-fdca-5031-8bf8-301995610b08 | note | Inspection: By - IP
3d916e4e-a833-4721-810b-3c7156c1032d | checkpoint | 4.4 - Pump 5 Installation
c6902efb-1735-5aec-817c-8ea6249c720d | note | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 5 into position & bolt down
fc452dde-f8fc-56b7-ab14-39f9d978dff4 | note | Acceptance Criteria - Pump base plate mounted in correct position
e9510b64-5d1e-5fe2-99be-4df8d9850201 | note | Verifying Document - 1.Grundfos documentation.
800dc769-4ebb-5ff8-bc11-152a51a4af6e | note | 2. Project Drawings
2990d87d-9292-501c-9cb7-0179b9300641 | note | Frequency - Once
fd495a01-aeab-569c-923d-c07e1df38723 | note | Inspection Type (Visual, other) - Visual
e4a3095f-1f54-5a8c-8579-368a4b942287 | note | Inspection: Key - I
29fa618a-4446-513e-a67c-e7e6aa09c9bd | note | Inspection: By - IP
acc1c913-0b46-41cc-8dfc-65c3cdb673cb | checkpoint | 4.5 - Install gaskets & dress sets
5f78ebb5-6239-55fd-b624-43aa0df4c0a1 | note | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
1a926416-8175-545d-b068-05da5c1f51a9 | note | Acceptance Criteria - Torque to 80N.m
4581ce5a-f604-50da-8b0e-c4b88b1c068c | note | Verifying Document - NZ Water Standards
3b1e4e8b-01ce-56a0-a107-a2a041dab39d | note | Frequency - Once per bolt
4ad3549e-91d5-5698-9fc5-785d77e02eaa | note | Inspection Type (Visual, other) - Visual
45b59af7-6e08-5725-bd4c-d72f293cf0aa | note | Inspection: Key - I
4fee23f7-709f-57bd-8679-3e0d00e6ff46 | note | Inspection: By - IP
d1db7246-7b00-4461-bdd4-872b4d2f3728 | checkpoint | 4.6 - Preparation to run Pump 5
56ac602c-bfd7-544b-b6a4-7bf64387ae2f | note | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
3fd2a4b8-98d8-524d-b5bd-75461380208e | note | Acceptance Criteria - Water visible from purging valve
98e455ae-0408-55aa-9426-e22255804e2e | note | Verifying Document - This ITP
e5085b01-f254-571d-9753-c53d567b87ae | note | Frequency - Once/per pump
2c56c4d6-6d77-53d8-981c-889282429950 | note | Inspection Type (Visual, other) - Visual
74743664-0b0d-5359-a14b-f7db07352b0c | note | Inspection: Key - I
4ccd4009-aa1c-595c-b6f0-ddd03676fc66 | note | Inspection: By - IP
32c08a21-5638-43d2-95d5-15f11d938099 | checkpoint-no-value | Note:
21ee066d-0ac6-550a-b7c8-4302561d32d4 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
bea33857-3f2d-4c67-a1eb-df7cfa7bdcd0 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
dc6f5d04-c2dd-4902-9afd-1a5f03817c3e | checkpoint | 5.1 - Pump 5 Changeover Complete (Mechanical)
668ee09a-b629-523c-a6d6-27c168233753 | note | Inspection Point: Quality Control Activity - Check for any leaks
55e0bedf-91e8-5bfc-afff-f809357b979b | note | Acceptance Criteria - No visible leaks
31eae9aa-801f-5e32-ab93-059d3bfa6d77 | note | Verifying Document - As per methodology
1e68911d-8c08-5258-a233-660d4b691048 | note | Frequency - once
f1d16031-ff42-50da-afd1-b9491cac09cb | note | Inspection Type (Visual, other) - Visual + Document
be5ad1b8-97a7-5c8d-ad24-d20182e3c029 | note | Inspection: Key - I
356bdd1f-9e01-5487-8323-1529a6dea15b | note | Inspection: By - IP
098ef213-3537-4c33-bd94-8a3015f3bf4b | checkpoint | 5.2 - VFD 5 Changeover Complete (Electrical)
be921ace-b255-5485-87b0-c6c9866024d0 | note | Inspection Point: Quality Control Activity - Power to VFD 5
b7f51633-62c8-513d-943c-82c9da70a8b9 | note | Acceptance Criteria - Completion of VFD 5 ITP
f98c2e2b-b1f1-599d-9261-ddad6f740a32 | note | Verifying Document - 561483-ITP-009.5
319f389b-f1b5-5872-a5d8-3b00cdb15dee | note | Frequency - once
c70a494a-bda7-5523-8a1b-24b5212c97e4 | note | Inspection Type (Visual, other) - Visual + Document
3616b3fc-13d0-51b9-9641-2beb48447076 | note | Inspection: Key - I
83a4acf3-2953-52c0-8495-29df77e7f56c | note | Inspection: By - IP
a5205d41-ef96-43cf-8adb-5e7493ef8a33 | checklist | 561483-ITP-008.6 - Pump 6 Delivery & Installation | itp | 561483-ITP-008.6 - Delivery & Installation of Pump 6
8ea632ab-e359-4c51-82e0-e2370710e60f | section | SECTION 3 – RECEIVING INSPECTIONS
2d78b075-724e-45ba-b894-eb01972e3f78 | checkpoint | 3.1 - Delivery of Pump 6 to site from Downer storage facility
1e2b58c7-fdd1-5546-bce8-b80923e3a15b | note | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
237b6a2b-7774-5ac1-ac0a-9358d5e23551 | note | Acceptance Criteria - Pump is damage free
04f645cc-523e-5f3f-b4c1-10612deaf562 | note | Verifying Document - 1. Pump delivery docket.
62e29b10-30f4-582d-a058-3d11ceb1a507 | note | 2. Pump storage ITP
bafa442f-8b5e-5ef8-a661-4ad8ea7c57cb | note | Frequency - Once
65f97d92-4398-56a7-8a58-2b35365162cf | note | Inspection Type (Visual, other) - Visual
6965e88c-9596-5e1a-989b-475464f66a90 | note | Inspection: Key - C
dda4f4df-4eea-5df3-a2e4-9365d028dc75 | note | Inspection: By - IP
b4d85d8a-456d-4b12-8425-4d2cb74076d1 | checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 6
3f26ffac-a7ae-594c-a712-d756b8232b14 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
80d78d92-5cbe-5fa0-9edb-ffb02ed21e6b | note | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
7d1d9ce4-8b61-59ee-9148-26d2008dbcb7 | note | Verifying Document - Written approval
dfb1a5f2-374c-51a6-9fd4-4ff7cef013a7 | note | Frequency - Once
a15cd53e-b346-5d6e-b5aa-27246b75cea0 | note | Inspection Type (Visual, other) - other
019c121b-fc5f-548f-8d42-8297f097dc40 | note | Inspection: Key - R
e1101a0b-2b56-535d-ac82-b9f909c60989 | note | Inspection: By - CR
024036c1-de52-4892-9f4d-6731a20fafc1 | section | SECTION 4 – IN-PROCESS INSPECTIONS
227013e7-9347-4183-9b84-b01bd58c4d4c | checkpoint | 4.1 - Shutdown Pump 6
c4d359e2-3d9f-51e3-a055-af1f3f8d5db9 | note | Inspection Point: Quality Control Activity - Isolate Pump 6 Electrically & Mechanically and release any residual pressure.
dba2a162-1dd8-500d-9960-e30b60fa7e06 | note | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
c4c2f35f-137f-539c-834a-bcc742b9efde | note | Verifying Document - Advice from DCC Operations
a322744e-a84d-5085-8ee2-22cbce336abc | note | Frequency - Once
12a8949e-0a35-5f12-92f3-a5aadb83db37 | note | Inspection Type (Visual, other) - Visual + Written + Verbal
0859c7c8-5ef9-5a47-97c8-d4ecb143facf | note | Inspection: Key - C
13c4bf99-421b-5f58-a1f8-9e868627c070 | note | Inspection: By - CR
7056dcb3-7bae-4167-b65c-020970003dd5 | checkpoint | 4.2 - Remove Pump 6 base plate - This may have to be cut into individual sections to accommodate each pump
5cd6a8da-80ea-5209-8981-4fccd56ba4c0 | note | Inspection Point: Quality Control Activity - Remove fixings from floor
aaa987f6-1e93-5ed4-bce8-25e348f29a8a | note | Acceptance Criteria - Pump 6 is removed
1fba94c8-50d7-5795-bf14-3cef2a0eaa30 | note | Verifying Document - This ITP
4c41a553-c624-504f-b883-74fca464c150 | note | Frequency - Once
0c31b806-ec10-5f4d-8b67-d5dae7704239 | note | Inspection Type (Visual, other) - Visual
c9e208a6-1cdc-5efb-943a-730ea7e75a1b | note | Inspection: Key - I
e02b4eef-9ebc-5afc-a08d-57d385f40085 | note | Inspection: By - IP
d3c1548d-74d6-48f5-96da-49b8dcb2d801 | checkpoint | 4.3 - Install New Proprietary baseplate for Pump 6 - This may have to be cut into individual sections to accommodate each pump
d8fe9274-33db-5e45-a45e-7f8e8c9ccbe2 | note | Inspection Point: Quality Control Activity - Check dimensions
868b44c1-2bab-50fc-98bc-8052d8c3a225 | note | Acceptance Criteria - Plinth is in suitable condition
2b62e34c-241e-50f6-be64-296cdaf46663 | note | Verifying Document - 1.Grundfos documentation.
d5e5c865-fb78-5ab1-9899-524b1fc7f011 | note | 2. Project Drawings
67e0913e-0d4e-5743-ad90-7e915b8473ea | note | Frequency - Once
7edf8ffc-6a0b-5772-b650-aaf52d0da20f | note | Inspection Type (Visual, other) - Visual
94ba9905-7ea5-5a14-9aa3-e609881c9cfa | note | Inspection: Key - I
9049a10f-b929-52da-ac27-f39d0dac3cee | note | Inspection: By - IP
7d9704b4-08e5-4a8f-a2db-220fdd7ba1a2 | checkpoint | 4.4 - Pump 6 Installation
d2b08b9a-afed-5a47-88ab-f3698bf8fb34 | note | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 6 into position & bolt down
31ecc995-c52e-5564-b3ea-587c66720cf2 | note | Acceptance Criteria - Pump base plate mounted in correct position
b828517d-6d49-54de-a3ea-74d6bdbb5c1d | note | Verifying Document - 1.Grundfos documentation.
2c9b8ae4-e868-5f17-b247-2fb180224dbe | note | 2. Project Drawings
39f7481e-1b15-5537-9e51-abe04134a078 | note | Frequency - Once
003d1f4a-f960-51a0-94f9-9dd312cfbe21 | note | Inspection Type (Visual, other) - Visual
986b4c48-9be7-5efa-991c-09de2c8ca296 | note | Inspection: Key - I
b2853116-aa50-50f8-a7fa-3fa5445dfc2c | note | Inspection: By - IP
65691c14-94a3-4f60-8f96-974ce7152fe9 | checkpoint | 4.5 - Install gaskets & dress sets
e47b5441-848d-591c-a1b5-4b3894b83a65 | note | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
cbc774bb-f359-59f8-aef5-cc9c0fa4c37d | note | Acceptance Criteria - Torque to 80N.m
16085b89-1136-5fa2-af10-cdc9628a75ec | note | Verifying Document - NZ Water Standards
4489f468-e327-5393-a1dd-2c9abf0c958f | note | Frequency - Once per bolt
244090eb-f243-557f-96db-ca502a75ca96 | note | Inspection Type (Visual, other) - Visual
0f7c1be7-ebbf-5ba1-acf8-36328d1353a6 | note | Inspection: Key - I
0be16bb6-da34-5cde-bdd2-2a3dd3311f4b | note | Inspection: By - IP
98e888a8-0088-43d1-b49e-8d1ed2b2f6d5 | checkpoint | 4.6 - Preparation to run Pump 6
a0f435e5-90f0-5d59-a092-d2d034f37b3c | note | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
d3f612f6-239a-5e59-9a27-0ea2d0bdacc8 | note | Acceptance Criteria - Water visible from purging valve
60eb66a2-c4b1-5677-b8c2-a9a0490341e5 | note | Verifying Document - This ITP
668e9ef5-e259-5240-baf6-757be29dc46c | note | Frequency - Once/per pump
2b3f27c8-0d82-5626-bb33-0274273ffcfb | note | Inspection Type (Visual, other) - Visual
c51ce6c4-be69-50d7-a12f-5325acd710d1 | note | Inspection: Key - I
857091a4-7772-5a49-94dd-fea8c03e0f66 | note | Inspection: By - IP
ce6241bf-c2ee-45f7-bd8d-a722a5060a89 | checkpoint-no-value | Note:
a7b395b4-5b55-579e-a52e-999b8d486fd2 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
17ece18e-b1dd-4395-8a46-1a780728df53 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
6188351d-6894-42de-9ade-795dd4292d4f | checkpoint | 5.1 - Pump 6 Changeover Complete (Mechanical)
81d2bc9d-a007-5015-8cb0-323683c29d66 | note | Inspection Point: Quality Control Activity - Check for any leaks
87923c84-2aac-5360-9fc6-d8b8ce368e30 | note | Acceptance Criteria - No visible leaks
997943a1-94bb-5a0e-9e8b-010be97705c7 | note | Verifying Document - As per methodology
23204398-9b8f-5a91-a636-be28e97d5345 | note | Frequency - once
e22f00f6-d31d-50b6-8322-2acaf1864ff4 | note | Inspection Type (Visual, other) - Visual + Document
6cd549f8-135f-5967-9909-d2871465dfb8 | note | Inspection: Key - I
80dc5c5c-b770-5e75-be94-9144fe55200c | note | Inspection: By - IP
25b8448e-351b-4d6e-9018-29c184f12d11 | checkpoint | 5.2 - VFD 6 Changeover Complete (Electrical)
c733c5dc-eb92-5829-87a4-9c6a0a48945c | note | Inspection Point: Quality Control Activity - Power to VFD 6
52760583-e3fd-583a-a45d-5a3212f57681 | note | Acceptance Criteria - Completion of VFD 6 ITP
fd8a9622-8c65-535c-8896-1b949c86baa0 | note | Verifying Document - 561483-ITP-009.6
90f960e0-3eae-5860-b8d6-1e9e707845df | note | Frequency - once
e675c5b2-292d-59e2-8daf-08f0177be0ed | note | Inspection Type (Visual, other) - Visual + Document
d6358b2c-274e-566c-8fd3-02de729a039d | note | Inspection: Key - I
992c7e99-91d9-5a04-943d-c2ae0d642b9b | note | Inspection: By - IP
ec893953-ee81-411f-9b79-f843dfd563ca | checklist | 561483-ITP-009.1 - VFD 1 Delivery & Installation | itp | 561483-ITP-009.1 - Installation of VFD 1 (Pump 1) - Inspection Test Plan
68139522-04e1-4abf-a516-946267fe76db | section | SECTION 3 – RECEIVING INSPECTIONS
c09a5a1d-9c24-4e10-87ed-19f9df2ef620 | checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 1
8e69b29f-ad0e-5305-8a59-fb236f0f0a78 | note | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
4545a58e-b9b7-5db7-9e82-3e54debbd581 | note | Acceptance Criteria - VFD is damage free
895bcf0b-d890-5388-87ce-ca0da877c5e9 | note | Verifying Document - 1. VFD delivery docket.
f684f3e6-5488-5c39-ba71-b61797850fbe | note | 2. VFD storage ITP
f7c1b5e3-b2fc-5ed4-9efd-237c870c0472 | note | Frequency - Once
06dc3613-103c-5535-bd85-5e609b08163e | note | Inspection Type (Visual, other) - Visual
b683b058-bc80-51cd-91e0-1c42ebfcfaab | note | Inspection: Key - C
26fff231-e8c1-5a9f-87d9-9441a48656be | note | Inspection: By - IP
558a6146-e547-4170-92b2-a532f026d5b0 | checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 1
dd5629be-f8a0-5c8d-bbae-53a0cf5bd181 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
b8b8b661-e92e-5696-8807-e16badbf3718 | note | Acceptance Criteria - Approved Products list and approved for use
9170e7f4-e5fc-589c-a707-2be9a347c2e5 | note | Verifying Document - Specification - Approved Materials list
f118251a-2af8-560f-81eb-a80399a82014 | note | Frequency - Once
9bc20e92-b257-5fa2-aa1a-d1b5ae547161 | note | Inspection Type (Visual, other) - Visual
a9170c7a-97a0-5d2a-96fe-16c47bfda78f | note | Inspection: Key - C
99d00a41-b5e8-521e-a64b-10ec4634cf5f | note | Inspection: By - IP
5ecf13b7-1ba0-4782-893c-020ab7a5c58e | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
66b7feb6-0b68-532a-bcef-74113743400c | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
517fbdbc-5c8a-5f50-b90f-fccc00aede5b | note | Acceptance Criteria - Upon approval from Client & Engineering team
ea189b0e-17a3-52b4-a33e-536873b722c7 | note | Verifying Document - Written approval
9f134654-30f4-5cb0-b5a0-184dab03385c | note | Frequency - Once
960cdb82-c6f9-5863-9892-4c82520117a7 | note | Inspection Type (Visual, other) - other
f44f13d2-aacb-5c57-b800-243416171175 | note | Inspection: Key - R
3a64de07-c6a6-5335-83e3-0d9d18a0dc26 | note | Inspection: By - CR
dada7578-71c4-4f02-a356-67b1df885022 | section | SECTION 4 – IN-PROCESS INSPECTIONS
1f0788bb-45c2-450b-a618-69f17d7a971e | checkpoint | 4.1 - Electrically Isolate Pump 1 at Control Cabinet. Ensure no issues with Grundfos Controller.
f83b8ec6-a7ae-5fbc-8af4-48e949660bfd | note | Inspection Point: Quality Control Activity - Isolation is applied to Pump 1 and existing VFD
7d683367-3efd-5c97-8eb1-96eea4d96fa3 | note | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
6e6ee5e5-3996-5c49-9d4a-1fb61feadd61 | note | Verifying Document - This ITP
716ee829-d19b-5cac-a8f0-06941d018b82 | note | Frequency - Once
77a4a7dc-a604-58e8-b190-1febaf4ae615 | note | Inspection Type (Visual, other) - Visual
2fc3a9c5-5909-5ab2-9843-b4a56ca12024 | note | Inspection: Key - I
3268483f-b218-5225-929d-3f0bb02adc1d | note | Inspection: By - IP
c5fd38a1-dff4-45dc-9013-317a65db8ccb | checkpoint | 4.2 - Electrically disconnect Pump 1
5a65676b-c66e-592c-a160-eb3ad3698ebb | note | Inspection Point: Quality Control Activity - All electrical connections are removed
92ffcea6-2318-5959-85ff-95801de5757c | note | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 1 disconnected, no voltage on cabling.
ce9312aa-ba83-5b3f-80b1-daca833c9c95 | note | Verifying Document - This ITP
c7b7b097-05c4-59e7-8535-3679400371c5 | note | Frequency - Once
5d4af4f8-062a-5b83-b45c-7bedcd525168 | note | Inspection Type (Visual, other) - Visual
f7e43655-bb97-58f9-b6c3-8cf15f7df292 | note | Inspection: Key - I
34d3d42e-7a47-5cc9-9ca1-ed290101369f | note | Inspection: By - IP
298763da-7fad-4562-b289-abf97aa19bcd | checkpoint | 4.3 - Remove Pump 1 Cable from Motor to VFD
036bd3b2-8d14-59b6-b15c-9f262bd33fa1 | note | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 1, Cable Removed From Support System
057a574f-9c42-5286-9b52-d80e9e0cf1b8 | note | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 1).
46045afb-9969-5978-837d-707dd6738c68 | note | Verifying Document - This ITP
633d7789-a81f-5794-b6ed-733004b618de | note | Frequency - Once
5ef1b81f-3b1e-56c2-9b38-0514b4a44bc6 | note | Inspection Type (Visual, other) - Visual
c9265030-ccac-5925-9b3b-0ccf2133d7cc | note | Inspection: Key - I
49c54ffd-b70c-53bf-bd53-56aefe2b32bb | note | Inspection: By - IP
686d39ff-1d48-456b-a5d4-79a6b2d985fc | checkpoint | 4.6 - Remove Pump 1 VFD
b5056d95-6e56-508b-b02a-33b58e609c91 | note | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
732e53ed-291e-5507-907f-4031b8ce4098 | note | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
018a833c-378f-5fd5-bbf3-4f6de410757f | note | Verifying Document - This ITP
aa525eee-88b1-5c7d-a529-3d8243112236 | note | Frequency - Once
2665c34c-a990-5011-96ba-a307b35e6feb | note | Inspection Type (Visual, other) - Visual
84eca65b-0e45-56f7-8798-40217f87d870 | note | Inspection: Key - I
592fe601-770a-5ded-8f39-b91ed244bf5d | note | Inspection: By - IP
2d7ef872-9b97-4ee1-9634-0205df9d48ec | checkpoint | 4.7 - Mount new Pump 1 VFD
993afcd8-0d18-567d-81a3-153c54a3d8bc | note | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
1ed4c174-5868-5c13-8180-ed8ae01b95e1 | note | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
f7911cf2-3b53-540e-bfde-26cf094c66ae | note | Verifying Document - This ITP
f3a145c3-aad6-5dbc-9e93-230d03bed585 | note | Frequency - Once
6b6aaf09-50c3-5fdb-a671-bbe6ba2e1ee4 | note | Inspection Type (Visual, other) - Visual
0fc75913-6e98-5822-8555-8557b88a293c | note | Inspection: Key - I
60ddffda-0319-5dc4-a8e6-58e2a5187e44 | note | Inspection: By - IP
116d2518-f13f-403c-8953-02d442990ad7 | checkpoint | 4.8 - Remove VFD 1 Feed Cabling and Isolators
5352c32a-f227-5f66-896d-90135b982a3b | note | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
09709edd-5bd1-5d7c-b580-5df3c998e55a | note | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
64ccb3a3-5f3e-5a3f-aeca-4c09fe9c3a65 | note | Verifying Document - This ITP
b8a9dd18-3839-52de-828a-ecabd38f1907 | note | Frequency - Once
75660eba-3526-5ec0-97e1-5eb275b008b9 | note | Inspection Type (Visual, other) - Visual
d13fe3d0-9fe9-5356-b895-f5d64abbb653 | note | Inspection: Key - I
552f2f50-0c33-5382-b34d-e0fa7ee029f0 | note | Inspection: By - IP
d06517cd-b18b-47c5-b7d4-d9d2b4c0ac8d | checkpoint | 4.9 - Install new supply cabling and isolators for VFD 1
ba91aab5-4dbf-5d73-a6c6-b85e532cb47b | note | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD1 is prepped and tested
f6a83932-3c96-52f3-b022-ee0b28e0e20b | note | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
16b419f6-b4ac-528d-8d76-428cf8409967 | note | Verifying Document - Cable Test Sheets
460c9bcb-00a7-5ae5-9ba4-12f5e7008a25 | note | Frequency - Once per pump
3fb70269-8df4-5aec-b796-d586eb81b48c | note | Inspection Type (Visual, other) - Visual
61eb6bf5-59d6-5c8e-86e3-69b9ae8adbe4 | note | Inspection: Key - I
4aa588f0-034b-5e6e-8fd9-3089716672ce | note | Inspection: By - IP
9a2d8bc7-2ebc-4216-a1d9-3c18e742351b | checkpoint | 4.10 - Terminate Cabling for VFD 1
406fb975-8941-507f-9c96-2961c238c685 | note | Inspection Point: Quality Control Activity - Cables fitted off into VFD 1 isolators and supply cabinet.
774935ed-7472-5a7a-a02b-94f6c7605a68 | note | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 1
7cd29bad-64a1-5ab7-af0d-0159014a2a90 | note | Verifying Document - Cable Test Sheets
df4dde27-9c19-515b-ae10-1b932a801708 | note | Frequency - Once per pump
00e25019-73df-5ee7-b5bb-9606d1a7fdb6 | note | Inspection Type (Visual, other) - Visual
feb058b7-be45-5ff3-b432-a79b5e33ecb7 | note | Inspection: Key - I
44171fa0-84fa-592e-a515-a3d6acf128e3 | note | Inspection: By - IP
24ec2148-56a6-4852-b75f-19160dfc58f6 | checkpoint | 4.11 - Remove isolations
be1d40dd-86e3-5eb3-8ce9-cff0ca620df6 | note | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
0d6be95e-9baa-5f74-9731-ffbfb03ccb48 | note | Acceptance Criteria - isolations removed circuits re-energised
1361aad9-06da-5562-b89c-0a9786965bd4 | note | Verifying Document - Lock-out Tag out Register
75b796c9-497b-5249-b0c9-320927599cd3 | note | Frequency - Once per pump
c85e8b2a-81ff-5c5f-a07d-3ef037269340 | note | Inspection Type (Visual, other) - Visual
32ba9a75-0e46-507d-a550-fabfa4674555 | note | Inspection: Key - I
252af308-46b6-53cf-92f6-ae617de9b04b | note | Inspection: By - IP
d2ab1d79-d567-4b13-84c6-3e4c1fd64d3f | checkpoint | 4.12 - Configure VFD 1
17c0a897-6a67-5a53-bc8e-a4cbf837cd0d | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
f4a5c449-31ec-52f2-9340-95204ccc1963 | note | Acceptance Criteria - VFD configured correctly, controller setup adjusted
a9d7cc5f-86ad-5bb0-aa71-35c0b0019238 | note | Verifying Document - VFD test sheets
2712c7f4-23af-5894-a423-71e4dc73ea07 | note | Frequency - Once per VFD
e3fdcc54-ed53-5a8a-80cd-4e2b3af36fe7 | note | Inspection Type (Visual, other) - Visual
c284de06-0284-5d62-8bcd-4e0cd70a9f9c | note | Inspection: Key - I
471bebd7-37ba-501b-b6a8-31f073350921 | note | Inspection: By - IP
5b135d14-2cf8-4bd1-8b40-081bc7f53d9b | checkpoint | 4.13 - Confirm correct operation of VFD 1 and pump
bf5383e9-a5f1-5afd-a1d4-12792b32bbb0 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
410d45f5-9bab-51ec-ad8a-cf95fc710945 | note | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
c75f6f9a-0feb-507f-b90b-faf528bbb935 | note | Verifying Document - VFD test sheets
b35373b3-6339-5cfe-a73c-f3261206ff12 | note | Frequency - Once per VFD
b4b92216-9b1c-5ff8-b668-47984a971f95 | note | Inspection Type (Visual, other) - Visual
181080d5-9d8a-5fb1-bb7b-697c1a9b9c3a | note | Inspection: Key - I
963d146c-189c-5f4c-a014-bff20acee913 | note | Inspection: By - IP
088a8518-3d01-4552-bf52-31a2e61a7d9a | checkpoint-no-value | Note:
69d54686-093c-5752-b86a-14de7b7cd511 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
31b46042-712b-4e53-94d5-165faa6ed921 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
b48ea4f7-f111-4da7-ab76-ff4c3b58cf3b | checkpoint | 5.1 - Stage 1 Changeover Complete (Mechanical)
d4fa3fbb-0c1e-5b97-a6fa-9f7b341fa675 | note | Inspection Point: Quality Control Activity - Pump 1 in service
e985c447-2f46-52b8-ad7f-da90997bcdba | note | Acceptance Criteria - Pump 1 is installed. Valves installed to Pump 1 are installed
6c5b228a-60ba-57b5-ac70-5a78d891b6d2 | note | Verifying Document - Grundfos commissioning report
d510f662-b2a9-5212-8985-8e2e455deef1 | note | Frequency - once per pump
6651b9b1-d06a-58e7-a988-f8636c69c307 | note | Inspection Type (Visual, other) - Visual + Document
4a249718-73d7-5415-9688-eb025950af73 | note | Inspection: Key - I
b4c28862-e826-54d8-872d-ed13c2b4c80e | note | Inspection: By - IP
f7e1b6e3-9c75-473b-9f10-05b5a225dafa | checkpoint | 5.2 - Stage 1 Changeover Complete (Electrical)
4040fd7c-b1e8-5dec-b5c8-233152212d0c | note | Inspection Point: Quality Control Activity - VFD 1 in service
babbeb8c-b39d-58a3-a843-ac8425fcbef4 | note | Acceptance Criteria - VFD 1 is installed and parameters set by Grundfos
b5270d66-7426-501c-983a-045b784f614b | note | Verifying Document - Grundfos commissioning report
26328c74-b276-5a95-afd1-4c2a70c5260e | note | Frequency - once per pump
43f41c03-1276-5169-a43b-d570f04eda4f | note | Inspection Type (Visual, other) - Visual + Document
609d30a2-6b53-565d-b5ba-4ade13ab0894 | note | Inspection: Key - I
884ec496-dd5c-5979-9f25-ca8d128be59e | note | Inspection: By - IP
9ecefba0-8d4f-43c8-b918-0c2b93039179 | checkpoint-no-value | Note:
2cec3431-4622-5a90-aea6-4e8ec9e8b8e0 | note | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
edfe3ce2-c0db-4a75-a471-131afaa5a55b | checklist | 561483-ITP-009.2 - VFD 2 Delivery & Installation | itp | 561483-ITP-009.2 - Installation of VFD 2 (Pump 2) - Inspection Test Plan
9069193a-c6b3-4360-bae9-0a71dc1e2251 | section | SECTION 3 – RECEIVING INSPECTIONS
f49b50ca-dcd6-477a-a5a9-3d687751bfa3 | checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 2
f8794571-07dc-549d-b9d8-fde276f6e292 | note | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
3af2de76-44e4-5980-833d-90c7a3965cfa | note | Acceptance Criteria - VFD is damage free
a1d7c505-97ae-5a24-bf25-94880d494f68 | note | Verifying Document - 1. VFD delivery docket.
ab99081d-b76f-5d0e-b0c6-35e8e1445737 | note | 2. VFD storage ITP
f64aec8f-45ac-574f-a30d-f4935d910f82 | note | Frequency - Once
ca99e253-8b89-5b62-8593-369bc18a8e46 | note | Inspection Type (Visual, other) - Visual
a09d7a9f-d592-5039-bbf9-9495e8d779e1 | note | Inspection: Key - C
3a60bd42-d061-51cc-8e96-d1123cf84b27 | note | Inspection: By - IP
5fabcca2-109e-441a-8453-6ea140922e98 | checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 2
358fec47-e09c-5435-98f4-1d684680d121 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
47da87db-b4a2-59f3-913c-0d0ea77b6c85 | note | Acceptance Criteria - Approved Products list and approved for use
cedc8fc9-0b9b-521c-b9af-4997b6e0432b | note | Verifying Document - Specification - Approved Materials list
0fb7fd8c-81c4-5246-b55a-a1ac3f411f10 | note | Frequency - Once
df74fd3c-aa34-5e58-a80c-7451db6054dd | note | Inspection Type (Visual, other) - Visual
7ff1be34-1bf0-5f8e-8245-061725c32ecf | note | Inspection: Key - C
77a16934-7c15-59b2-8b88-e8928ed0688c | note | Inspection: By - IP
2c9cda76-0de6-4e2f-bb17-1f68485432ed | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
1caf6d3f-7955-5b9e-929a-1b963e61af27 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
210d20d8-4929-5377-aa25-8adb8aef1cbe | note | Acceptance Criteria - Upon approval from Client & Engineering team
f2ca786e-b34e-5740-9214-3b70dae92ea0 | note | Verifying Document - Written approval
5002b3fc-dc59-5f89-84e4-9c9d6dc0f601 | note | Frequency - Once
bc5299d0-65b8-5bcf-87d0-3bfeb6b6bc73 | note | Inspection Type (Visual, other) - other
3972af00-e329-5a1e-b641-30dc08cad377 | note | Inspection: Key - R
2f920974-5c20-5c0a-bab4-949c532cfa00 | note | Inspection: By - CR
73670275-7091-4511-9bdf-f278836d3b20 | section | SECTION 4 – IN-PROCESS INSPECTIONS
4899c4ba-22b7-4494-8f3e-04b34ab97ec7 | checkpoint | 4.1 - Electrically Isolate Pump 2 at Control Cabinet. Ensure no issues with Grundfos Controller.
3bf119d4-f6c8-5934-b593-659b37245a91 | note | Inspection Point: Quality Control Activity - Isolation is applied to Pump 2 and existing VFD
211cfeba-6ebc-5c63-9cf3-dbee83c2afbc | note | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
d4042b44-7ee4-5336-97fd-b6196c1bb9ee | note | Verifying Document - This ITP
2b5fddbe-d386-5b67-a188-2dcc104d2971 | note | Frequency - Once
82870280-4768-5a68-a847-ea29354035e2 | note | Inspection Type (Visual, other) - Visual
a1f394ee-4d00-517b-bfce-9f9068159ee7 | note | Inspection: Key - I
9299e943-1112-5c7e-be0e-6bb6158c1ba6 | note | Inspection: By - IP
7d4da867-6850-4143-bedb-4880868f943f | checkpoint | 4.2 - Electrically disconnect Pump 2
136d8bae-f34a-5fcc-84ef-12172cee95a6 | note | Inspection Point: Quality Control Activity - All electrical connections are removed
f71a5f2d-e4dc-596f-88b6-dc0f40b6e1af | note | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 2 disconnected, no voltage on cabling.
08e2d566-892e-5270-98e8-e9a34e0c372e | note | Verifying Document - This ITP
33f62ba6-50d3-50b7-9319-ca0fc67396af | note | Frequency - Once
a1fe4293-f11f-558d-b013-60e858e559e9 | note | Inspection Type (Visual, other) - Visual
9e81fe44-a6cf-589e-be82-3c504eec0106 | note | Inspection: Key - I
438fcd39-6faa-5b98-8bba-c860b6340043 | note | Inspection: By - IP
915463d8-0ea2-43dc-9a48-f032f87ca729 | checkpoint | 4.3 - Remove Pump 2 Cable from Motor to VFD
1ba70d20-4b2f-5929-b8e1-065455ff2cfb | note | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 2, Cable Removed From Support System
1e0f50a9-662d-5806-8ec6-6842600b1f4f | note | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 2).
7101c847-d4a1-5e84-aa94-c3908153b21a | note | Verifying Document - This ITP
1188e873-f344-54f2-84fa-a1a909223990 | note | Frequency - Once
5bb1f79f-e119-5bfd-9158-8e28ad8a6d07 | note | Inspection Type (Visual, other) - Visual
03bcecb2-3c3e-5b01-add2-d203341ea016 | note | Inspection: Key - I
f1b4a2c9-f1cb-5498-bd36-185fb751347f | note | Inspection: By - IP
12396d7d-1f26-466e-bd0d-4779fb3345fc | checkpoint | 4.6 - Remove Pump 2 VFD
0e62e92b-5d0f-5170-8c6f-0783ff8d5557 | note | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
6f1ea218-3ab9-5025-8cf2-a8c39ac587fd | note | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
681f76f1-3384-54c8-8ba4-add0f890aa93 | note | Verifying Document - This ITP
be01da1a-88b4-55ba-a663-da2cbcae4c1f | note | Frequency - Once
d3a45c60-7a79-5436-84c8-db3ae83cc40e | note | Inspection Type (Visual, other) - Visual
43153d39-7d16-5a65-b6c3-88018e320e8b | note | Inspection: Key - I
2dca3228-8c8a-51e0-bb9c-84c7fdbd1a10 | note | Inspection: By - IP
72fb9699-0768-4f58-9c79-12562ade22f2 | checkpoint | 4.7 - Mount new Pump 2 VFD
42734fda-cec0-5f74-b0c3-72199ba7b010 | note | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
172af844-ba2c-5c0e-9ec1-1e95d072175a | note | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
becae1c3-4553-5ceb-9914-aa7800425052 | note | Verifying Document - This ITP
81c4b8f1-f536-519b-aee2-7d98d68aba42 | note | Frequency - Once
ef9093df-1afc-5c99-a9b6-018b8cdb31a7 | note | Inspection Type (Visual, other) - Visual
5571111c-f640-580a-8fb1-86e1e6bb8c7e | note | Inspection: Key - I
aae3e91a-073d-56c9-acbe-208f8810fc8d | note | Inspection: By - IP
b49c701e-346d-48fc-a2d3-857184242fb7 | checkpoint | 4.8 - Remove VFD 2 Feed Cabling and Isolators
d6b3fa23-f08c-5353-a819-65f0f221fb07 | note | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
32b75c1c-22c7-5c3f-b076-0c14b1dca001 | note | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
bfa4732c-b650-5b35-ba13-0ab2fd6a55e1 | note | Verifying Document - This ITP
6f76b36a-9c63-529b-97af-810030401832 | note | Frequency - Once
f0edd4fb-d195-5c98-ac80-3dfe04aa8606 | note | Inspection Type (Visual, other) - Visual
eacbc19a-b029-56fe-9091-7ef80b656844 | note | Inspection: Key - I
1e90baa5-913d-5a1b-851d-9ee3f13b3403 | note | Inspection: By - IP
e7d6a4be-ca1a-4d37-ba5e-9b11446dbc40 | checkpoint | 4.9 - Install new supply cabling and isolators for VFD 2
3626c32f-a5be-5f3c-98d3-c65331616670 | note | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD2 is prepped and tested
4d04b7f6-1652-5e18-bd02-8658c8c65c86 | note | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
fee034ae-4227-59f2-a9fb-845afac99d47 | note | Verifying Document - Cable Test Sheets
3bdab9af-f099-5720-89de-8c6c2c81dd96 | note | Frequency - Once per pump
a134f5d3-f98d-5f72-a06d-ded4a85abdca | note | Inspection Type (Visual, other) - Visual
36679f7d-8d80-5147-8f1a-176f7a1c34dd | note | Inspection: Key - I
f929622e-e470-5123-b695-7bbe9e687c7b | note | Inspection: By - IP
fb927b2a-57c6-40ba-a812-3275a30c5dff | checkpoint | 4.10 - Terminate Cabling for VFD 2
0d5ae466-9536-5f22-a157-a07cfe14296d | note | Inspection Point: Quality Control Activity - Cables fitted off into VFD 2 isolators and supply cabinet.
40a0e46e-3c2f-59fa-a038-2f685a6a0853 | note | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 2
bf6e5c29-2e9a-5292-b34a-39bcdcd24c09 | note | Verifying Document - Cable Test Sheets
f2d83474-e9fb-58ed-8d9b-b1a48e925873 | note | Frequency - Once per pump
5e5352f4-a22e-5d07-b3f4-acc0549382bf | note | Inspection Type (Visual, other) - Visual
707f37a9-d941-5620-ab1a-e88fff61acf3 | note | Inspection: Key - I
9185dcfb-de49-58e0-818b-c367fa1dcafd | note | Inspection: By - IP
819fb397-8364-4691-94fc-010003753031 | checkpoint | 4.11 - Remove isolations
53f59925-b61f-5bba-bcf0-a165d0c2b344 | note | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
a882b69b-3eaf-56dd-a4c2-2df6a6c555a9 | note | Acceptance Criteria - isolations removed circuits re-energised
580cd418-94f1-5d53-beb6-60c4c4424e01 | note | Verifying Document - Lock-out Tag out Register
b2225751-0684-5feb-b1b2-8f1601dd5e81 | note | Frequency - Once per pump
dd54a22c-5d4f-5c84-9570-19123104576e | note | Inspection Type (Visual, other) - Visual
4f8cfccb-0569-5f1a-8cf1-6578b195a141 | note | Inspection: Key - I
d2d8fc93-8671-5d65-a3e4-aa3c97fd9d9a | note | Inspection: By - IP
fc41d35b-93d3-4bf1-8795-767ee3b257e0 | checkpoint | 4.12 - Configure VFD 2
e7cc4f98-bbc1-57a7-bcda-a18d123f7dd5 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
5a8cb9dc-1000-5152-806a-46736937f3ff | note | Acceptance Criteria - VFD configured correctly, controller setup adjusted
b9a3c1a9-2a93-5366-b570-0bf862426fda | note | Verifying Document - VFD test sheets
89d06d2c-b3b5-57a8-86f1-df6c9f7891e7 | note | Frequency - Once per VFD
2b77b95a-9324-56ac-974d-04055175ac38 | note | Inspection Type (Visual, other) - Visual
38ce8f4e-b9ef-50d2-b03d-49caee204b76 | note | Inspection: Key - I
ba44a5da-132a-52df-b2fc-8515d4034381 | note | Inspection: By - IP
45ce0e82-46af-4836-a2d6-f054a4263410 | checkpoint | 4.13 - Confirm correct operation of VFD 2 and pump
9891af51-6868-56d1-933e-b6a795de41c1 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
f5b45bee-3420-5a14-80d3-1979c2e49d25 | note | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
f7a19c03-c617-57f3-beca-9ce5bce71727 | note | Verifying Document - VFD test sheets
5f632807-f875-5531-9d37-c03f6644cb3c | note | Frequency - Once per VFD
e55541c2-4f69-5ab2-b5b9-f9c399f8fc9f | note | Inspection Type (Visual, other) - Visual
6c7ef179-e97e-527e-b792-1ce396922303 | note | Inspection: Key - I
0eafd12a-7f15-5513-aa37-0545d2992b08 | note | Inspection: By - IP
ed36fbfe-9641-4021-9bd5-d140a2c7950a | checkpoint-no-value | Note:
5b8c78df-437f-5f1e-8576-9c5526294df3 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
db372d6c-2e37-4884-80cb-1744b3920e44 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
2ebba4ff-cd08-4039-870c-e67e1689a98a | checkpoint | 5.1 - Stage 2 Changeover Complete (Mechanical)
7ddf6ab6-2ce1-5a0f-a793-b18fab56f10a | note | Inspection Point: Quality Control Activity - Pump 2 in service
6b463289-ae32-53c9-95c3-31e0537f7561 | note | Acceptance Criteria - Pump 2 is installed. Valves installed to Pump 2 are installed
600d35f0-67a8-52a1-ab74-c781b0534b28 | note | Verifying Document - Grundfos commissioning report
1ad674f7-7db5-5592-89a8-e7737b63c4e5 | note | Frequency - once per pump
f50cec97-4ecc-5978-92d9-1bcb16f549cf | note | Inspection Type (Visual, other) - Visual + Document
1b8c4aa6-00e0-5276-a2e1-2699034d13c4 | note | Inspection: Key - I
1fb22a5a-b87b-58fb-9b19-14bfa217edaa | note | Inspection: By - IP
3e637816-4f71-434a-b123-ebc191e38fb8 | checkpoint | 5.2 - Stage 2 Changeover Complete (Electrical)
2e812fa6-03d9-5d67-8ddb-ad66c7e4fd13 | note | Inspection Point: Quality Control Activity - VFD 2 in service
92ecda91-e566-5b54-a64a-fd732f17d26c | note | Acceptance Criteria - VFD 2 is installed and parameters set by Grundfos
792c0da1-b465-5ef3-a56f-aee679daaec1 | note | Verifying Document - Grundfos commissioning report
e1631145-4359-5bb3-bebc-fe7f6111ffc9 | note | Frequency - once per pump
95127414-ec18-57f2-9c92-3721acd066fc | note | Inspection Type (Visual, other) - Visual + Document
6db22a8e-3696-5e4a-bddd-ecd548c7ba88 | note | Inspection: Key - I
b532cf9a-2610-5270-bd23-4b74dfde1e2a | note | Inspection: By - IP
0c909df8-4ff3-465a-a0c4-e2ce6e1277f9 | checkpoint-no-value | Note:
f430a61d-fbdb-5c7a-8466-9c0b35ec77b2 | note | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
5d0c3e82-50af-4a11-9181-ab2a8170a590 | checklist | 561483-ITP-009.3 - VFD 3 Delivery & Installation | itp | 561483-ITP-009.3 - Installation of VFD 3 (Pump 3) - Inspection Test Plan
7b7c5f90-7cc7-452e-915b-5ba6859b1c1e | section | SECTION 3 – RECEIVING INSPECTIONS
8ab309cc-17a4-4250-b72a-a3b0dd7712a2 | checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 3
a55c2026-5adb-5e8f-9b04-145a4bb40f4f | note | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
a867e6ab-5c01-5d6e-8f31-04bc636b9d52 | note | Acceptance Criteria - VFD is damage free
40f02d91-e5a9-59fc-98a6-6b410bf7701f | note | Verifying Document - 1. VFD delivery docket.
59958dee-2a39-5d54-a5f8-e5876287056b | note | 2. VFD storage ITP
ac6290b8-1835-59d0-84ec-c7bbec2d9aea | note | Frequency - Once
74e881fe-c28f-5151-a837-29c1c7f00d07 | note | Inspection Type (Visual, other) - Visual
7f7a9ef8-2d10-501d-bf60-2a47b4bde486 | note | Inspection: Key - C
cef5df9f-8d9d-57cc-a479-88cee9e63898 | note | Inspection: By - IP
7ce216aa-99d1-4f02-a7aa-9c90052f75f2 | checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 3
abb095ba-e774-5872-aeee-f6324af2f4df | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
690a6932-ca01-5d10-bc68-dc8f580bb400 | note | Acceptance Criteria - Approved Products list and approved for use
b9bdd075-0e14-5eec-80a1-700ebab835c2 | note | Verifying Document - Specification - Approved Materials list
f9bfb6df-b069-583e-a130-7590f67c184f | note | Frequency - Once
64a82ae7-7572-533c-826d-9eee34e91fa0 | note | Inspection Type (Visual, other) - Visual
f6f79573-472a-530d-b0f9-0178f2ffb2ce | note | Inspection: Key - C
2da01597-a3ba-56a1-b7ef-a25f97b3452d | note | Inspection: By - IP
aef9c2f4-f37c-437a-a3ed-77604ca9140d | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
7129dd65-86ce-5957-bc47-b6d2f1843e12 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
bbf13ffe-3ecf-5d73-9c10-3d1189b10fed | note | Acceptance Criteria - Upon approval from Client & Engineering team
8d1cc2e8-284f-5280-a098-88993e3be3e6 | note | Verifying Document - Written approval
f89a22a2-cca3-5530-bbf0-ae80853705ea | note | Frequency - Once
2fd7b4c2-4400-5744-9717-6ab534fcf1b6 | note | Inspection Type (Visual, other) - other
23568a51-1769-5ea4-9f3a-faa0e59a5978 | note | Inspection: Key - R
71e5d061-cfeb-535e-82ba-5587c11b885f | note | Inspection: By - CR
9ce4620a-d725-4743-93e8-63ff9bbb06d9 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
eff5b081-d03b-4bde-a5f2-696763c45c06 | checkpoint | 4.1 - Electrically Isolate Pump 3 at Control Cabinet. Ensure no issues with Grundfos Controller.
5bd7a6e9-487e-5aa3-a933-2f3dc6223c95 | note | Inspection Point: Quality Control Activity - Isolation is applied to Pump 3 and existing VFD
02d9c5b3-91e5-5e6d-a826-7964b092ae58 | note | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
5d82a249-8e97-59e7-80d1-bf404847ef42 | note | Verifying Document - This ITP
231dedec-31c1-54d6-9f07-68f5f6c407a7 | note | Frequency - Once
c69ace9c-26c4-55ee-973d-0b31fe08b821 | note | Inspection Type (Visual, other) - Visual
2370294a-3e5c-5713-9b9b-2ccdd168277a | note | Inspection: Key - I
f532a217-9743-50ad-823a-85f8b7319477 | note | Inspection: By - IP
892fbd96-9f57-423c-a7d4-bfef706315a6 | checkpoint | 4.2 - Electrically disconnect Pump 3
4cdcacc3-3778-5da1-8692-5ea8757eb2ee | note | Inspection Point: Quality Control Activity - All electrical connections are removed
1c78ca1b-43b5-57e8-93cd-a04a26b0b5b0 | note | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 3 disconnected, no voltage on cabling.
39736246-981c-58ce-9415-027d940e0ec8 | note | Verifying Document - This ITP
d9e58d4b-9dd4-5b05-8f87-8c6996058d01 | note | Frequency - Once
3868ac8c-080b-5725-a2ad-71113ddeaacf | note | Inspection Type (Visual, other) - Visual
3ca4ede1-f502-5447-b996-5de36f7135f8 | note | Inspection: Key - I
3eb71807-7780-53c0-aa77-b438216e9a4b | note | Inspection: By - IP
4b30d22d-e605-4648-8d8b-86a3a4cc6777 | checkpoint | 4.3 - Remove Pump 3 Cable from Motor to VFD
8cd8122a-bb3b-5295-b5d5-371ed651175c | note | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 3, Cable Removed From Support System
131ef0a9-50ec-52bd-b824-08f5567abc26 | note | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 3).
7e9fdbdb-e48d-567e-a2c0-9a5dae043308 | note | Verifying Document - This ITP
6fb2b1a9-6cdb-5112-b655-bcb0c34a9869 | note | Frequency - Once
a39e182b-ffa0-5b1f-b390-f7574935c211 | note | Inspection Type (Visual, other) - Visual
6652738d-d5e0-5323-b1d2-876f07a4a485 | note | Inspection: Key - I
15786c40-a682-59cf-9cda-716d55cdce97 | note | Inspection: By - IP
92d37fc1-218a-438b-b45e-c5f502ec9512 | checkpoint | 4.6 - Remove Pump 3 VFD
0eea05c4-1bb1-57c6-9a2c-556d139341fe | note | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
6b357cab-be28-5826-b9e4-1339f2a51198 | note | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
d03adbe6-e30e-5d7e-ad6b-e09779dd304f | note | Verifying Document - This ITP
9d196b8f-e584-5ca8-8f96-ec1371a8d725 | note | Frequency - Once
ff28b72a-9fca-5653-847a-4bf52dbdf3dc | note | Inspection Type (Visual, other) - Visual
6d93004e-77e3-5351-a0d8-a50c9669b7bb | note | Inspection: Key - I
16151433-a503-549f-ae4b-8c72b204a701 | note | Inspection: By - IP
fa9c1699-a5d5-4ad7-ae23-0030134d62b4 | checkpoint | 4.7 - Mount new Pump 3 VFD
2d5bab6c-117a-5b27-9bfd-05e47d51bd53 | note | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
aef44a3d-c4af-5483-8f02-90952d09eb20 | note | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
34247707-f95b-5804-b6f3-ebea8ffff61c | note | Verifying Document - This ITP
e3e4e68d-ca1f-5d2c-8a23-4ca801fc38a5 | note | Frequency - Once
08dc0856-20c9-5f04-86cd-727a5f201fd1 | note | Inspection Type (Visual, other) - Visual
e8ae583d-06c1-59ef-be68-d4f317ef07cd | note | Inspection: Key - I
e6c5d6a2-3c50-5e08-b22f-9c684fc387ee | note | Inspection: By - IP
fa223047-dfb2-46ae-8cca-a50fa6b82a6a | checkpoint | 4.8 - Remove VFD 3 Feed Cabling and Isolators
77c6e6d6-c235-5c95-ad86-665777182ba9 | note | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
ede816cc-bb9c-5036-a23e-c0c3dcf1084d | note | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
a23cf038-386e-5bbd-a9f8-af389fb69190 | note | Verifying Document - This ITP
cc763e0a-4e02-512b-93a2-564ec45681ae | note | Frequency - Once
5752643a-9e95-568d-a768-9fd36f539852 | note | Inspection Type (Visual, other) - Visual
81c42259-026b-5f30-bfad-6601499922f2 | note | Inspection: Key - I
1dd4f781-eff9-54d8-8f5c-ea00f4067a76 | note | Inspection: By - IP
75d35de8-4cd8-4262-a1ba-cafc3d027c02 | checkpoint | 4.9 - Install new supply cabling and isolators for VFD 3
e6b7624e-c368-5bed-b869-460dc5ebb1da | note | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 3 is prepped and tested
b72d6d8d-7be3-5df0-b4e5-7e3ffd96a2ae | note | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
81f90505-d794-5b72-bd0a-571a6b71cae2 | note | Verifying Document - Cable Test Sheets
74945cbf-a0bd-5692-a7ba-40f974c4aeb0 | note | Frequency - Once per pump
7c7ab30d-796b-583b-8e39-3721d7e97eee | note | Inspection Type (Visual, other) - Visual
9683fb2a-5636-56a9-874c-b8d55869f73f | note | Inspection: Key - I
fab42791-07f4-5a42-ba6c-9693d5271511 | note | Inspection: By - IP
a9af4ee0-dcd5-4499-b8d4-e1ba57359a7a | checkpoint | 4.10 - Terminate Cabling for VFD 3
f97428fd-8f14-5706-89ff-ae21e1fee7b3 | note | Inspection Point: Quality Control Activity - Cables fitted off into VFD 3 isolators and supply cabinet.
9dcfc5f6-cdba-5bb1-8083-d5b574880b4a | note | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 3
76499c4f-1a6c-55ba-829e-6f87131d6e15 | note | Verifying Document - Cable Test Sheets
49419522-8b15-5c11-b258-7c77dc91ef01 | note | Frequency - Once per pump
18b4b835-ab72-584d-9fd0-611a3424fd5b | note | Inspection Type (Visual, other) - Visual
20ba27cf-6363-5b58-a1c3-c3d104b2d896 | note | Inspection: Key - I
eaaef776-ea1e-5b6d-88ff-d3e92c5a793a | note | Inspection: By - IP
525d6cf9-6857-4d9e-ac1c-664ed6cc8835 | checkpoint | 4.11 - Remove isolations
d0b37652-617d-5162-b050-398d67cb281f | note | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
e3e669c8-b51f-5007-9968-120004b7216b | note | Acceptance Criteria - isolations removed circuits re-energised
322b383d-61a9-5bd4-ba27-474ab6035bc8 | note | Verifying Document - Lock-out Tag out Register
2695e6c5-cf7c-5855-a5ec-b956aea91441 | note | Frequency - Once per pump
ec0c7233-f176-535c-afcf-6e93e1827a74 | note | Inspection Type (Visual, other) - Visual
6a3d6717-5aa8-5771-a633-4b73999ee68d | note | Inspection: Key - I
ca5a5b60-5d3a-5c7a-a8b5-56134bf2d517 | note | Inspection: By - IP
cc08ac39-1689-45ef-8a6c-131c966942c3 | checkpoint | 4.12 - Configure VFD 3
8e8abd85-781e-5959-be0e-31c0099e87f8 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
2f95d1b8-a1b4-5c17-b8b4-47df52bfc0e1 | note | Acceptance Criteria - VFD configured correctly, controller setup adjusted
0222b9f5-05f6-59da-bbe8-cac7482ab661 | note | Verifying Document - VFD test sheets
18281cba-8d69-534c-a161-4524022f49e9 | note | Frequency - Once per VFD
d7465de8-4209-5bd2-b89b-68f651973b9a | note | Inspection Type (Visual, other) - Visual
ccb93330-5bb6-53b7-a16b-0d1ce46f032a | note | Inspection: Key - I
99245790-ae2e-5f3c-94ce-eb1766a4bdd1 | note | Inspection: By - IP
5883d474-24e8-4de4-8740-b9b3452de20a | checkpoint | 4.13 - Confirm correct operation of VFD 3 and pump
655d14a5-5c6e-5fb3-8521-8b4ba9f021ef | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
39e612ef-0233-57ee-a40b-f39e82091010 | note | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
e7374795-a99a-5a42-9e4d-31e2874495b6 | note | Verifying Document - VFD test sheets
98fc5d37-6348-5431-9256-b3bbe803678c | note | Frequency - Once per VFD
dc45902d-4e4b-5a13-bea5-5b148332e1f2 | note | Inspection Type (Visual, other) - Visual
d813a554-7b69-5d7b-a86a-6be00fc078f7 | note | Inspection: Key - I
73a92cc8-b38a-54c4-b4d8-3ba3b008c944 | note | Inspection: By - IP
995e5382-f7bd-4e72-a44c-530ef7d798f5 | checkpoint-no-value | Note:
d0560f0d-1fb4-5d15-8e95-aa61744b502e | note | Electrical connection of pumps and commissioning are covered in separate ITP's
5f40187a-de8a-4524-886c-c960cceb7ba8 | section | SECTION 4 – IN-PROCESS INSPECTIONS
49a38841-6bac-4d28-ad0c-b09d414e88eb | checkpoint | 5.1 - Stage 3 Changeover Complete (Mechanical)
f84633bb-5c61-57ac-a3ca-e9b39fc95100 | note | Inspection Point: Quality Control Activity - Pump 3 in service
009c7057-40ff-59aa-90d3-f767b9bc5f95 | note | Acceptance Criteria - Pump 3 is installed. Valves installed to Pump 3 are installed
d803a937-3b36-51cf-9816-bf74dc3e050f | note | Verifying Document - Grundfos commissioning report
68d69839-f52e-5d19-af61-b6f4da68c93f | note | Frequency - once per pump
8cfb33ee-e6ff-5de5-8c7f-1b61ba42f9ca | note | Inspection Type (Visual, other) - Visual + Document
eeca2379-9ef6-5266-b209-2f81b1cf86f9 | note | Inspection: Key - I
589f9c1e-c9a7-50aa-9784-a55c6c7e95ff | note | Inspection: By - IP
4d9bd9d5-8c61-47ce-8fd7-8150cc757dea | checkpoint | 5.2 - Stage 3 Changeover Complete (Electrical)
c550c85a-5f93-52d0-8907-6bec01a3d418 | note | Inspection Point: Quality Control Activity - VFD 3 in service
9ce8096f-ec72-5790-92b9-6644a55a9366 | note | Acceptance Criteria - VFD 3 is installed and parameters set by Grundfos
19944d2f-168f-5eef-8da9-21548dccbd7c | note | Verifying Document - Grundfos commissioning report
0304651e-3f44-58ac-a602-93036cefdaa1 | note | Frequency - once per pump
61a0846d-3688-56df-b7eb-ed69998412f4 | note | Inspection Type (Visual, other) - Visual + Document
d20213c9-6581-5132-97e0-5282ee420e95 | note | Inspection: Key - I
67ee4ad7-83f8-5b71-bff1-e49ae1ede330 | note | Inspection: By - IP
9e80307f-7c28-4dde-8a4f-7f6464ee32c3 | checkpoint-no-value | Note:
bad8196b-bb58-5b6a-ad2a-ef89ddb1e1e8 | note | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
7cba29f8-edca-440e-b3b4-1dfcf21afb39 | checklist | 561483-ITP-009.4 - VFD 4 Delivery & Installation | itp | 561483-ITP-009.4 - Installation of VFD 4 (Pump 4) - Inspection Test Plan
2c57ba79-a8cb-470b-93b6-4f3502b3ad3a | section | SECTION 3 – RECEIVING INSPECTIONS
127f6e19-4760-4e7d-aa05-b577e49e7249 | checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 4
d9cf7cee-bd65-566e-8b8c-b1884376ce36 | note | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
4b9f18ee-a056-5aa4-970a-cbf5e90b0ef8 | note | Acceptance Criteria - VFD is damage free
a821d3b5-687f-587e-a73d-2e4e995b2944 | note | Verifying Document - 1. VFD delivery docket.
c71abf5d-984e-5ba8-9f4a-ade78d8a91aa | note | 2. VFD storage ITP
7b0cd782-8976-5ce2-b9be-2dfbda0acb7a | note | Frequency - Once
1f34bc83-d6d7-5207-aa54-cecf6becf4d9 | note | Inspection Type (Visual, other) - Visual
43bcc7fc-fd51-5a6d-97df-7b0a3eb67707 | note | Inspection: Key - C
dd821691-36ea-56fe-80bf-8f25ea7a5eea | note | Inspection: By - IP
b13b79bd-1aab-4811-853e-191c3d7e0e96 | checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 4
da245ff9-049d-5ba9-8c6c-f123a3462c1c | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
42df735c-a009-5cfa-b942-977659839bd3 | note | Acceptance Criteria - Approved Products list and approved for use
d926d6db-91f3-5084-9a1d-a968680f7ad3 | note | Verifying Document - Specification - Approved Materials list
6ff52a28-2b87-5b41-aa45-4b16fee66f5c | note | Frequency - Once
09e246a4-59bf-5a51-94f4-ef9c9ad88f9f | note | Inspection Type (Visual, other) - Visual
077535b1-36a4-541d-8278-936edf04511c | note | Inspection: Key - C
6c75ada8-b4d0-5583-b7cc-d2da2b0d635f | note | Inspection: By - IP
f282c799-2758-4e4e-89d1-b2e4c7f43004 | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
87e52178-7368-5fb5-90dc-4d4aedc8dd14 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
c6e4be73-2156-5554-b064-ec697fc61179 | note | Acceptance Criteria - Upon approval from Client & Engineering team
ba761ec1-7192-52a8-a6f1-2069f9372a8d | note | Verifying Document - Written approval
6c5b8bca-8431-52a8-8133-c62243b1744e | note | Frequency - Once
cca1c3c4-dfee-57dc-a06a-d99b605a5791 | note | Inspection Type (Visual, other) - other
5bfa8451-40e6-5858-8861-c6dacbe41d86 | note | Inspection: Key - R
ca130905-84aa-5b0a-b3bb-d81a50a03abd | note | Inspection: By - CR
4d5d5315-1cd9-423b-a8f2-36f539da2c55 | section | SECTION 4 – IN-PROCESS INSPECTIONS
654a1374-623c-40bd-87b7-8e29749eb390 | checkpoint | 4.1 - Electrically Isolate Pump 4 at Control Cabinet. Ensure no issues with Grundfos Controller.
c5ad0fc4-e64d-5805-9cc9-c880497bf826 | note | Inspection Point: Quality Control Activity - Isolation is applied to Pump 4 and existing VFD
270ca063-8fe6-59ce-824a-c4173fb43498 | note | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
d3dddfcb-53b8-501a-bda2-1436090d3b3a | note | Verifying Document - This ITP
7a95d9c0-608d-5079-b7eb-5a3eafc74217 | note | Frequency - Once
c1605604-0be1-52ee-b741-b7fa6a09408f | note | Inspection Type (Visual, other) - Visual
22349b3a-8b55-5237-8e74-fa76b0ecdad5 | note | Inspection: Key - I
fd915410-2045-5c6f-8142-8c669d13aa0a | note | Inspection: By - IP
81333711-a1b1-4341-a9ef-8f7cf46d2034 | checkpoint | 4.2 - Electrically disconnect Pump 4
8cf686d8-eedc-5d88-8759-110fc43357ea | note | Inspection Point: Quality Control Activity - All electrical connections are removed
3005fb24-79f8-50a8-9342-ad9fbca9ff5b | note | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 4 disconnected, no voltage on cabling.
cf56a36e-3af2-5682-ad56-4642c8567d46 | note | Verifying Document - This ITP
96bd0733-e0fc-5352-a8ae-5a80fa42ae16 | note | Frequency - Once
93ffb6d5-c121-5573-9521-3fbeceff0f0a | note | Inspection Type (Visual, other) - Visual
3fff2985-69c9-56f0-b29d-9d5cb06fda9f | note | Inspection: Key - I
3abd6c4c-6ef0-5c4c-b4c0-0a100023f9c2 | note | Inspection: By - IP
75d535e2-5a6e-42a9-b5b0-5d9a5f1591f3 | checkpoint | 4.3 - Remove Pump 4 Cable from Motor to VFD
9cb84794-3e7a-5b5f-9b8b-711ced3a3e46 | note | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 4, Cable Removed From Support System
4e2a3bb8-f364-5cd6-aac8-e18ee5c6d08d | note | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 4).
829fa9e2-dd5e-5387-a079-fe576ccfc9fd | note | Verifying Document - This ITP
0ce5e2fe-769f-59f0-8a76-81724148fe7d | note | Frequency - Once
3c5d4052-ff54-5a72-a08b-cbb0e80a1ba8 | note | Inspection Type (Visual, other) - Visual
e450c899-4ac5-5285-8a7b-15f31c7a72d4 | note | Inspection: Key - I
fbe32c67-4f3a-5e7f-ab50-f64a8650637c | note | Inspection: By - IP
236ddc2f-fef1-4c69-b07e-1e85093c1a9d | checkpoint | 4.6 - Remove Pump 4 VFD
5450d39c-ea54-50da-90b6-751903e79436 | note | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
ac5b0dbc-eb61-53a7-8865-885ccecff907 | note | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
2c9cf0c0-228e-5538-a147-bde669ae3d62 | note | Verifying Document - This ITP
30cf5362-0a4e-5aa1-9aa4-92acb3ac713b | note | Frequency - Once
d683295f-8d38-50fb-afa2-e7f1dd9d4b31 | note | Inspection Type (Visual, other) - Visual
45334daf-4a4b-5533-b99a-fe01a3bf307a | note | Inspection: Key - I
664a51db-17aa-597d-9149-ced0923a1fad | note | Inspection: By - IP
68690a61-f213-4426-b58f-468863025f1d | checkpoint | 4.7 - Mount new Pump 4 VFD
b98e30f4-c7d8-5a21-93ee-5d49fc0b3fc2 | note | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
2f85b8cd-48e2-5ab1-abf0-ce34fd733ea4 | note | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
7b18ba82-8d76-582b-bb28-1b691881b486 | note | Verifying Document - This ITP
219587f7-5194-5690-bed2-22063f5fd358 | note | Frequency - Once
ae2b4ed8-7b85-53e4-b3b1-fb53dee5e2b7 | note | Inspection Type (Visual, other) - Visual
625f2e12-84fc-5322-9dee-757520c63564 | note | Inspection: Key - I
d37c0c4a-3b30-50fb-9de7-e380fa8c1e91 | note | Inspection: By - IP
b7afab63-56bf-4039-87b3-386f0aa3d81c | checkpoint | 4.8 - Remove VFD 4 Feed Cabling and Isolators
d784d7f0-267d-5392-af2e-8f1617d528fa | note | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
dc9acfac-74da-5376-a5c4-46c2d51b8298 | note | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
faedb2ef-8d7e-5a62-972b-de6ceb961c1d | note | Verifying Document - This ITP
5bc8f013-b598-556d-8000-64a7ccea0c0c | note | Frequency - Once
b538bb13-ccee-5267-89c6-892315548b14 | note | Inspection Type (Visual, other) - Visual
8cc242f3-14e4-5d5f-8708-8a49db2d666e | note | Inspection: Key - I
b2ba7005-573e-5322-885d-11b2522e4f0b | note | Inspection: By - IP
8771f871-df57-406f-94ba-4ca76dda956c | checkpoint | 4.9 - Install new supply cabling and isolators for VFD 4
7a5ace77-b9a3-524b-80ef-23056528419d | note | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 4 is prepped and tested
d534d0ee-14f2-56e9-8f04-990ae581a7f0 | note | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
e55f02ce-4503-5156-8d9e-ee3550de8fb8 | note | Verifying Document - Cable Test Sheets
6817beeb-ca0f-5104-9096-ba29c22ca230 | note | Frequency - Once per pump
8b28e141-402b-5922-8098-42d27df6843a | note | Inspection Type (Visual, other) - Visual
e638fba7-4bd4-53a6-a077-ac57770dc369 | note | Inspection: Key - I
93325024-f09d-5546-8757-2b66e2a04e2a | note | Inspection: By - IP
8589ffdf-2eb5-4603-a0e9-39f7d3966005 | checkpoint | 4.10 - Terminate Cabling for VFD 4
7fc55dbd-2730-5109-ac28-d21e79a9b026 | note | Inspection Point: Quality Control Activity - Cables fitted off into VFD 4 isolators and supply cabinet.
2737efc4-66a0-5256-911f-1020111e74d4 | note | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 4
658a83bd-38eb-590b-adcf-d90df9d0fdee | note | Verifying Document - Cable Test Sheets
0a045da0-7dc3-5478-9b1f-f74bf6e1c378 | note | Frequency - Once per pump
a87c1ad6-2ca8-58ef-ab6f-26c7e805769f | note | Inspection Type (Visual, other) - Visual
1b0af1c1-0331-529c-8a4a-d84626af74cd | note | Inspection: Key - I
5d73b260-2d76-5c39-8e74-0d2494a56368 | note | Inspection: By - IP
61a232b2-2f5c-4e00-899d-d34fe9549eaf | checkpoint | 4.11 - Remove isolations
966d3ea4-563a-5e53-ab66-5ece0d23cffd | note | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
e06ba8c5-de59-5c5e-8732-8a8ce997513a | note | Acceptance Criteria - isolations removed circuits re-energised
700a67c9-651f-530a-ace2-a46800c8af28 | note | Verifying Document - Lock-out Tag out Register
6bafc8d6-a39a-579d-826b-98f060ecd086 | note | Frequency - Once per pump
d689cdda-d152-5057-ac00-09059c95973f | note | Inspection Type (Visual, other) - Visual
a56a6de9-7d52-57d8-aaed-b2a2db0b0899 | note | Inspection: Key - I
a279fcaf-a1ed-53c8-a78e-0f09ece87677 | note | Inspection: By - IP
d91b1695-16a4-4f8b-93fd-4d2579693a97 | checkpoint | 4.12 - Configure VFD 4
f64ae43a-e081-5fda-b6b9-768890cb16f1 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
46f5a1d5-6bb0-56d2-941c-63953c8a3cc5 | note | Acceptance Criteria - VFD configured correctly, controller setup adjusted
8f5975fc-9df8-5512-b4ea-c9bf37b884ee | note | Verifying Document - VFD test sheets
85158e22-7fda-58aa-882d-9da53e8abcf1 | note | Frequency - Once per VFD
0fab2b68-2718-57e3-8400-1172dc308925 | note | Inspection Type (Visual, other) - Visual
df1f1f69-03db-5d2c-9373-f4586c86e851 | note | Inspection: Key - I
b9a7a271-a95e-5f62-a000-62f125555211 | note | Inspection: By - IP
e973bec8-4bec-42d6-bc4f-f4ab6ec520cc | checkpoint | 4.13 - Confirm correct operation of VFD 4 and pump
15d7f8e5-8201-5e3b-9eb9-43dc5881f533 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
d9c2a0d1-06ea-53cf-bc11-892a46ab0161 | note | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
dec0cfb7-dc79-5904-a164-c9be5c45d876 | note | Verifying Document - VFD test sheets
d4cb141b-c5ee-5cb3-bd1a-e10d45dfddb4 | note | Frequency - Once per VFD
87d0f14a-635b-5218-ba70-5a850a9ad36b | note | Inspection Type (Visual, other) - Visual
3d26f13c-2d8b-549a-8f82-08fdba247134 | note | Inspection: Key - I
a1c16ee7-04a4-53f7-a2ca-ff67da038a2d | note | Inspection: By - IP
a97d7b93-1e2e-41a0-8806-02163580f991 | checkpoint-no-value | Note:
78a78985-d6de-55a8-b7b1-7a21bb077a60 | note | Electrical connection of pumps and commissioning are covered in separate ITP's
fe276297-f34f-4e22-81a6-17da139c2a4d | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
2d3380f7-6725-4f6b-aae1-537b116d84ec | checkpoint | 5.1 - Stage 4 Changeover Complete (Mechanical)
d0a01990-ed32-5502-94a4-cddcf5c31fdf | note | Inspection Point: Quality Control Activity - Pump 4 in service
a6f9caf3-ade2-5b9d-963e-08fd86d4bb15 | note | Acceptance Criteria - Pump 4 is installed. Valves installed to Pump 4 are installed
348940f1-c3ac-5eb2-a4b3-935f2f2bab0c | note | Verifying Document - Grundfos commissioning report
3ff9efbf-4ad8-5491-a33e-be5ccf2c36d0 | note | Frequency - once per pump
a5e47841-86f4-5c3c-8e0a-93c12a0bdc93 | note | Inspection Type (Visual, other) - Visual + Document
db95eca8-f33b-5628-9098-fc2271eeb762 | note | Inspection: Key - I
d54d2a1e-8570-5202-903a-4d1a25aa8b2e | note | Inspection: By - IP
b9d39e80-03da-42b9-a7f3-133126e13447 | checkpoint | 5.2 - Stage 4 Changeover Complete (Electrical)
0bed44b8-5ca2-580d-8c3d-7a30ae06cd9a | note | Inspection Point: Quality Control Activity - VFD 4 in service
457ee2e8-4c88-53a8-8025-5a8aab203a16 | note | Acceptance Criteria - VFD 4 is installed and parameters set by Grundfos
ec55d2ef-681e-5fa3-bef1-299374a6a515 | note | Verifying Document - Grundfos commissioning report
6f59b893-5c65-56e9-a11b-c9a5992db563 | note | Frequency - once per pump
5158352d-b364-5d62-816f-b11ecd723613 | note | Inspection Type (Visual, other) - Visual + Document
68032cfd-ea9f-591f-b847-a6dcd5cb3c9f | note | Inspection: Key - I
344ca7be-fa91-5f56-a7d7-26bfbf40ecd9 | note | Inspection: By - IP
7a9d7a46-afb4-43fc-bb2a-4a44bce01730 | checkpoint-no-value | Note:
26bf0bfe-f754-51e1-aa5d-e6ffd123c923 | note | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
d528d53a-12a1-4419-af60-1ee0fb4fa0ba | checklist | 561483-ITP-009.5 - VFD 5 Delivery & Installation | itp | 561483-ITP-009.5 - Installation of VFD 5 (Pump 5) - Inspection Test Plan
355d47a8-3968-4028-9ca9-8c3ce65b96d7 | section | SECTION 3 – RECEIVING INSPECTIONS
e6db79d5-c7dd-41c6-a258-43a61b921b6e | checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 5
374792e1-1ff4-5a86-8d6e-be60efe6126d | note | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
da685458-281d-5e5d-a415-410f5c75afea | note | Acceptance Criteria - VFD is damage free
d9b9bf19-9713-5951-b0db-99742274e208 | note | Verifying Document - 1. VFD delivery docket.
6b0d60ed-1a86-58e5-ae3f-89f7eeba7e33 | note | 2. VFD storage ITP
6f6f6797-fab7-5871-b949-afb1ff79e7fc | note | Frequency - Once
6252bab0-1815-57a5-b69c-a808353e9876 | note | Inspection Type (Visual, other) - Visual
713d3c7c-d791-5add-abcc-c1d16889fc7d | note | Inspection: Key - C
fb35f175-c1d9-5767-8ca0-375e7181f603 | note | Inspection: By - IP
940793fc-633d-4266-9f61-65c4ad4354bd | checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 5
6211c6a5-1e0e-5a45-bcbb-0a77f28980d2 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
453429bf-32e0-5e75-9939-b2f8aa9051e8 | note | Acceptance Criteria - Approved Products list and approved for use
8e4f5519-eb15-51c3-bbf6-ff562260dbad | note | Verifying Document - Specification - Approved Materials list
15f537cb-a614-594a-8bbf-ee772ccf3d72 | note | Frequency - Once
7684e6ce-39e1-53d3-a716-d05ef6a3f01c | note | Inspection Type (Visual, other) - Visual
3dc1d177-c6b1-52d2-91b3-a97eb47544a0 | note | Inspection: Key - C
f859d8d6-6480-507e-ab1e-974869971add | note | Inspection: By - IP
fcd3fc33-4f67-4156-b941-8e3d496c1335 | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
baef01fb-c8db-5aa1-860b-a4a2d04371a3 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
c12b8627-b0b8-59cf-a51e-779fde43e5c6 | note | Acceptance Criteria - Upon approval from Client & Engineering team
f2e9b8a5-55a6-595f-9553-302a4eb68397 | note | Verifying Document - Written approval
ac7ec989-5b59-5984-9c0b-88d801b4a67a | note | Frequency - Once
51751a37-ac98-567e-8335-93351f726654 | note | Inspection Type (Visual, other) - other
7ae139ab-c09c-50ac-a72d-09bd06a547e8 | note | Inspection: Key - R
6ff7cb41-c2d4-54db-92d1-a770bcee27c4 | note | Inspection: By - CR
8100cbcc-6e21-4cdf-a3f1-178f9bad1b04 | section | SECTION 3 – RECEIVING INSPECTIONS
0d50daee-94a8-4fd5-8c01-08afe26f1415 | checkpoint | 4.1 - Electrically Isolate Pump 5 at Control Cabinet. Ensure no issues with Grundfos Controller.
e11fe768-8234-5be1-9650-5665bd2b22b0 | note | Inspection Point: Quality Control Activity - Isolation is applied to Pump 5 and existing VFD
b9e75079-8dde-5876-9723-b7d35ae39e3b | note | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
966ff590-a76c-53f2-979d-8721d8e06c49 | note | Verifying Document - This ITP
27dbbda1-69de-5477-bded-a42cce813e7e | note | Frequency - Once
9459888b-811b-53af-95fb-cdace97d2cb2 | note | Inspection Type (Visual, other) - Visual
42a2425b-9682-54a4-8cd9-ba50a298591f | note | Inspection: Key - I
cc79539f-1345-5faf-a378-be9d1852e21b | note | Inspection: By - IP
730d8ad3-9c72-4e86-a4f4-c5d5a535d95e | checkpoint | 4.2 - Electrically disconnect Pump 5
1757b6d2-9423-5ff9-87f1-bec4293e5a88 | note | Inspection Point: Quality Control Activity - All electrical connections are removed
97722df2-0384-5e78-875b-1705b8f24cd0 | note | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 5 disconnected, no voltage on cabling.
b70fd1c6-d3bb-500e-bbee-99350cb9d89a | note | Verifying Document - This ITP
b161d7bc-df26-5b8f-b72d-810a5d935cbd | note | Frequency - Once
db1fedc2-892a-58a6-9f67-895f317f6034 | note | Inspection Type (Visual, other) - Visual
49add7b7-62a8-59c9-a2f8-c16166f4b23b | note | Inspection: Key - I
d1351e13-361b-5dbb-9c1f-dc31d9cf439a | note | Inspection: By - IP
434fa3c5-4752-4684-be50-18ba00a2c4ba | checkpoint | 4.3 - Remove Pump 5 Cable from Motor to VFD
b77af40f-2431-5c68-b5c4-373d1a0ea81b | note | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 5, Cable Removed From Support System
72d943f2-b47b-5bf2-b2a7-c24889affb0f | note | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 5).
afa47abb-9486-5f2e-b288-bba37dda8834 | note | Verifying Document - This ITP
9c85eed2-4a19-5439-9fab-c4812b153edd | note | Frequency - Once
7c092ddd-532b-5744-915b-a7bb0a854ed4 | note | Inspection Type (Visual, other) - Visual
7a9bd6b6-f26d-54ff-8d20-01523cf2fe02 | note | Inspection: Key - I
b796f3b4-9419-5918-9534-6b54bad819aa | note | Inspection: By - IP
eab252a6-d88e-4ae8-a208-af53ff1d7e49 | checkpoint | 4.6 - Remove Pump 5 VFD
f23fdbde-9e5c-51f8-a321-404f0c022fe5 | note | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
a78e33a6-cc6d-53f2-9765-8af37a2e3332 | note | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
a4865acf-c4b7-5d1e-b8f4-4d5c9a32850a | note | Verifying Document - This ITP
1feaf4cf-b16d-5a01-850e-e7fc544a28dc | note | Frequency - Once
dadd02a4-0380-55d5-9015-23bc52437913 | note | Inspection Type (Visual, other) - Visual
3f8c2b23-90b2-5b1e-9bb0-1d586d91a6f5 | note | Inspection: Key - I
f256c8f3-969b-596b-be43-24b35a0822a9 | note | Inspection: By - IP
1375fcc3-14b7-40b0-bfe2-f143160473f4 | checkpoint | 4.7 - Mount new Pump 5 VFD
ba1f9ab9-ed41-5491-b0f5-9212fd7a83e1 | note | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
d5ce31ea-647e-59f3-a2f0-1eb5a2afea23 | note | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
1daf6cc8-9a2c-50d1-ba85-c4f369a278b4 | note | Verifying Document - This ITP
49c05513-f66b-54e1-a523-6f0e1a7e53cb | note | Frequency - Once
350c93a8-497c-5542-9e18-1945bcd0baa8 | note | Inspection Type (Visual, other) - Visual
defdd39e-7a72-5cac-974b-db7caa7823cc | note | Inspection: Key - I
2c01522d-ebfe-5cb3-9bcc-5a93411081a9 | note | Inspection: By - IP
52efd722-8ff4-47f1-81fa-c6613e5d6b2c | checkpoint | 4.8 - Remove VFD 5 Feed Cabling and Isolators
ed551eae-9422-5a59-91ba-75c17349b4cd | note | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
72563815-06e7-559b-8a31-daffbd2271c6 | note | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
f55789f8-4a7c-51b2-a435-6a0016e46e12 | note | Verifying Document - This ITP
63d94754-dcb5-5007-bfb0-8bc9b5d1227d | note | Frequency - Once
cda259f8-007f-5c2d-9514-0a8048943c79 | note | Inspection Type (Visual, other) - Visual
a90d5c95-f3df-50b7-951e-2f7d5d038d2c | note | Inspection: Key - I
5aab5094-509d-53f4-9a94-3c4714a2dc7d | note | Inspection: By - IP
8f3e9267-adbf-47e5-87c2-54bd265135b3 | checkpoint | 4.9 - Install new supply cabling and isolators for VFD 5
d23ce236-4191-5770-9985-5551297bc543 | note | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 5 is prepped and tested
36d59490-a5a2-5cac-936c-8a9161c053f8 | note | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
0c8e8de1-caa0-59c0-b462-2827bb4ac6cf | note | Verifying Document - Cable Test Sheets
11973fae-a7f5-517f-9192-598acff5c2a0 | note | Frequency - Once per pump
b3ea1d1f-666d-5c43-9563-4d4ab6f8762f | note | Inspection Type (Visual, other) - Visual
fff90fb4-6759-5146-8cbb-d47192a1bdb9 | note | Inspection: Key - I
095019ac-518e-563a-b581-a2766742cfe4 | note | Inspection: By - IP
4c514459-aa8a-446f-af42-8846d8ea11f1 | checkpoint | 4.10 - Terminate Cabling for VFD 5
0681e1a3-2319-50f8-bff4-474d5b4c8703 | note | Inspection Point: Quality Control Activity - Cables fitted off into VFD 5 isolators and supply cabinet.
3091ea98-9fdf-549e-8fdf-24205ba73ce6 | note | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 5
dd29e3dc-d0b4-5c53-a9eb-e74e6b6a9a9c | note | Verifying Document - Cable Test Sheets
53905493-ba5f-5d0f-8e63-88cdb7fded23 | note | Frequency - Once per pump
ebab6e7c-594e-5bf9-9f59-81c3dc45688d | note | Inspection Type (Visual, other) - Visual
a0bdc1c3-d4fe-57a5-8bc2-5f1a8acb8b55 | note | Inspection: Key - I
785165ad-0bdf-58de-86a0-16e81fa2747a | note | Inspection: By - IP
3938bf6e-4759-4396-a743-be6ffd8a5087 | checkpoint | 4.11 - Remove isolations
786683e7-a61c-5392-b363-b1e309f858cb | note | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
ec8105f5-8100-5a1b-9634-f93ca67d67a9 | note | Acceptance Criteria - isolations removed circuits re-energised
c7b2cfa6-8672-541a-89fd-c70b5b607955 | note | Verifying Document - Lock-out Tag out Register
2078fb58-d369-5f2a-87f8-bd14fd643cc4 | note | Frequency - Once per pump
49b5d957-5e5f-543b-82c8-eb7ec933793b | note | Inspection Type (Visual, other) - Visual
1e6adc80-7f29-59ba-a388-d69511fa6e8e | note | Inspection: Key - I
9d90c077-34f9-5a6a-8f6c-8226afd8e53d | note | Inspection: By - IP
27452940-f411-4fee-bd5a-98a862d1cfc8 | checkpoint | 4.12 - Configure VFD 5
15a2c64f-3797-5eb5-bc65-58cf3b559b46 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
02702130-dcd3-5b02-9b06-63f6f8d78915 | note | Acceptance Criteria - VFD configured correctly, controller setup adjusted
0a0e9d01-5235-5a86-a03e-14105b4a63f4 | note | Verifying Document - VFD test sheets
146d810c-222a-5064-beb3-a0636e4bf77b | note | Frequency - Once per VFD
2b10099b-8020-5686-8865-3f36e519b124 | note | Inspection Type (Visual, other) - Visual
3c738074-2544-5422-9711-2da149f24539 | note | Inspection: Key - I
0e360106-8cdc-5630-b0c2-40377444a4d9 | note | Inspection: By - IP
3fd98437-f87f-4140-a50a-5e78e1dbbbb5 | checkpoint | 4.13 - Confirm correct operation of VFD 5 and pump
83f28b04-40d3-5836-b41a-63f595109ebc | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
1edffefd-53b2-555b-a5b9-4fb84eea624b | note | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
37d027ad-c9e6-5e6b-9951-355700e0f1dd | note | Verifying Document - VFD test sheets
82f7e424-058f-5c78-9c45-779c65230db5 | note | Frequency - Once per VFD
af2bc6d8-54da-5c45-ad16-14f7287dcaec | note | Inspection Type (Visual, other) - Visual
a8aa0d87-0bc9-59d8-b507-8504919ac83a | note | Inspection: Key - I
87e8757d-010f-5741-8243-7bfbf28bf117 | note | Inspection: By - IP
15ca78b2-1b6e-4f12-85a3-fb82d7675610 | checkpoint-no-value | Note:
286ac5b3-773c-50ea-a534-1589a72542bf | note | Electrical connection of pumps and commissioning are covered in separate ITP's
0f4091f3-ed69-438d-ad9a-dd55dabe8c6c | section | SECTION 3 – RECEIVING INSPECTIONS
65f5964a-c001-441b-8d3b-36b6516eceb5 | checkpoint | 5.1 - Stage 5 Changeover Complete (Mechanical)
49968062-0d1e-5d8d-9c11-b3725b4d3e5e | note | Inspection Point: Quality Control Activity - Pump 5 in service
542b7f57-33db-55ba-8bc6-8049f8236247 | note | Acceptance Criteria - Pump 5 is installed. Valves installed to Pump 5 are installed
2d1c8559-391c-5574-b958-5e9673d56e38 | note | Verifying Document - Grundfos commissioning report
1ed7240c-8187-5291-827b-732e1246a6e2 | note | Frequency - once per pump
a0d3b63c-fa40-5c97-9bf3-38928ab4ce7d | note | Inspection Type (Visual, other) - Visual + Document
937d0d47-6e88-51e4-b5a6-99c4f75bec66 | note | Inspection: Key - I
81e57e35-14dc-5140-b2dc-d080f43a30a0 | note | Inspection: By - IP
93212a04-49b6-4102-964c-b396dd64740e | checkpoint | 5.2 - Stage 5 Changeover Complete (Electrical)
605248ad-8ee9-5fcc-ad35-f9a0d87cd67c | note | Inspection Point: Quality Control Activity - VFD 5 in service
1be0bb8a-b28e-5462-a476-a24ca8e05eb7 | note | Acceptance Criteria - VFD 5 is installed and parameters set by Grundfos
25582fae-d1b2-5153-a85c-06df34fb5fc7 | note | Verifying Document - Grundfos commissioning report
78ab0c38-856e-5584-8fc2-79dbebf2bdea | note | Frequency - once per pump
8883cc88-644f-5b30-aba4-f04a210679bd | note | Inspection Type (Visual, other) - Visual + Document
f4f40a83-ce36-50c3-9348-ec8a863c420b | note | Inspection: Key - I
47707441-5433-5cb3-a6d8-98509e3bacce | note | Inspection: By - IP
a46edf50-e021-4345-8120-33047eb4c123 | checkpoint-no-value | Note:
126ca397-626b-57bd-b38f-7666faa0b32e | note | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
6a4b5125-a6fe-4326-ada6-84bbb2902411 | checklist | 561483-ITP-009.6 - VFD 6 Delivery & Installation | itp | 561483-ITP-009.6 - Installation of VFD 6 (Pump 6) - Inspection Test Plan
9c3a5019-3ee7-4895-92e7-95d764f7ac0f | section | SECTION 3 – RECEIVING INSPECTIONS
ad6c5f5a-94b6-4105-82bd-df63c1b8bd39 | checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 6
09a48b1d-67fc-52b1-9c63-c9940fc37edb | note | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
8a5544f8-84c5-5f0b-b5aa-589ab9aef153 | note | Acceptance Criteria - VFD is damage free
8f387b62-cfdc-539b-9988-1f840da62e1a | note | Verifying Document - 1. VFD delivery docket.
b7a0b2df-067f-507d-ae35-cbf1d6a6c852 | note | 2. VFD storage ITP
a42268d5-9215-5ccd-b042-3b22ff3149ce | note | Frequency - Once
7fb2a56e-5198-558f-89fb-49a93b51c810 | note | Inspection Type (Visual, other) - Visual
825ee236-8487-595a-822b-d46ee7f48f7b | note | Inspection: Key - C
a2c4e531-de8c-5a70-9b38-4e26f6010812 | note | Inspection: By - IP
ff07a2ca-f5e3-45b4-9d8d-13c65f6cd01d | checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 6
8ec6176d-53ae-5f32-9020-ea9146610835 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
97988af8-24f7-51d0-9d66-fff1bfb98f94 | note | Acceptance Criteria - Approved Products list and approved for use
195084dc-a212-5129-8999-e6e2ec145f5a | note | Verifying Document - Specification - Approved Materials list
87a1e451-f9c5-5366-9b9c-e09ed78e72c5 | note | Frequency - Once
9f358d48-48e2-5d69-9874-1bd5390cece0 | note | Inspection Type (Visual, other) - Visual
13f5230b-cd81-54e7-b795-b9cfcb16f864 | note | Inspection: Key - C
426484c7-6376-583a-96d8-233b203994b9 | note | Inspection: By - IP
4f94b790-eb6b-4001-9870-4a0746885241 | checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
ea9a0616-0d63-5f2b-90f1-3c2ac31f85e6 | note | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
5946a8b5-4754-5e31-be2a-086880c5e092 | note | Acceptance Criteria - Upon approval from Client & Engineering team
db2319fc-53c5-5e2d-ba86-8c7bab60c21c | note | Verifying Document - Written approval
6799ed63-36d9-533d-b6a0-f5ebe59cdda1 | note | Frequency - Once
5cb36cb3-7700-5a38-9133-82e5dca60e09 | note | Inspection Type (Visual, other) - other
cfbcb9ec-3a55-501a-a53a-58c6575a5082 | note | Inspection: Key - R
27191359-e44a-53f8-b098-900126fee69a | note | Inspection: By - CR
afc535d4-3d09-4284-bb7e-c0fab9b11439 | section | SECTION 4 – IN-PROCESS INSPECTIONS
b079fd54-7fe3-4c9e-aec5-924a9ace2799 | checkpoint | 4.1 - Electrically Isolate Pump 6 at Control Cabinet. Ensure no issues with Grundfos Controller.
9731e2c8-d17c-5cf3-89b5-aca48af7755e | note | Inspection Point: Quality Control Activity - Isolation is applied to Pump 6 and existing VFD
0e1f7231-211b-5088-b46a-e819ba0ca2bd | note | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
1b849dfc-c5fd-5b65-8387-e60860bd2245 | note | Verifying Document - This ITP
90353c45-7f7c-591d-aacf-db4da1bbfd46 | note | Frequency - Once
2d8d2d30-cdbb-5fb4-8d07-26a95aed160e | note | Inspection Type (Visual, other) - Visual
78481279-c538-5487-89d3-98ca7a83c46a | note | Inspection: Key - I
39ae9808-d88a-59af-8a42-1f4cb37fa9fd | note | Inspection: By - IP
8c608c5d-b1e8-4bbd-b4b1-335c7bfd42d9 | checkpoint | 4.2 - Electrically disconnect Pump 6
391b63c7-9d12-5d0c-abea-06458ced5980 | note | Inspection Point: Quality Control Activity - All electrical connections are removed
523cd014-b3dc-5f8d-9ca4-b2cf5f01e12c | note | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 6 disconnected, no voltage on cabling.
72a6e93f-62b6-5048-84ab-b858e4cfd185 | note | Verifying Document - This ITP
136343f3-4177-5e27-b1c2-318964773e93 | note | Frequency - Once
2200e2a6-8a5a-5705-9c9d-2a64683be6c9 | note | Inspection Type (Visual, other) - Visual
bba7a828-fa9c-5984-afe2-61888da1bc01 | note | Inspection: Key - I
a7b81c87-e390-5ac3-9151-4ec670eda1cb | note | Inspection: By - IP
2316b517-e17d-4fb4-bbc7-281961ee4111 | checkpoint | 4.3 - Remove Pump 6 Cable from Motor to VFD
47908373-043d-5687-b69d-c2870710d2a4 | note | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 6, Cable Removed From Support System
68a181be-59cf-55a3-86fc-1dd5f46b3743 | note | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 6).
2b001691-11b1-5626-a92d-afc6e81b2016 | note | Verifying Document - This ITP
b7a70eb8-6eb1-5322-8e82-b627205b5a93 | note | Frequency - Once
4b25e55e-64ce-50c8-922e-f03d2203ed07 | note | Inspection Type (Visual, other) - Visual
6aabdbf4-46fc-54bf-aca0-4444cde5325a | note | Inspection: Key - I
65fe53a6-6da0-5612-b412-40e2829449d8 | note | Inspection: By - IP
3f00fcab-5783-4c9e-9c98-74f22036bba1 | checkpoint | 4.6 - Remove Pump 6 VFD
5d56ace5-4892-5a52-96f0-4bb583dcff57 | note | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
290eb68b-7e88-5f92-abaa-eb4262a16ec5 | note | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
a8fcb94a-22d1-502f-ab53-133e4d05c4f5 | note | Verifying Document - This ITP
3012ec0c-43cb-5f5f-be1a-b68efc711112 | note | Frequency - Once
cbfa23c3-27c0-59c5-be48-b86e72012179 | note | Inspection Type (Visual, other) - Visual
2ef34d99-d10a-5908-8727-755efeae9abb | note | Inspection: Key - I
7b2bb782-382c-5929-a166-46d6243f9107 | note | Inspection: By - IP
dd161bad-14ff-49e4-bc2b-8a62ff7e15df | checkpoint | 4.7 - Mount new Pump 6 VFD
7687d7a7-5624-53fe-b957-f4d24296a938 | note | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
00ba62b4-6e24-54c9-a1ed-a6f7be666232 | note | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
2c5e09fe-c708-5775-b33e-efe01eaec53f | note | Verifying Document - This ITP
7ac3b215-df3a-5e9e-b8b5-3865f8221467 | note | Frequency - Once
48bf515a-f38f-5203-a9f2-5780f15bb4fd | note | Inspection Type (Visual, other) - Visual
a2ad0e7a-c9d2-5cee-ad8e-6ebed38a7c31 | note | Inspection: Key - I
bf625a14-a9c1-5278-9c3c-6a1ce277c6b2 | note | Inspection: By - IP
64d1eb63-a4d8-48c6-af30-7bf1f2563a0a | checkpoint | 4.8 - Remove VFD 6 Feed Cabling and Isolators
4dc10d08-0b12-5f33-a7af-4d460fa3e5c1 | note | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
7afa5eb9-4830-52e7-b1d1-ed9682f45cee | note | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
274e249c-501c-5ffc-9d82-67caf038e5db | note | Verifying Document - This ITP
c1553b79-ae8c-5886-8c54-3c98108427e7 | note | Frequency - Once
64221842-1863-5e42-bc60-795dab819421 | note | Inspection Type (Visual, other) - Visual
41486839-2314-5021-af15-f038c1c9c476 | note | Inspection: Key - I
57f0cc53-9786-554f-bbe2-cc4311502f57 | note | Inspection: By - IP
d433977a-af85-4588-a39b-b50c1f2018b1 | checkpoint | 4.9 - Install new supply cabling and isolators for VFD 6
e976ea87-4045-515b-a061-949c56aacc25 | note | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 6 is prepped and tested
89e43bfb-eeaf-5744-b787-9c9be3fa0e1d | note | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
04dd9752-2fe2-5553-816b-5b00fc52f28d | note | Verifying Document - Cable Test Sheets
9c590095-3dcd-58f6-980f-5926c43d1082 | note | Frequency - Once per pump
801f4b41-9329-5a09-b772-307c423992a9 | note | Inspection Type (Visual, other) - Visual
dced46cc-5121-55e2-88df-7a3e0c0efb57 | note | Inspection: Key - I
5a72eca7-226a-5ab4-817c-81b5e566b8b2 | note | Inspection: By - IP
dcb43ce0-8f78-49af-8335-c13ccfca992e | checkpoint | 4.10 - Terminate Cabling for VFD 6
cb2d9383-53d9-5920-96dd-d39b67fa19bf | note | Inspection Point: Quality Control Activity - Cables fitted off into VFD 6 isolators and supply cabinet.
9214a5ee-5bf7-544b-bee3-27e31b4efa9f | note | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 6
9cd77329-f31a-5b7c-8514-cc65310a153d | note | Verifying Document - Cable Test Sheets
0bc239c9-bbe3-5de1-974c-3d98fd70174e | note | Frequency - Once per pump
ac4f858c-c329-5e5c-8e38-61a7c63e74fa | note | Inspection Type (Visual, other) - Visual
e26a0da4-2198-5bef-bf6c-ea9ce2509eef | note | Inspection: Key - I
0e52e16b-153e-5531-b5f6-f6574cdf361d | note | Inspection: By - IP
fa6f8ebc-e9a1-43da-a9f7-c4b70b7eeeee | checkpoint | 4.11 - Remove isolations
75ada8b4-dad7-5626-b992-2b0cee3bc226 | note | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
f830dae9-5a02-5c68-ac34-4641b69e7c9e | note | Acceptance Criteria - isolations removed circuits re-energised
27e81159-edf9-53b3-9989-deb39a714f8c | note | Verifying Document - Lock-out Tag out Register
790cfb07-1b0a-50dd-bf7b-e4712ab56b2e | note | Frequency - Once per pump
f2a7d77d-ae34-5000-ba10-1b792367661c | note | Inspection Type (Visual, other) - Visual
8593735c-b2f7-5255-b8ba-0853d10e8a21 | note | Inspection: Key - I
d5b2f7a3-7cb3-51e2-bcc7-fae92ca12e0b | note | Inspection: By - IP
d42a6693-8486-4203-9461-e008bcab1f60 | checkpoint | 4.12 - Configure VFD 6
835513f7-9616-5af6-9870-8d511865ce63 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
57287ed4-cfc6-5258-ae61-3b05269a79cf | note | Acceptance Criteria - VFD configured correctly, controller setup adjusted
b5646eb1-9d0a-5711-bed0-eeb587643817 | note | Verifying Document - VFD test sheets
b9ac11f0-2fd9-5e47-b257-5354ef1ea05f | note | Frequency - Once per VFD
9ced4b79-e2c3-5a03-aeae-163b90f2bd10 | note | Inspection Type (Visual, other) - Visual
a42a729b-43dd-55a5-adce-7ca51e10fe87 | note | Inspection: Key - I
5d4edcf4-0f5f-5c9f-8ceb-5917ff6c3929 | note | Inspection: By - IP
2dd6fc12-5be6-48c4-83f0-d0b42b200fb9 | checkpoint | 4.13 - Confirm correct operation of VFD 6 and pump
9a276ea9-c243-5278-a91f-01a5fa3c1732 | note | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
a2a90c3c-39bb-5501-bf6d-824c37b5adf5 | note | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
8617a70a-824a-518e-b79e-f8e5f6055349 | note | Verifying Document - VFD test sheets
18748402-1d4d-5e38-80db-ff0609ee346e | note | Frequency - Once per VFD
9aba0a1f-e0a3-5e28-9223-83cb80877958 | note | Inspection Type (Visual, other) - Visual
ce17a91a-4cda-513f-97ea-1cf450c5be45 | note | Inspection: Key - I
a6847090-594f-5033-bf32-0995d280fd5f | note | Inspection: By - IP
45c1b51e-92d3-47c2-bcee-591aea8a327f | checkpoint-no-value | Note:
21679361-011d-56e0-9dc8-f7ea6076344c | note | Electrical connection of pumps and commissioning are covered in separate ITP's
94a69bb2-3cdd-4632-a301-16b089bbaff3 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
7ac8d743-f516-44fa-b304-d252f00baaa9 | checkpoint | 5.1 - Stage 6 Changeover Complete (Mechanical)
a66e57e1-e132-50bf-b68f-d002323997f3 | note | Inspection Point: Quality Control Activity - Pump 6 in service
f49149d7-c19f-5160-a2dd-dff4702af146 | note | Acceptance Criteria - Pump 6 is installed. Valves installed to Pump 6 are installed
c2283911-9d86-5c3c-bcf9-b8371968418a | note | Verifying Document - Grundfos commissioning report
5ecb985f-62a2-50b4-b489-68aa05e38b87 | note | Frequency - once per pump
355f2c23-63f9-5d82-bc2e-8870bd14ce57 | note | Inspection Type (Visual, other) - Visual + Document
2988d393-1a22-5d89-90d2-545af8b35802 | note | Inspection: Key - I
eded10b6-d2ca-53cf-8037-bc09997b4664 | note | Inspection: By - IP
67cbe9bd-f5cc-4dd6-b396-38505f0a5900 | checkpoint | 5.2 - Stage 6 Changeover Complete (Electrical)
f3ac10a7-985c-5435-a8ea-a4663c266a89 | note | Inspection Point: Quality Control Activity - VFD 6 in service
c63366f0-0124-58f7-9bef-5504201ade8d | note | Acceptance Criteria - VFD 6 is installed and parameters set by Grundfos
7c37aadb-5374-59d6-8b54-26dae05e12ad | note | Verifying Document - Grundfos commissioning report
01cde9e1-94af-51bf-a9bd-a66ffd287394 | note | Frequency - once per pump
b9579c55-bb7f-55cd-9e7e-6fd9116be8df | note | Inspection Type (Visual, other) - Visual + Document
b7daa9f8-828d-5b12-a3fa-0f13943d2f4e | note | Inspection: Key - I
3163a57b-fd40-5efc-8595-055c80a1e591 | note | Inspection: By - IP
cf56bc00-fc4f-4130-ab8d-04cf47adb75e | checkpoint-no-value | Note:
9181b8de-ca39-5edd-b291-fa898daadfd3 | note | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
2c3d8ebc-f170-4158-93e4-fc114e57918e | checklist | 561483-ITP-010 - Electrical & Controls Installation | itp | 561483-ITP-010 - Electrical Installation, Generator Changeover & Switchboard installation
d02b736f-8185-46dd-b808-fdb04b6e7e74 | section | SECTION 3 – RECEIVING INSPECTIONS
06176e47-0689-4bef-a462-45c18d0f7510 | checkpoint | 3.1 - Inspection of Generator Changeover Switch Cabinet
61370cce-53e8-5c45-a0ff-df4afa03c29c | note | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
ec169e28-526f-57a1-8f0d-100932f0b5a4 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
be58b7f6-7421-5716-a6f7-a44a8cec4ff7 | note | Verifying Document - Email or NTE to report
74786421-4abe-5162-a37d-b27c04fc5020 | note | Frequency - once
0170057a-88f2-5542-8f7f-a79c09224bec | note | Inspection Type (Visual, other) - Visual + Photograph
7941199c-da6c-514b-8730-e9e5c0bfa359 | note | Inspection: Key - C
1ee881e6-9ab6-5269-b012-04d55a0cb6a2 | note | Inspection: By - IP/B
1331779d-5c4d-458c-9ead-778976efede1 | checkpoint | 3.2 - Inspection of Generator Connection Enclosure.
862d2fa0-25f4-5d6b-b4a9-27525d2c801f | note | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
62e4963e-1f96-5386-8808-33099c953ae0 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
bdce89b8-fa40-5179-baa7-87945d4b0908 | note | Verifying Document - Email or NTE to report
593807ab-c82c-530f-a081-f69d826aeb3a | note | Frequency - Once
05232ca4-6aa1-5d2d-bfe0-534f595b5653 | note | Inspection Type (Visual, other) - Visual + inspection
6cc739ff-35d1-53cd-9239-0cd073166dca | note | Inspection: Key - C
77591d66-dc92-5dd3-9337-df793e843a6e | note | Inspection: By - IP/B
ae2145dd-99c1-4eb4-8ed1-0beab073162c | checkpoint | 3.3 - Delivery of Generator Changeover Switch Cabinet to Site
ae3a21cf-7bcd-5828-a9bb-fa5a646776f7 | note | Inspection Point: Quality Control Activity - Check and verify that the Generator Changeover Switch Cabinet has been delivered damage free
7a202666-ebb5-51af-b09f-f16f154b474f | note | Acceptance Criteria - Cabinet is damage free
db4e90df-ef7c-565a-94cc-db760004e6ec | note | Verifying Document - Switchboard Builder Delivery Docket
caa61881-6f6e-5299-879e-fd8fe92edbe9 | note | Frequency - Once
4a131507-8c3e-5f66-96d4-c684ef55c71e | note | Inspection Type (Visual, other) - Visual + inspection
05714b17-02ea-575f-8958-29254ef40e4a | note | Inspection: Key - C
055c8e9a-0f83-5e57-8ae6-6117f35d973e | note | Inspection: By - IP
66d506a2-c6a7-41ca-b4cc-2a6a40d94a73 | checkpoint | 3.4 - Delivery of Generator Connection Cabinet to site
7eeab9c6-e0f6-5286-8c41-fdaf2a51b748 | note | Inspection Point: Quality Control Activity - Check and verify that the Generator Connection Cabinet has been delivered damage free
482adecb-8fde-586c-b21e-c7db49c2a486 | note | Acceptance Criteria - Cabinet is damage free
e46c93c2-143c-5da9-a178-74b7b4798886 | note | Verifying Document - Switchboard Builder Delivery Docket
94444239-e216-5f8a-8640-e152a8fba794 | note | Frequency - Once
bf1c2e76-f8cd-56e5-b31b-661f83d985a0 | note | Inspection Type (Visual, other) - Visual + inspection
0ad5f58a-1f55-5cf2-b1c7-b2433568db6c | note | Inspection: Key - C
e6c824d3-8c8a-5dc3-a46b-636b3a3cc36f | note | Inspection: By - IP
bc3e1de3-5dbb-4dcf-a129-568fae016dfd | checkpoint | 3.5 - Inspection of Switchboard
afc26b3d-0868-5f5b-bfa5-739fe7eb617f | note | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
d24110fb-6b48-5098-bfca-baa8ffa74a31 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
8fdbee33-f803-5a62-898b-2fbd0bd8223d | note | Verifying Document - Email or NTE to report
639bd2a8-d125-5d26-9f2b-29584c115ec5 | note | Frequency - once
50f3679a-5738-596a-94cd-206c1177fddb | note | Inspection Type (Visual, other) - Visual + Photograph
021fa9eb-440c-5c18-9fa2-b782cc46041a | note | Inspection: Key - C
4e6a5438-a390-5aae-b079-a16739bd73b6 | note | Inspection: By - IP/B
b8f78682-3c01-45b1-ae80-42b478468e5e | checkpoint | 3.6 - Delivery of Switchboard to site
5811c8b0-21b9-52b1-b749-19d430ca8364 | note | Inspection Point: Quality Control Activity - Check and verify that the Switchboard has been delivered damage free
58f7387a-6325-51a2-964a-7e57a9e3df90 | note | Acceptance Criteria - Switchboard is damage free
a141ab66-e76d-59b9-adc8-e1543f9145bc | note | Verifying Document - Switchboard Builder Delivery Docket
a69ad152-fc7b-5831-8e83-37d30f6ceda7 | note | Frequency - Once
6cce0b3d-dc4a-520d-9504-7996fa1ff911 | note | Inspection Type (Visual, other) - Visual + inspection
df4dcd16-d7db-5ce5-8030-ce68aeac1a70 | note | Inspection: Key - C
30fb44fe-d1e2-5877-802f-0d01edb509af | note | Inspection: By - IP
35f1e7d3-7356-47b9-af56-126d32bda23e | section | SECTION 4 – IN-PROCESS INSPECTIONS
214eca0a-8b6c-42f8-ac32-b2b6944f6884 | checkpoint | 4.1 - Mount Support Brackets To Hand rails for Cabinet
56175076-8ee8-5cd3-ac18-1e3b452ccedd | note | Inspection Point: Quality Control Activity - Support Brackets mounted to Handrail
d3d7074e-6106-5040-85fd-bc27709fce48 | note | Acceptance Criteria - Mounts are secure and firm, with no excessive deflection
43d521ba-79a2-5f87-ba7d-eb40c2afa3b4 | note | Verifying Document - This ITP
efedc109-4216-51b9-ad5a-3efb2a375d2a | note | Frequency - once
fe55423a-eafb-53b7-90e6-ef830e8b12ee | note | Inspection Type (Visual, other) - Visual
7c1a441c-903d-5107-b261-11bdbbecf0ff | note | Inspection: Key - I
eab6e176-ad0b-5895-a5f6-05f1751efe80 | note | Inspection: By - IP
5e549141-042a-41e4-89a2-0580eb548c7e | checkpoint | 4.2 - Mount Generator Change over Cabinet to Mounts.
b188c555-32eb-5513-9b4e-75eaae09ceed | note | Inspection Point: Quality Control Activity - Cabinet Mounted
ff2cef4c-b781-5f07-84c5-8d15d7bedfeb | note | Acceptance Criteria - Cabinet is mounted securely, all bolts tight, seals intact and in good condition
7cd8b793-86f5-5218-82af-2d0787731c75 | note | Verifying Document - This ITP
d53cfabe-a3eb-5585-a63e-af15a9f18443 | note | Frequency - once
08f96820-93ef-5c68-a7de-b7d809ada9bd | note | Inspection Type (Visual, other) - Visual + Photograph
c7302460-547b-524c-bca8-8acbb30618d9 | note | Inspection: Key - I
2b0df25f-9b16-5f05-b29e-8f0385c800ab | note | Inspection: By - IP
356e6822-95c7-4be6-ac18-6cbbb6cc7e09 | checkpoint | 4.3 - Mount Generator Connection Cabinet on outside of Building
5d5fb57d-e26d-5038-8fd5-367ba2617456 | note | Inspection Point: Quality Control Activity - Cabinet Mounted
e2fe9ea6-ae1c-578a-8f99-a91c45b82d45 | note | Acceptance Criteria - Cabinet Mounted Securely to wall
40187244-d6d2-565e-9157-e21e2c1cf7ec | note | Verifying Document - This ITP
ff7883f6-05e5-582a-8060-1f16be56c18a | note | Frequency - Once
4b816ba5-a6ad-55c0-a4c3-85e98aebae17 | note | Inspection Type (Visual, other) - Visual + Photograph
34a5208a-152a-5bd5-9985-4477c803e3c7 | note | Inspection: Key - I
b37abfb8-31e6-57fb-a520-9cb7b3856404 | note | Inspection: By - IP
8053ecca-cc1c-4a26-99c5-1b3ab6767329 | checkpoint | 4.4 - Install Cable Supports for generator Change over
bd7b5569-0379-5116-b63e-842d3f69ba32 | note | Inspection Point: Quality Control Activity - Cable ladder installed securely, with adequately spaced supports.
abfa4b31-3ccf-53ef-aa9e-ffa532710f67 | note | Acceptance Criteria - Cable ladder mounted correctly.
47ec140a-579b-5846-ba04-27b5f125173e | note | Verifying Document - This ITP
e4a9b7bc-64bf-573c-8546-220312e9c902 | note | Frequency - once
c71d2e48-7f15-54b2-b9e8-9c0080b2920a | note | Inspection Type (Visual, other) - Visual + Inspection
724b0c89-3679-5ebd-8efd-b61164633772 | note | Inspection: Key - I
da368bd1-5042-5498-8d13-b71008b876ce | note | Inspection: By - IP
4388e005-46f6-46e8-9680-3e0eb5b32024 | checkpoint | 4.5 - Mount Generator Connection Cabinet on outside of Building
6bf92432-805f-5eed-a8c6-b40fbf9df66d | note | Inspection Point: Quality Control Activity - Cabinet Mounted
3c6f15ff-b630-5773-b893-6bdac3f475f3 | note | Acceptance Criteria - Cabinet Mounted Securely to wall
c561d4eb-ae5a-5888-8ab2-f0e45068d221 | note | Verifying Document - This ITP
70b63953-633c-549b-901d-59fb94b4937b | note | Frequency - Once
93236ddb-18c0-5d4d-a474-bb4743606665 | note | Inspection Type (Visual, other) - Visual + Photograph
f5579532-82c7-52a0-bc30-916b11ef2e85 | note | Inspection: Key - I
6c6628c5-0e3e-514c-bd99-5c6b332fc289 | note | Inspection: By - IP
ad0abbbf-cb22-4e1d-9a23-59c265be3cbb | checkpoint | 4.6 - Install Cable Supports for generator Change over Cabling
863528b0-116d-5347-af41-4b16ec981dd3 | note | Inspection Point: Quality Control Activity - Cable ladder installed securely, with adequately spaced supports.
df8fbeec-3ac4-53d7-9263-ee61090e5144 | note | Acceptance Criteria - Cable ladder mounted correctly.
ee2c2ba8-53b8-53c4-a4e5-c1a10756913d | note | Verifying Document - This ITP
1ea9ccc6-9ba3-5258-a8b3-d3bb65b1d421 | note | Frequency - once
19995a03-4ba2-5b00-812f-6745f8bab90b | note | Inspection Type (Visual, other) - Visual + Inspection
42c1f8fb-92d6-520c-bedd-631f63b891c1 | note | Inspection: Key - I
7be84cf4-1056-5cb2-b89f-2e0b6d0eb81e | note | Inspection: By - IP
061989b1-11d1-4670-b6d3-04dbfd83975a | checkpoint | 4.7 - Install Cabling Between Generator Connection Cabinet and Generator Change over Cabinet
9c4ff688-be5b-556c-9412-6e111393e5a9 | note | Inspection Point: Quality Control Activity - Cabling installed, secured to support systems, no excessively tight bends on cables.
567a99ec-88a8-5b7a-994d-b56652cc543f | note | Acceptance Criteria - Cables adequately Secured, Cable Ties cut off clean with no sharp edges.
779687da-19c3-5877-9713-39064f3b3942 | note | Verifying Document - This ITP
831e86c9-bcbb-5c03-9b16-ffce366158bd | note | Frequency - Once
b970d5ed-e4e5-5a49-a8c1-05a577fac7ca | note | Inspection Type (Visual, other) - Visual + Photograph
4efb0008-c86d-559c-9948-3ebec2f5418a | note | Inspection: Key - I
da0982e8-2a5a-590d-bd10-d1b85205196e | note | Inspection: By - IP
68bc0828-2d90-4c49-9ce4-389530f14b43 | checkpoint | 4.8 - Terminate cables into Generator Connection Cabinet
628888a7-fae5-5e64-a602-369c4fea233e | note | Inspection Point: Quality Control Activity - Cables fit off into cabinet.
a939551b-5dfb-5772-a364-4565e695ebbc | note | Acceptance Criteria - Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated
dd18a32b-be01-563c-8307-18cec923f956 | note | Verifying Document - Cable/Cabinet ITR's
4b9ad180-6605-5032-8764-6d18fd50ecd6 | note | Frequency - once
5dadad44-1738-5aa0-885e-64051168e953 | note | Inspection Type (Visual, other) - Visual + Inspection
58b8b148-de02-51c2-aaed-42e761d30c58 | note | Inspection: Key - I
fe64f335-eb7e-58d5-9716-9a35aba2f7f9 | note | Inspection: By - IP
3924b0c0-92db-4e49-8a55-b66cd4adc663 | checkpoint | 4.9 - Isolate Supply to Pump Station at WTP Switchboard.
daf16689-1cfc-50e6-b90a-071b382f0007 | note | Inspection Point: Quality Control Activity - Supply isolated
82aa87ba-e962-5df9-9b4b-933a70496482 | note | Acceptance Criteria - power to Pump Station isolated, no voltage/ current present on cables
439d1c3e-74cb-57b4-aecc-26c17c5c7fcb | note | Verifying Document - This ITP
be06ff4a-6d64-5e0d-9c7e-1fb1156fb6b0 | note | Frequency - once
5a127de6-0192-541c-a85f-d78e7d03b5b4 | note | Inspection Type (Visual, other) - visual
0eed59b2-413d-5d46-9393-715382d6925f | note | Inspection: Key - W
25f3c9f8-71c6-5637-92a9-86628375e68d | note | Inspection: By - SP
dadd2b9c-0e7f-4489-9d9b-0ef76927ee41 | checkpoint | 4.10 - Disconnect Mains Supply from Pump Station Switchboard and relocated to Changeover Cabinet
0069e81a-5294-50ba-acc1-99cae060a2c8 | note | Inspection Point: Quality Control Activity - Cables disconnected and routed to changeover enclosure
b3550e16-085b-5321-b7fd-b97063a34c56 | note | Acceptance Criteria - Cables clearly identified for origin/phase.
f0a84d7e-2348-5808-8a39-3210dac82d5d | note | Verifying Document - This ITP
058ee62d-001b-56d8-852a-e9bb2479ce56 | note | Frequency - once
edca9a42-03e1-5f20-94a0-4a84a069bd8a | note | Inspection Type (Visual, other) - Visual
94bb877a-0bdb-51f6-a59f-332ea4c90993 | note | Inspection: Key - W
5eefe30c-af50-5358-805b-1dc58729d42e | note | Inspection: By - SP
a335b793-0d88-4809-9bcf-55fe39425fa5 | checkpoint | 4.11 - Terminate cables into Generator Changeover Cabinet
11defddb-9087-5e95-9b6c-45f408779663 | note | Inspection Point: Quality Control Activity - Cables fit off into cabinet.
489d414f-e788-5cc4-8f1f-f575eee6da29 | note | Acceptance Criteria - Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated to correct terminals on Changeover Switch.
7fea71ce-469e-59e4-a73a-b5e3894cf2ce | note | Verifying Document - Cable/Cabinet ITR's
8094ae2f-2d3b-53e6-b631-f097eeb8f93e | note | Frequency - once
174de937-bcca-5fd2-b11a-9ab36edbce94 | note | Inspection Type (Visual, other) - Visual + Inspection
6b1adda8-cbcf-5a44-95fb-86b8e1e6ef25 | note | Inspection: Key - I
81866cee-a04f-5482-96b5-84dd9991e431 | note | Inspection: By - IP
3dc78cf9-3378-4e52-b965-9b050bdfdfce | checkpoint | 4.12 - Install New Cables Between Changeover Switch And Switchboard
63d205a3-c811-54d4-b98b-56db50c8a007 | note | Inspection Point: Quality Control Activity - Cables installed and secured to existing cable trays
6715b956-b6c5-5748-951a-8ea94f3c93d3 | note | Acceptance Criteria - Cables are correctly sized, secured adequately to cable trays.
28d965b2-d886-5579-a483-d098e55bc1a9 | note | Verifying Document - Cable/Cabinet ITR's
78a19dff-19d0-5b3a-b538-b4ba849c061f | note | Frequency - once
2ebb886e-a5c9-5ddd-b7c7-ef9bcbaae884 | note | Inspection Type (Visual, other) - Visual + Inspection
955f3db0-8d1b-5531-a86b-2c101d0d17ff | note | Inspection: Key - I
91a7a072-c604-5a75-bb22-15e2097b1aad | note | Inspection: By - IP
545a1b06-6a0d-4077-be43-c4093d694e6d | checkpoint | 4.13 - Terminate Cables into Switchboard
7dac9b4e-981b-5583-ac63-78604071fbd7 | note | Inspection Point: Quality Control Activity - Cables fit off into Switchboard and Generator Changeover.
3129ebd5-d534-5b82-b231-b2b39c2ff9cb | note | Acceptance Criteria - Cables enter into Enclosures through appropriately sized glands, cables fit off correctly and terminated
b7579f12-0a10-5bd1-8d42-f7ad514bdf42 | note | Verifying Document - Cable/Cabinet ITR's
632de2f0-b683-52d1-86ab-c86ab5b38167 | note | Frequency - once
38582044-5ddc-52be-b664-db8eb4a1a293 | note | Inspection Type (Visual, other) - Visual + Inspection
c0abef4a-9aec-55a8-9678-3d8b6ef2a32c | note | Inspection: Key - I
5138c35e-f36f-5284-99df-5f8e025604f0 | note | Inspection: By - IP
80def3a8-cedc-4cdf-b4da-56c06114d3d3 | checkpoint | 4.14 - Mount Switchboard
41da51a5-b76a-5d19-ae59-9f9ff613f8ac | note | Inspection Point: Quality Control Activity - Cabinet Mounted
c3470abf-71db-5f89-9084-d7f461cbf13c | note | Acceptance Criteria - Cabinet is mounted securely, all bolts tight, seals intact and in good condition
085b9d97-4dc0-51be-926d-14f362bb5dd5 | note | Verifying Document - This ITP
b690d838-1598-5cea-aff3-19274c13cc71 | note | Frequency - once
2eab083d-fff1-582f-83fc-5e81f866a3cd | note | Inspection Type (Visual, other) - Visual + Photograph
4520489b-8ad1-5bbb-aa70-f623f3d4d31c | note | Inspection: Key - I
5b3b311f-665b-5da7-a1ff-6cd73c2d5ff6 | note | Inspection: By - IP
ae49b9c9-14df-4237-ad9f-0a4faac621ca | checkpoint | 4.15 - Terminate cables into Switchboard
6f17f72f-f0f4-5c73-bbd4-f84c69df0ec9 | note | Inspection Point: Quality Control Activity - Cables fit off into cabinet.
72137d96-a491-5725-8423-6b598c9490f0 | note | Acceptance Criteria - Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated
c4063b67-51a4-5faa-9ce5-632005c3487e | note | Verifying Document - Cable/Cabinet ITR's
6647b575-778d-5440-9b5b-b620cfdb28d2 | note | Frequency - once
6aff7de9-3e32-5277-837e-f545705cf308 | note | Inspection Type (Visual, other) - Visual + Inspection
98219d07-437b-5370-9ece-83d4d900dc71 | note | Inspection: Key - I
c8d81cf6-73da-5426-b16a-14e8fd512acc | note | Inspection: By - IP
c51b8315-3bdc-4f6c-baf3-08d1093b7e15 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
e432896a-2908-4213-8a2d-a2020a7d103d | checkpoint | 5.1 - Switchboard
f8c1533d-19ff-54fa-9144-7503353ee2b8 | note | Inspection Point: Quality Control Activity - New Cables installed, insulation, continuity and polarity tests completed, phase rotation confirmed
41525fa5-c17b-5714-a55c-be7e11defcaf | note | Acceptance Criteria - Electrical Testing completed, board Livened and operating as prior to modification.
40ad7191-3e20-543c-80f8-a8504b860eee | note | Verifying Document - Cable ITR's/ COC
543c6303-3727-51e5-9fe9-2e598b996de0 | note | Frequency - once
1f18caae-eb78-5a08-8c58-b919f887be1f | note | Inspection Type (Visual, other) - Visual + Document
730399b2-881a-59f5-aa80-68e03fbe9366 | note | Inspection: Key - I
da3be3bf-b3de-58be-90eb-dd116b5456db | note | Inspection: By - IP
4ce92b45-90df-4ec6-8687-308e30583823 | checkpoint | 5.2 - Generator Changeover
afa88dd0-f249-5e3a-871c-021f03f90d8e | note | Inspection Point: Quality Control Activity - Cabling installed and terminated. changeover tested and inability for back feeding of supply confirmed.
72f3e512-56c1-5968-810f-e0e053f5eb5d | note | Acceptance Criteria - Changeover operation Verified as satisfactory. unable to live test due to lack of a suitably sized Generator
90ab57ad-c48e-5233-9c05-f24b2ea371e3 | note | Verifying Document - Cable/Cabinet ITR's, COC, ROI From Inspector
67c27c66-6a36-594c-b272-5e4d624617dd | note | Frequency - once
02aafd17-778d-50a9-9552-fd59436f8c90 | note | Inspection Type (Visual, other) - Visual + Document
55d62257-004f-524c-ad5e-7bb68d542971 | note | Inspection: Key - I
77d37dd3-ba93-5710-b6a7-2bc7c2955df3 | note | Inspection: By - IP
8b95fd4d-8397-41c4-92e1-fbd46c961536 | checkpoint | 5.3 - Generator Connection Cabinet
a1cba8ba-c3dc-5ec5-861b-5fa7711d5c15 | note | Inspection Point: Quality Control Activity - Generator Connection Cabinet mounted, cabling fit off, testing completed.
0f33522e-339c-50de-ae7a-399abeb94048 | note | Acceptance Criteria - Cabinet Mounted Securely, polarity of connections correct,
42c53407-d8dd-5cbf-9ec6-b7daf5b9c9ad | note | Verifying Document - Cable/Cabinet ITR's, COC
a0a489bb-6aaf-5a21-9d06-da63cf639992 | note | Frequency - once
f3af5446-7b8a-59fc-b3a1-d3b5172272f8 | note | Inspection Type (Visual, other) - Visual + Document
6a61a77f-9f4f-5f71-8b91-04f9bd9d8594 | note | Inspection: Key - I
b359d0d6-d03f-5862-9ced-9acfb97ef546 | note | Inspection: By - IP
7ac15666-5ecf-4674-91f8-a33d3ecf7204 | checklist | 561483-ITP-011 - Pumps 1 through 6 Commissioning - HOLD POINT | itp | 561483-ITP-011 - Commissioning Pumps 1 through 6
9f0f9b2e-e892-4a37-8f68-6a25850c77f6 | section | SECTION 3 – RECEIVING INSPECTIONS
c2b176f1-c24e-4cb1-af1b-5b63a2efbd80 | checkpoint-no-value | Note:
319ed140-7e7b-56cd-aa12-3d1c4d3ad97a | note | Pumps have been set to match the existing pump performance temporarily. This ITP is for the final commissioning of the system
6668e8ea-6da2-4809-9629-8864f2436bbe | checkpoint | 3.1 - Pump 1
92d87a05-6c02-5229-8d34-5457acd96bed | note | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
7c4d7f36-3414-580b-ae59-1fd81a4aac35 | note | Acceptance Criteria - VFD 1 configured to match existing pump performance
a3df2054-29ff-5e9c-9c19-07dde87c2e1a | note | Verifying Document - 561483-ITP-009.1
129ad61f-8c0b-514b-9733-f079f09d9529 | note | Frequency - Once
fd520680-d7c9-5dd0-9edc-f8c91cdd2395 | note | Inspection Type (Visual, other) - Visual
62c08ee5-0f40-57ea-a3c8-822f74d2fdd0 | note | Inspection: Key - I
f6e9ba6b-9eb5-5319-a274-7b3b39f75e60 | note | Inspection: By - IP
8cfa7e12-b112-448d-8fb2-04e76b3c2573 | checkpoint | 3.2 - Pump 2
0d3c51e9-9bb5-5c05-b4e5-a30896aaa906 | note | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
9f43e2f9-9c6b-5a9e-9886-79b36f5c8dd5 | note | Acceptance Criteria - VFD 2 configured to match existing pump performance
d750d97c-83c5-50a3-b814-f19e6a3884ba | note | Verifying Document - 561483-ITP-009.2
cfef5316-ef15-52dd-acec-75ebae3d85e7 | note | Frequency - Once
66c95a3e-a55b-5516-b2da-55e506a86e2f | note | Inspection Type (Visual, other) - Visual
e8ad95ab-1e1f-5edc-9e72-0db0849031e4 | note | Inspection: Key - I
bebaf1f7-9b69-52ff-a38b-47a2f41051f5 | note | Inspection: By - IP
01e40565-96d0-4f70-a4ad-340bdf5c55a6 | checkpoint | 3.3 - Pump 3
d98a99a5-bd96-50d1-ba47-7ac1a38be957 | note | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
da76362d-f4dd-5616-ba47-b899333eadc1 | note | Acceptance Criteria - VFD 3 configured to match existing pump performance
ea1fceed-a262-5b2b-83ea-d57684395d6b | note | Verifying Document - 561483-ITP-009.3
c111d97d-0a02-5871-a448-22295049fa1d | note | Frequency - Once
105ff44a-b63f-5b7d-9666-7d4afc4e23f5 | note | Inspection Type (Visual, other) - Visual
7e373f9c-a682-5c43-a6d9-f1a6c7fe643d | note | Inspection: Key - I
b8b78498-d2cd-54ba-b9eb-7cb55f731ebe | note | Inspection: By - IP
f8877f39-87bf-4489-af06-7b6599b6c349 | checkpoint | 3.4 - Pump 4
978ed9e9-6c02-5a5d-af5a-0267ed3d55d2 | note | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
96d4b1f2-8b5a-5df4-9d9e-d2706912383f | note | Acceptance Criteria - VFD 4 configured to match existing pump performance
23a6fe1a-1143-501d-abce-94ee9778e044 | note | Verifying Document - 561483-ITP-009.4
c516ce3d-0549-5fbc-b745-1386e7e9f6f4 | note | Frequency - Once
d58e0f56-1397-5314-97d4-7afff04565ab | note | Inspection Type (Visual, other) - Visual
6374d2f7-76d4-50f1-b7af-a933a3c04ef5 | note | Inspection: Key - I
978ed2f3-234d-534f-b18d-1a340bcf6b76 | note | Inspection: By - IP
297deca8-2459-4b35-882e-bdcf74c6c84c | checkpoint | 3.5 - Pump 5
8db83fe4-ecf3-5c39-afb4-ed6c9267465b | note | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
411cb200-436a-52df-8016-105bc952fd64 | note | Acceptance Criteria - VFD 5 configured to match existing pump performance
6d12cae7-af6c-5c9c-8fd0-96141086c5c6 | note | Verifying Document - 561483-ITP-009.5
5b586009-3ab1-597f-80fa-adbbd917b54c | note | Frequency - Once
82125e2f-5372-5016-8b37-dee515ae1f10 | note | Inspection Type (Visual, other) - Visual
78c3384e-66b5-5a4b-906a-131c8d843fe1 | note | Inspection: Key - I
18d836e7-e9fc-5b15-b5d8-6afd95d6593f | note | Inspection: By - IP
9151797b-e42c-4d16-a054-bcb0c7fb1db8 | checkpoint | 3.6 - Pump 6
ec73a008-6ed3-5e99-a189-464fa6ab5dcf | note | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
f35afe18-b679-564f-8d1e-095b0f58cf93 | note | Acceptance Criteria - VFD 6 configured to match existing pump performance
a1f8a8d5-da46-5a0b-af14-1d68143f2b3e | note | Verifying Document - 561483-ITP-009.6
9ac33c2a-651e-52e0-a489-2ca9a819477e | note | Frequency - Once
79531ffd-c821-5df5-8440-53bba893b286 | note | Inspection Type (Visual, other) - Visual
e1ad19e5-a81c-50e9-bb6d-517de09ef19e | note | Inspection: Key - I
f056b11f-7e1a-55a7-bdfc-5a46d474e992 | note | Inspection: By - IP
e3835d11-9fb1-4a91-a978-08d105ed82de | section | SECTION 4 – IN-PROCESS INSPECTIONS
899a216b-cca1-40d6-89db-d3e2abf64095 | checkpoint | 4.1 - Pump 1
9b1dee19-beaf-5fa8-92ab-a6589b9d62a5 | note | Inspection Point: Quality Control Activity - Set pump 1 final pressure and flowrates
a99ad28c-1721-54e2-884c-263cd40942fe | note | Acceptance Criteria - Pump 1 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
e6685b1f-0ab2-57b6-82c4-4cc4df89ab01 | note | Verifying Document - Grundfos controller display/Commissioning sheet
6830fb78-db26-5bc9-88a6-450de3e68466 | note | Frequency - Once
da8807e2-bca2-5134-9d5a-0577484ccdce | note | Inspection Type (Visual, other) - Visual / Photograph
70c0350e-244f-5086-93c1-fc2b67814725 | note | Inspection: Key - O/W
b04b70aa-8293-590f-a5bd-f5cbe25c4bbb | note | Inspection: By - Grundfos Commissioning Engineer
5e640975-6c79-45c4-889f-40db89167b6d | checkpoint | 4.2 - Pump 2
2cea12e2-8891-5eca-85a9-bf28b5e0478d | note | Inspection Point: Quality Control Activity - Set pump 2 final pressure and flowrates
fe2b88ac-a1b3-5863-a03c-701cbbb2bde6 | note | Acceptance Criteria - Pump 2 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
ca818dc1-d804-52e5-b6a0-9f2bb2e3e32e | note | Verifying Document - Grundfos controller display/Commissioning sheet
9c28141f-d2d7-5d0e-b847-3807d3e068f2 | note | Frequency - Once
cf954d57-bf9c-5cd6-8b3b-204d6016288a | note | Inspection Type (Visual, other) - Visual / Photograph
8d5632df-3f70-5a1a-b8eb-1440fad45495 | note | Inspection: Key - O/W
42babf06-39c3-5688-8254-6a8b402bf1ce | note | Inspection: By - Grundfos Commissioning Engineer
f12b468b-c00b-4f77-a76d-1f2a77b8d1c9 | checkpoint | 4.3 - Pump 3
273045b9-977c-53c5-8098-b553e3c92464 | note | Inspection Point: Quality Control Activity - Set pump 3 final pressure and flowrates
e2fe5bb5-2692-5476-a344-9c5636094666 | note | Acceptance Criteria - Pump 3 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
043017db-378e-5938-8294-9ca6ae448a6b | note | Verifying Document - Grundfos controller display/Commissioning sheet
6f21e893-435c-5ad9-bf9a-99afbd6d0844 | note | Frequency - Once
c789560c-c189-5b6d-9928-9643d345c913 | note | Inspection Type (Visual, other) - Visual / Photograph
6326bd9d-a147-5dd9-bbd8-ca70e1c6509a | note | Inspection: Key - O/W
6cf67b42-d0b9-5145-abca-06b80dd7765c | note | Inspection: By - Grundfos Commissioning Engineer
bff242d7-f6ad-40e9-b9c7-424bdaff1e49 | checkpoint | 4.4 - Pump 4
1bdd180a-d56a-523e-aa1b-e2a5e2639f61 | note | Inspection Point: Quality Control Activity - Set pump 4 final pressure and flowrates
f6bcbf3e-e2cd-5229-b27b-71e8e816f0bd | note | Acceptance Criteria - Pump 4 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
6d3f9e45-c977-5891-a340-14eeae966402 | note | Verifying Document - Grundfos controller display/Commissioning sheet
d0e9897e-cc5c-5ec5-b36c-efcb31d6d07d | note | Frequency - Once
f9e855c7-cff5-5b3f-b167-1601e912e154 | note | Inspection Type (Visual, other) - Visual / Photograph
fc524477-6575-511f-aea2-e3bb66326cc5 | note | Inspection: Key - O/W
7c4191a6-86c4-5ba3-b888-9b145a130ff4 | note | Inspection: By - Grundfos Commissioning Engineer
ec4a2892-1b47-4e1b-9680-cb3278fc7a23 | checkpoint | 4.5 - Pump 5
618556d4-25d8-58ee-94f3-c53454cb20c1 | note | Inspection Point: Quality Control Activity - Set pump 5 final pressure and flowrates
ca730cb9-2a61-503a-94a3-bb2ba93a652d | note | Acceptance Criteria - Pump 5 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
2f78bd4e-5200-51fd-b665-bee9bfea8a41 | note | Verifying Document - Grundfos controller display/Commissioning sheet
1e6a1fad-11e2-5ed9-b3f5-ec71b0c859d8 | note | Frequency - Once
9052e97f-de81-5c41-9861-c1571ffbea1b | note | Inspection Type (Visual, other) - Visual / Photograph
25d24fb0-4591-56ec-9548-16aff6d639e8 | note | Inspection: Key - O/W
9f1a3eb2-ebae-52c0-8331-3ab3a6cebdbc | note | Inspection: By - Grundfos Commissioning Engineer
6368e54d-367e-4c33-8fc3-78f22621da1b | checkpoint | 4.6 - Pump 6
69c33f73-dfdb-5d5d-bcf5-037ef5f3068c | note | Inspection Point: Quality Control Activity - Set pump 6 final pressure and flowrates
55706778-a6ca-5e75-a2e8-139855c7b307 | note | Acceptance Criteria - Pump 6 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
af0ffe48-ce6e-5ef7-84e1-86f1212b3323 | note | Verifying Document - Grundfos controller display/Commissioning sheet
0a357d85-28c5-5d5b-98a5-95287e4e6f4a | note | Frequency - Once
e1ac85c4-7a9f-5793-8ad8-57f13fc1e14d | note | Inspection Type (Visual, other) - Visual / Photograph
72e46c24-ff2f-5846-a4ec-193d9ccd67f6 | note | Inspection: Key - O/W
1bd370bc-5c11-5659-b0d4-2ccd878c541d | note | Inspection: By - Grundfos Commissioning Engineer
854af8b2-469d-415b-bfa3-eca3cac65f0b | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
4a2b1b4f-bde3-42ea-b4a9-3e7c2b99525a | checkpoint | 5.1 - Pumps 1 through 6
7d13c1c2-4524-51a9-b6ae-a0891d5729c5 | note | Inspection Point: Quality Control Activity - Full pumping duty is restored from Mt Grand to Wingatui Reservoir
911a1893-7886-5672-89dc-864c21062f42 | note | Acceptance Criteria - Flow rates equal the specified design value (130 L/sec High flow)
8b9e13fb-fb84-5935-893d-55c4a057c661 | note | Verifying Document - View on Grundfos Controller
19638a30-08ae-5f16-98bf-76c32feb7c31 | note | Frequency - Once
08e8bc95-c584-5e0d-8768-dc22780630b1 | note | Inspection Type (Visual, other) - Visual / Photograph
d1487db9-00d2-5767-9097-ab43ce39bb48 | note | Inspection: Key - W / H
43377bfc-a0b6-576b-acbc-e2001921eb87 | note | Inspection: By - CR
c2a56518-d677-4730-925b-218bd511918f | signoff | HOLD POINT
61e6c7a4-f35d-45f0-981c-1c0549e204f0 | checkpoint | 5.2 - Pumps 1 through 6
cc068fb2-3f11-5f1e-a3ce-408e43fe35e3 | note | Inspection Point: Quality Control Activity - Pumping duty is restored to Stoney Knowe Reservoir
fa8a68eb-d701-563a-bf42-6ac44d1c0215 | note | Acceptance Criteria - Flow rates equal the specified design value (70 L/sec High flow)
34c47277-72a1-5d32-a363-b54cad80714e | note | Verifying Document - View on Grundfos Controller
5562d471-de81-5ad5-afb9-221b50b9bb97 | note | Frequency - Once
d3280ac0-bd0f-5f30-bbd6-ae272fa13376 | note | Inspection Type (Visual, other) - Visual / Photograph
8204ea7c-3d0e-5d5d-9c53-f9f547983da2 | note | Inspection: Key - W / H
d92fce78-e1fa-5a31-b05a-09d67ac6fa27 | note | Inspection: By - CR
5f6f2be7-fe0b-4e9b-bbaf-22c68e7fcab6 | signoff | HOLD POINT
d2409c53-bc53-4ae9-aa42-378fc2e9928b | checklist | 561483-ITP-012.1 - Wingatui Control Valve 1 final commissioning | itp | 561483-ITP-012.1 - Pipe Spool & Control Valve - Inspection Test Plan
6fdaf2a1-0a2a-4ba1-b0b7-13919b5d66cb | section | SECTION 3 – RECEIVING INSPECTIONS
f29e821f-e9f7-4f8e-be30-52b1f08dd3bc | checkpoint | 3.1 - Pipe Spool Installation
03c35b00-14e0-58ce-857a-49ba9cbf398b | note | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
7af4f6ea-304e-5788-9c64-fe76718b996c | note | Acceptance Criteria - Completion of ITP
69efc3e1-67b6-512e-bbe6-ee65b32388e2 | note | Verifying Document - ITP-002.1
9144b1d1-a99e-53ac-b0b8-9a1108dcb306 | note | Frequency - Once
cddecf68-ad1a-55eb-8fc2-106d0dfd36b5 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
91df3f66-6850-522b-b8e7-fea7cccc739e | note | Inspection: Key - I
d1249328-36d9-554c-abe7-97f2a0da7682 | note | Inspection: By - IP
f743d095-1905-4c5e-a66d-2a2c3ecd2c42 | checkpoint | 3.2 - Control Valve 1 Installation
2e7a1e24-0b7c-5e54-8d32-3b8c8b95541b | note | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
12fbacc6-092c-55ee-95d1-58875d7f97ec | note | Acceptance Criteria - Completion of ITP
06a27369-c20b-529b-9be1-55385a63e291 | note | Verifying Document - ITP-002.1
0d7361ac-1845-5a66-9216-324081c9d002 | note | Frequency - Once
de798324-df2d-5113-8cf2-266ca3736d98 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
787928e3-ead3-54b7-8c81-9ce169efd796 | note | Inspection: Key - I
e7157ec8-748e-5a84-beb0-05fb2371da73 | note | Inspection: By - IP
6ae910b0-45ba-48ba-8feb-dfb0ad1354c4 | checkpoint | 3.3 - Control Valve 2 & ancillaries
c3bb3904-efcb-598b-9fda-d04a01e7b0cb | note | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
c72a753d-8d65-5420-8469-672c97e73e2e | note | Acceptance Criteria - Completion of ITP
5775a151-d6ff-5d3a-93ac-f727fa56ddb3 | note | Verifying Document - ITP-002.2
df3dce8b-2408-5623-bcdd-5870b0c1a24b | note | Frequency - Once
619f6733-5ad8-577f-a535-c8ba9f397a01 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
573565ff-990d-5fa6-97f5-fea354fdf396 | note | Inspection: Key - I
b68f928f-7d9e-5d8d-92e2-1ad3cb8a84d2 | note | Inspection: By - IP
afc73ff9-829d-4cb0-9a9c-1c1810d3ad69 | checkpoint | 3.4 - Pumps 1 through 6 are installed and commissioned
bbdbdbf9-2471-50ac-aa3a-354784ad94b6 | note | Inspection Point: Quality Control Activity - Verify commissioning is complete via Grundfos
b391260e-66d7-5f66-bdec-5416800f3047 | note | Acceptance Criteria - Completion of Commissioning
a6ed8e0a-43da-589a-968d-5a2f955bccd1 | note | Verifying Document - Grundfos report
c8a5de8a-773a-5e01-94a6-28ae51e88bd9 | note | Frequency - Once
a50e68d5-e60d-5915-868e-cd50e3f5313e | note | Inspection Type (Visual, other) - Inspection + Documentation
04c48cbe-6f82-5c90-afe7-55cb68b26e86 | note | Inspection: Key - I
a6ef7bc8-4fec-59e5-a779-c64515b4f98b | note | Inspection: By - IP
93db0f42-5cb9-4493-8b72-a0d476a2042d | section | SECTION 4 – IN-PROCESS INSPECTIONS
91c327dd-6fd8-4954-9a5c-aa649d04644d | checkpoint | 4.1 - Commission Control Valve 1
bc2ef9b4-87ce-59f0-80e6-1e6cc5ecd939 | note | Inspection Point: Quality Control Activity - Set to achieve correct flow rate
0fafbdb5-1dba-585a-9fcc-39962a086206 | note | Acceptance Criteria - 130 litres/sec achieved
448ea817-762c-5176-8407-ce2ff4498b7e | note | Verifying Document - Commissioning Methodology/Claval Commissioning sheet
aa53e8dc-ed96-5fc9-99ee-a4389c508b8b | note | Frequency - once
09680cc4-54a6-53c1-b33b-dec28f042c8e | note | Inspection Type (Visual, other) - Visual + Photographs + document
adb33470-288c-5d48-b5a4-1f52efdf71ac | note | Inspection: Key - I
89f4d62d-ceeb-5c23-bc7e-98682342eeeb | note | Inspection: By - IP
3a110f21-2287-4719-9078-e7b2f3677338 | checkpoint-no-value | Note:
57e86f2e-335c-54ce-80d6-631e20c895da | note | Valve chamber will need to be assessed by Downer HS&E to determine as to whether is a confined space
f328d278-0546-41f8-a886-9e9d4e93de00 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1a5e0379-7a75-4c45-81b7-308704196ec7 | checkpoint | 5.1 - Record Value
91086867-05cd-5252-983c-51cc49c3785f | note | Inspection Point: Quality Control Activity - At completion of valve commissioning
9f303ca7-ef11-51da-a4d2-53124cd007ea | note | Acceptance Criteria - When consistent results are achieved
8234d1b6-ff8f-5efb-aa10-06d86f317815 | note | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
e9edd5c6-06e9-52fa-b0d7-7e45876e7e0d | note | Frequency - once
60ffce97-4d84-51de-bd4e-099d1e4fb72d | note | Inspection Type (Visual, other) - Visual + Document + Photograph
a6773bbb-6f8d-5b7e-87f1-88ac714f32eb | note | Inspection: Key - I
42df18ed-3295-58df-bded-1a13c37ece53 | note | Inspection: By - IP
1ae0293c-8918-41fb-a850-d60486e1e86b | checkpoint | 5.2 - Set Lock nut on pilot valve
fb2034ae-5ef9-50ae-80be-ab67a661c05f | note | Inspection Point: Quality Control Activity - At completion of valve commissioning
f68e4474-0251-5788-9229-56fa1231540d | note | Acceptance Criteria - When consistent results are achieved
eee53a0b-ee92-52be-ac48-14883b1dd6d3 | note | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
a489c02b-3dd3-5c72-95fd-7694cb0808ca | note | Frequency - once
2ea7db6d-aedb-5745-89ea-02b774118288 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
173ad314-6b7f-5806-a297-9faebc292169 | note | Inspection: Key - I
93c32865-1ffb-5901-b218-3ea7e7433800 | note | Inspection: By - IP
f4bd3608-840c-4038-9db9-31da55996db6 | checklist | 561483-ITP-012.2 - Wingatui Control Valve 2 final commissioning | itp | 561483-ITP-012.2 - Pipe Spool & Control Valve - Inspection Test Plan
44adbbdc-ed01-4207-bc40-bf32038160a8 | section | SECTION 3 – RECEIVING INSPECTIONS
1b9943f6-d72f-4c2f-8d6b-3f137cb20d28 | checkpoint | 3.1 - Pipe Spool Installation
a07ef2ee-f245-5268-9c53-ac4db68a1acc | note | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
b49e57e1-96ed-5778-9fba-e12d5dad1d14 | note | Acceptance Criteria - Completion of ITP
2e55d6a6-ef6b-534f-80a8-375ccae917ed | note | Verifying Document - ITP-002.1
12120305-db61-58fe-9b00-b12a0201799a | note | Frequency - Once
44d000a8-795f-5337-86ec-1bfdc7f1697d | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
1ab81534-f26a-5284-8e20-f0512b74964d | note | Inspection: Key - I
d36f0a10-6914-5f5f-9e3d-b29bcc6af706 | note | Inspection: By - IP
a72f6d95-97b8-48c5-b3a5-a106deb63db6 | checkpoint | 3.2 - Control Valve 1 Installation
8ba37cb2-1415-51a1-8980-46843d28b6fd | note | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
a19d0e8e-50c0-5bec-bfc3-7684b580ab6e | note | Acceptance Criteria - Completion of ITP
5b4cb318-6c11-5243-8d98-570453bfd810 | note | Verifying Document - ITP-002.1
39f438af-73f7-5e5e-8aa5-00ff34519c7e | note | Frequency - Once
6a41069e-fce5-53d9-8e2a-a9dd3b54cead | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
8a93fbf1-eb55-54f1-af86-46843536eb3d | note | Inspection: Key - I
55632346-85b4-5acb-9a62-806ac6d3578e | note | Inspection: By - IP
06f3ba89-9383-49c6-ae0d-854b91c496e2 | checkpoint | 3.3 - Control Valve 2 & ancillaries
ed6d085b-946e-5c90-9e9f-ac58e452115f | note | Inspection Point: Quality Control Activity - Valve assessment. All bolts are tightened and torqued to their correct values
fb8bbe7a-c847-5a7d-a6d6-48cb6e031cbd | note | Acceptance Criteria - Completion of ITP
11a71922-3ec5-536d-b78a-850cda50a9e0 | note | Verifying Document - ITP-002.2
47dd38b4-0413-5c87-9706-c057f9c8a214 | note | Frequency - Once
ec4636f6-d96a-5c75-9f9a-a731210a5e10 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
17e45797-329d-5211-b1d1-6a8141c3c7d6 | note | Inspection: Key - I
7809f576-c963-544c-ac20-d13b50762ec2 | note | Inspection: By - IP
1f802dc6-2c23-4e7f-9afa-9bf6957c6819 | checkpoint | 3.4 - Pumps 1 through 6 are installed and commissioned
1108282f-e6d0-5bb8-8097-cd27d4abf5bb | note | Inspection Point: Quality Control Activity - Verify commissioning is complete via Grundfos
d9d7151d-c792-5e0e-a9dc-1bc70f2b2e8e | note | Acceptance Criteria - Completion of Commissioning
b64f54a2-470a-5a7b-b191-62c4af970a5c | note | Verifying Document - Grundfos report
ce2f3e69-9e58-5c5a-a63d-cee362ecde9e | note | Frequency - Once
24886cf2-7718-5254-9e8c-33ed26341c92 | note | Inspection Type (Visual, other) - Inspection + Documentation
bf98b387-0e1d-5a9e-a61f-adec4da95f93 | note | Inspection: Key - I
46ac103c-dcf4-51fc-a64b-fa3a5a903f20 | note | Inspection: By - IP
59b836c3-9ed8-4b8c-bffe-68f56519a5f4 | section | SECTION 4 – IN-PROCESS INSPECTIONS
c31d3698-119f-491c-b5b5-3938a26fe7e5 | checkpoint | 4.1 - Commission Control Valve 2
1c4d3682-1d80-5916-b376-45bdeb09650e | note | Inspection Point: Quality Control Activity - Set to achieve correct flow rate
71f04351-4d67-50fc-9651-7a37a7141103 | note | Acceptance Criteria - 130 litres/sec achieved
c87159c4-bdea-5baf-ba7c-dc3a6c6ba85d | note | Verifying Document - Commissioning Methodology/Clavel Commissioning sheet
7c8514c0-92f7-5d4f-9eaf-c426d6bb9dc9 | note | Frequency - once
efcefd45-0b75-516a-8969-1c75da4f3e0d | note | Inspection Type (Visual, other) - Visual + Photographs + document
77a718d7-7d14-574f-95aa-ddf3190a566d | note | Inspection: Key - I
1b6d4e78-14e4-5a31-bc6a-e979617bf988 | note | Inspection: By - IP
1574cfd7-9fc7-4097-9585-a8debb417827 | checkpoint | 4.2 - Solenoid function test
9404a359-8a96-5d4a-9069-61ff160f40bd | note | Inspection Point: Quality Control Activity - Test function of solenoid shut-off
1a9b92e3-e435-5c09-8924-5e949e148f29 | note | Acceptance Criteria - Shut off when reservoir is full
1117fe9f-79c4-5b1d-809d-c00ccc05345b | note | Verifying Document - Reservoir levels
5788d447-f0ef-5e65-b674-7230984884a2 | note | Frequency - once
2695a5a8-4263-557b-8e24-b91a1afd8094 | note | Inspection Type (Visual, other) - Visual + Photographs + document
a90909f9-6a89-502e-96d2-f9b73fada76c | note | Inspection: Key - I
7e0a9788-f90e-5c89-a806-d3344034035d | note | Inspection: By - IP
5cc91715-221f-4ab7-9bf4-f3813de620df | checkpoint-no-value | Note:
9c453ff5-d84b-5e79-a4c4-5ef627c588d9 | note | Valve chamber will need to be assessed by Downer HS&E to determine as to whether is a confined space
bb24a379-c54b-4080-b3fc-d367aa2b9049 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c05a70ec-34a0-4662-86df-1b1f209bf7c8 | checkpoint | 5.1 - Record Value
32382c53-aab2-537d-afce-4860f1b2e89a | note | Inspection Point: Quality Control Activity - At completion of valve commissioning
5df4cd71-449b-5f60-b544-e21285390ba4 | note | Acceptance Criteria - When consistent results are achieved
e510d84c-5f4c-5137-9468-73b664455a73 | note | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
101318a4-be97-5e91-a007-9dc126621877 | note | Frequency - once
cc3080fa-6ed8-5503-a00a-564506bb0635 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
e2dec87a-87af-599c-a8f2-e7cb7ccb4dfc | note | Inspection: Key - I
8f55a27b-2ffb-572b-8fa3-c0251d5aefd9 | note | Inspection: By - IP
7113c1b0-3c29-4328-aa1f-77bcc2e107ea | checkpoint | 5.2 - Record solenoid valve feedback values
d81703bd-6a7a-5f83-ae7e-3a30c81e55f4 | note | Inspection Point: Quality Control Activity - At completion of valve commissioning
48f39664-d8bb-5443-b4c6-8eebfc4ab49e | note | Acceptance Criteria - When consistent results are achieved
90247025-de92-5d02-aab0-adde746a90e6 | note | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
ef462314-e052-5b13-877e-ce74aa089558 | note | Frequency - once
70394d26-4d1b-5a07-8d47-7b85bbb8e2ce | note | Inspection Type (Visual, other) - Visual + Document + Photograph
9d9eb2b5-b74f-59d5-b866-c6aeeab84e5e | note | Inspection: Key - I
95dfb914-aa64-5005-b47d-6122be889fe3 | note | Inspection: By - IP
b5e89535-0ae4-442b-a358-c94d2d1fb2ec | checklist | 561483-ITP-012.3 - Stoney Knowe Control Valve final commissioning | itp | 561483-ITP-012.3 - Pipe Spool & Control Valve - Inspection Test Plan
93c53251-cda4-4b3c-a9be-47f49017380d | section | SECTION 3 – RECEIVING INSPECTIONS
a8126006-f60f-40fb-89cb-d88278a570ef | checkpoint | 3.1 - Control Pilot Valve Installation
3e16b6db-0bd5-5a21-99ab-2198280a2cfa | note | Inspection Point: Quality Control Activity - Installation completion. All valves & Unions installed
4be8b996-459b-5b9c-a846-dd597a6c24b6 | note | Acceptance Criteria - Completion of ITP
94189188-d7aa-59fa-ab98-c0d186839a8b | note | Verifying Document - ITP-002.3
c4fa323f-f1bb-541c-84af-afb39836f9a1 | note | Frequency - Once
08a87c58-f2ff-5e14-a594-ce3f763e47ff | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
53c53b83-53f1-5ade-8399-6515af6a99e2 | note | Inspection: Key - I
98c497f1-8439-570a-b9e7-e9e48022fe32 | note | Inspection: By - IP
841b7fbe-4d06-43b3-90ac-ab22cf306091 | checkpoint | 3.2 - Stoney Knowe Pipeline
0a819f0f-afed-5582-9bdd-2f29b7f8a417 | note | Inspection Point: Quality Control Activity - Pressure testing
3665ca42-cbbb-5550-8f5c-b3f7fd110d70 | note | Acceptance Criteria - Pressure test pass
b14f5302-64ea-56ab-a941-63ef33e48150 | note | Verifying Document - ITP-004
2de173db-f1ad-5f69-9cc2-a90b3cb05bad | note | Frequency - Once
ce973eba-e592-5524-b414-107b9db82639 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
ea34472e-3ea6-5797-ba87-8ecbb13484f2 | note | Inspection: Key - I
a874fa34-010f-57a7-ab99-b5895f774831 | note | Inspection: By - IP
db2e2b37-d49a-44f8-ad98-12ea51e09db8 | checkpoint | 3.3 - Stoney Knowe Pipeline
abdaef2c-9f4d-5344-b38e-1c4dae242de2 | note | Inspection Point: Quality Control Activity - Pipeline disinfection
0005fa4a-692a-52f7-b910-d9e0bbd9b4b3 | note | Acceptance Criteria - Pipeline disinfection pass
7fc07c53-8c41-52fa-b09e-66e8011c5efe | note | Verifying Document - ITP-005
d5d0a368-370c-5328-bcd9-c4b7970a8c9a | note | Frequency - Once
1e526679-da9d-5402-a474-1f60695255c1 | note | Inspection Type (Visual, other) - Visual + Inspection + Photograph
1d22bea8-20c9-5ad4-ab84-2cd3767c3ffc | note | Inspection: Key - I
190d5676-d3f2-55d0-b210-f8f22cfb20fc | note | Inspection: By - IP
ce2c0eac-6037-4fb2-80f6-67ce84b54f8b | checkpoint | 3.4 - Pumps 1 through 6 are installed and commissioned
34f4b7ef-9a02-5f5a-bcfb-89c9e1d52517 | note | Inspection Point: Quality Control Activity - Verify commissioning is complete via Grundfos
e160b914-2791-5ed0-9384-66e249121be1 | note | Acceptance Criteria - Completion of Commissioning
d271ae6b-da36-57f0-ace5-f51d59d089c3 | note | Verifying Document - Grundfos report
6a55d56b-18d4-5503-b181-10fa7141516a | note | Frequency - Once
60ef42b3-2bbd-5f84-ab55-35de39212cd3 | note | Inspection Type (Visual, other) - Inspection + Documentation
96147985-e043-5904-9cc3-caec86a00336 | note | Inspection: Key - I
dba5bd75-ac57-5419-831b-985836ae78b0 | note | Inspection: By - IP
49e3142c-3f99-48c7-ae14-4c43c8cc4a44 | section | SECTION 4 – IN-PROCESS INSPECTIONS
cd534f0a-c0f6-466d-aa2a-2da7043cad56 | checkpoint | 4.1 - Commission Stoney Knowe Control Valve
951dfc72-eb1f-5d44-9c67-b58add33e1a0 | note | Inspection Point: Quality Control Activity - Set to achieve correct flow rate
42997a73-f753-5ce2-ab5b-cf4d8fbd5744 | note | Acceptance Criteria - 70 litres/sec achieved
fc923aff-87cd-5abe-8bc9-02c3397bfc16 | note | Verifying Document - Commissioning Methodology/Clavel Commissioning sheet
6fbac5b7-630d-5dba-83b6-cd3a05a78193 | note | Frequency - once
0bfe1bfe-2ea6-573a-8fed-fbb3ff08802b | note | Inspection Type (Visual, other) - Visual + Photographs + document
71f8f5e3-65fd-52aa-ba41-6f385fa71ef0 | note | Inspection: Key - I
c863ffa6-de98-5975-b897-fbb46554845d | note | Inspection: By - IP
2989f60f-5128-4c88-9e85-17b316ff450c | checkpoint | 4.2 - Solenoid function test
de403c25-3300-5025-a8ef-2e54f309d596 | note | Inspection Point: Quality Control Activity - Test function of solenoid shut-off
ec77013f-12e9-504f-91dc-77d987417e42 | note | Acceptance Criteria - Shut off when reservoir is full
eee3a08a-ab64-57dd-a8ef-de93d826ce5e | note | Verifying Document - Reservoir levels
6beae2bc-bfe9-5df7-9664-9ccc1b7ddc06 | note | Frequency - once
fc6834d3-e356-56c6-b587-a0c89596da8e | note | Inspection Type (Visual, other) - Visual + Photographs + document
432767fa-e3a2-547f-bb75-5fc18c81ca71 | note | Inspection: Key - I
b8bb73cb-76c4-5000-9022-2c7f45eac31b | note | Inspection: By - IP
5dfd1ceb-7047-434c-8f47-e8c382609652 | checkpoint-no-value | Note:
291e4a71-00f3-527d-ac28-cce125979a35 | note | Valve chamber will need to be assessed by Downer HS&E to determine as to whether is a confined space
5f01cbde-9a80-465f-9e0b-f6c3a4e26956 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
ec1181d9-b18c-4cab-b637-9456e2e9d5e1 | checkpoint | 5.1 - Record Value
75a74f4c-8446-50dd-b397-0792b73b58ce | note | Inspection Point: Quality Control Activity - At completion of valve commissioning
a70f2b4e-448b-533e-a316-0cde7f67ee69 | note | Acceptance Criteria - When consistent results are achieved
ef06fffb-3379-5da6-85f0-9a4d875f8c77 | note | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
50d26153-2714-5e8f-a09a-29e4c9db7286 | note | Frequency - once
5d09ee59-4441-559f-a554-0b5ad2f31a08 | note | Inspection Type (Visual, other) - Visual + Document + Photograph
9278492e-c2c3-576e-92ff-c61f9a96265d | note | Inspection: Key - I
5cac2dd8-9e08-5df7-b380-0c8ab46216cd | note | Inspection: By - IP
599915d1-afdd-4554-969e-c41081b05e74 | checkpoint | 5.2 - Record solenoid valve feedback values
8536fee6-ea4d-5c8c-b919-7fc58a4deffc | note | Inspection Point: Quality Control Activity - At completion of valve commissioning
d2ba2556-bf70-5a1d-a69c-72ab0716f109 | note | Acceptance Criteria - When consistent results are achieved
36e01064-2655-548f-9727-96d3807aab2e | note | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
4c497f03-ba32-5ae5-b871-3daa0e0343b9 | note | Frequency - once
87eb89b6-eae1-5bc7-beb5-203f005c45ac | note | Inspection Type (Visual, other) - Visual + Document + Photograph
0644c236-8a88-59ee-9fa9-7e2bb214294a | note | Inspection: Key - I
0a120261-c343-5ab3-8743-d2681eaa6eda | note | Inspection: By - IP