## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
1cc5e213-9d9d-4db5-b1af-fce8baff9c03 | checklist | ITP 561462-DOW-ITP-CV-01 Butt Welding | itp | ITP 561462-DOW-ITP-CV-01 Butt Welding
b2eb2eb6-2cda-48a4-a7a0-4cb6b51ae291 | section | SECTION 3 – RECEIVING INSPECTIONS
4447e8c7-6d30-46a3-a65c-068cc757bf0f | checkpoint | 3.1 - Material delivery
895f0d44-a5df-55c2-8b5b-aae467e40208 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
7c41fc2b-3e6b-548d-a6a3-d7e756e4a971 | note | Acceptance Criteria - Pipes shall be DN250 HDPE PE100 PN20
458da35d-2e8d-5f4b-8046-54e92b039977 | note | ○ Material and fittings are approved as per contract specification
fd6c13d1-95b6-5a64-9e6d-7a63c3d8ba54 | note | Verifying Document - Photo of pipe bundle(s) showing pipe classification.
3eb672b5-77c5-5347-ac29-fbe6b371deb9 | note | ○ Delivery docket/packing slip
b3cbf9ca-a37c-5216-a07a-5c1e8bd275ba | note | Frequency - On delivery
f5a86b99-8b8d-516e-a8d5-9cbcb2c44070 | note | Inspection Type (Visual, other) - Visual
b50177e4-1871-5659-be92-cc3a0a1ea1a6 | note | Inspection: Key - V
534d6252-66dd-54d1-8ed1-71b21486060e | note | Inspection: By (Role Key) - CR, IP
901a9562-cfd2-400e-af8b-a7986664ebae | checkpoint | 3.2 - Certification of welding equipment
ddc2a526-42bc-54ac-b41d-ad07da7f04de | note | Inspection Point: Quality Control Activity - Confirming just one butt welding machine in use during life of project.
561450b2-7bd6-5945-abec-d432e9bfc787 | note | Acceptance Criteria - Accepted by Client as suitable for use
da6607d6-e9f9-5031-9f74-4096b936d440 | note | Verifying Document - Current calibration certificate/service record
47ad00e5-8938-5ea7-883f-7788002def65 | note | Frequency - Prior to commencement of works
03106ce1-8131-5f16-ac71-f26d92247bc4 | note | Inspection Type (Visual, other) - Hold point
af8fcf48-c1be-58a8-a935-bef05f56db1e | note | Inspection: Key - H
dc72304d-cb06-5509-b7da-9eb18b9bf186 | note | Inspection: By (Role Key) - IP
e66d8d15-9d9a-480c-97f7-2b8b2dedbea1 | signoff | AUTHORITY HOLDPOINT
16252598-517c-46a2-a013-7d74c0ebdc78 | section | SECTION 4 – IN-PROCESS INSPECTIONS
7dbb91ce-d674-4f41-8391-9bd744768443 | checkpoint | 4.1 - PE Welding – Operator and Equipment
70b0ca68-210a-59c6-a719-52c8529d76c0 | note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
3c3ee0c8-7ea0-5955-be3d-f25dba9b85c3 | note | Acceptance Criteria - Testing of weld samples carried out by an IANZ accredited laboratory.
79ff9312-8308-5bac-a80b-9527afdb6760 | note | Verifying Document - Current welding certificates of operatives
006bcd82-689e-59e2-8840-612de8e14291 | note | ○ Current calibration record of welding Equipment
944d3784-d64c-522d-97fa-c7dca3a29f8e | note | ○ Tensile test results
f8ba91bb-6d1c-595f-82a3-4753491b8573 | note | Frequency - During Installation
05dc3a37-0491-5c56-9503-b09125e7bed8 | note | Inspection Type (Visual, other) - Inspection, Examine
992c1182-62d7-54d0-8246-b86f4f82a8ce | note | Inspection: Key - I, E
d0f33652-8da5-5a98-9e28-2b94ed6a296e | note | Inspection: By (Role Key) - CR, IR
20fa60f8-ec14-4d7b-9cf3-02fd4ea59b16 | checkpoint | 4.2 - Test Sampling
5db0e199-5f15-5d28-aa33-0da3675481b1 | note | Inspection Point: Quality Control Activity - One pre-qualification per operator, one pilot weld per machine/per DN.
28c95ad0-f961-5e7c-832e-f2e537ceff3a | note | ○ Test failures will require the previous weld and the following weld to be tested and passed.
5ba5847b-7b65-5807-96bb-b2b92540aec7 | note | Acceptance Criteria - Pass/Fail
77ec186c-4346-564b-a3ac-29ec6615b338 | note | ○ ISO 21307
99dfda73-4e39-51e3-9599-f85bb3ea2eb5 | note | ○ ISO 13953 (Testing)
989880ef-722c-5c86-83b5-e8ce83b32949 | note | Verifying Document - Tensile test results from Kiwi Mechanical Ltd
9126fdcf-9dfb-5132-838d-828459f17003 | note | Frequency - Every 50 welds per operator (or as requested by Client).
96d0024e-f79d-5309-8e0c-e9f58edece9b | note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
6a82ad44-0d34-5e0d-b475-4998313d9cc0 | note | Inspection Type (Visual, other) - Operation
fca58a69-9e2d-5996-8837-117d4f3b549e | note | Inspection: Key - O, R
a3c034df-52a2-5779-bd30-e38699ddc97e | note | Inspection: By (Role Key) - WS/CR, IR
a947f084-4f4e-4dda-aadc-c9dffd9937ac | checkpoint | 4.3 - Weld Completion
dd647356-2a40-50b3-9869-e30a2e48b3cf | note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification
fb1fa064-0bf3-5cd3-b3ee-69ee56139b2c | note | Acceptance Criteria - Pass/Fail
5562b004-49a1-5161-aea7-a25279a8ee77 | note | ○ ISO 21307
5f9a5efc-3660-5087-8e01-7715d85ae268 | note | Verifying Document - Power App or manual records
6da880df-e6bb-567b-b0f3-f7e163e001ed | note | ○ Data log from welding equipment
f5e55a4e-21f7-5f4f-8fd2-78ae2ac07394 | note | ○ Photo Log
3f3e34d5-bb0e-56df-8d51-232648a77bd5 | note | Frequency - Each weld
d6c42bd7-4554-5a20-adb8-60d2a347027c | note | Inspection Type (Visual, other) - Check, Dimension Inspection
611118df-4572-5c02-9bf3-f4b2d9b37e49 | note | Inspection: Key - C, D, R
eb5fd551-bdbd-50e8-91d4-79c6ce638983 | note | Inspection: By (Role Key) - WS, CR, IR
7513cd5f-ccf3-452d-8c18-d76b429774eb | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
9c317617-df48-43fb-b503-2355d78aca8a | checkpoint | 5.1 - Completion of QA
454d263a-180b-5e69-bb2c-3b1306ee645d | note | Inspection Point: Quality Control Activity - Ensure QA package complete.
98e654be-24ff-521b-b895-aa194acc890e | note | Acceptance Criteria - All necessary documents including HDPE welding compiled and handed over to ER in completeness.
5eff8a71-945c-5bfe-9da6-15877cd54177 | note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
b0cb7998-142c-5bfa-86c7-3e979c0dff20 | note | ○ EF controller printout for all EF joints
36f04f68-a3e3-547e-8b57-01c37e4c4c74 | note | Frequency - Before practical completion
30963472-d7c3-57e6-8ec8-53ff847115da | note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
0b195199-3d0b-592e-80a7-94b69a05c2c4 | note | Inspection: Key - I, M
36af588d-f7c8-537f-812d-de395ebdf7c9 | note | Inspection: By (Role Key) - CR, IP
86d06ff0-83e3-4318-a8c3-fa6760f54778 | checklist | ITP 561462-DOW-ITP-CV-02 Watermain | itp | ITP 561462-DOW-ITP-CV-02 Watermain
21ce7cc5-4cc1-444f-abfb-3510d396c32c | section | SECTION 3 – RECEIVING INSPECTIONS
db984fe3-cfe1-4747-9733-3d1d936d2b8d | checkpoint | 3.1 - Material Delivery
b4a4538f-1479-5a56-a309-b2e5097b4200 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and specifications
8792f129-04b0-5982-83c6-46b930afc3bb | note | Acceptance Criteria - Pipes shall be DN250 HDPE PE100 PN20
2b8bf0b7-0b4e-58d9-9d38-f59199fe9fb6 | note | ○ Material and fittings are approved as per contract specification
6b247be9-c3a1-543e-b6ed-4e30d6bdf11f | note | Verifying Document - Photos,delivery docket, MDD results for backfill materials
a96d9a25-899b-59e2-92e6-5d8bd0c6414a | note | Frequency - On delivery
c693915f-dc2c-5256-81df-8743cc0f9730 | note | Inspection Type (Visual, other) - Visual
5793bee3-1de7-518f-ad5c-4265b5f1ad2f | note | Inspection: Key - C
297ea1e4-6f78-5452-840d-f819e53c73ae | note | Inspection: By (Role Key) - CR/IP
7c6d772b-fa6c-4197-aa39-36e0370e7418 | checkpoint | 3.2 - Set out
60c1b2a4-1bcb-5853-8105-0f617c422e8d | note | Inspection Point: Quality Control Activity - Allignment set out as per design or as agreed with Engineer
61fc13b8-1f63-5f53-bea8-899ce3b7d9a4 | note | Acceptance Criteria - Set out matches drawings or as agreed with the Engineer
2b20d452-839d-57bb-94e7-e6a4d85413d1 | note | Verifying Document - Photos
dfb1ea3b-d7c3-5038-847e-2a4170658296 | note | Frequency - Prior to commencement of works
edd2335a-ee0c-56f2-8372-b87c291c83cc | note | Inspection Type (Visual, other) - Visual
359cd4ce-405f-59fa-bd65-3d512fcd21f8 | note | Inspection: Key - C
1adb61b2-7a1e-5751-a350-1fed92dc6990 | note | Inspection: By (Role Key) - CR/IP
1ae5985e-5957-4e02-b90c-ddea4603310a | section | SECTION 4 – IN-PROCESS INSPECTIONS
dc4aa073-50f6-4aed-b258-92353cfa5bd7 | checkpoint | 4.1 - Trench Excavation
a2f4f952-117a-54c2-9ee8-526b55e84e83 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawings C501-C502.
5ec3c651-b51c-51fd-9cda-37cc0f8c954f | note | ○ Floor of trench to be even across width and length.
7b052dfb-9585-5f6e-9ee2-cfaedb0eb5a5 | note | Acceptance Criteria - Allow 100mm for bedding
208c0a57-f263-584d-a145-b5c0597f49ad | note | ○ Allow for minimum cover of 750mm.
5ea95ef2-5fb3-5c9c-b5d5-c170759ee76e | note | ○ as shown on drawings C505
e33d1833-b32e-5105-bea9-bf58c3100b6f | note | Verifying Document - Photos
681f6f09-02f8-5a5e-ae20-b371c080540f | note | Frequency - During Installation
9dcb8d32-547f-5407-8339-ddcd9da40c0d | note | Inspection Type (Visual, other) - Visual
c3253d8d-cc40-553c-8b33-817c96030596 | note | Inspection: Key - V
a7787b5b-dc8e-503f-a267-85c81d11f621 | note | Inspection: By (Role Key) - SP/CR
79e03fc3-7210-4718-93f5-2bdf2d748d03 | checkpoint | 4.2 - Foundation
6cd7b3fd-8ce9-53a4-bd2b-0f81dda8ba33 | note | Inspection Point: Quality Control Activity - Material trench floor is inspected to ensure suitable
5c1422a1-7dfa-56e1-9fab-1a5da52fd49d | note | Acceptance Criteria - Able to support loads
2889d223-299a-5d31-9ede-a1a47de414ea | note | ○ Free of very soft material or irregular or fragmented rock
ba50cbd1-9350-5a6a-92d4-ecc765c8cf40 | note | Verifying Document - Photos
8de98912-5dfb-55b0-aa2d-b2110b76c206 | note | Frequency - During installation
581c0e72-5f6a-52ed-9a08-56a104273ee7 | note | Inspection Type (Visual, other) - Visual
4cc9ab58-96e6-5daf-8556-02a0f1bf8d1b | note | Inspection: Key - V
e3601d23-6ff7-5bd6-8913-a5388f0a3f8a | note | Inspection: By (Role Key) - SP/CR
2d3fc26c-0ee1-454c-ae15-7a8d40b8b6b1 | checkpoint | 4.3 - Pipe Installation
a3fd1bb5-0b18-53f7-8c12-4242558f7496 | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
f4a023af-ccf2-53ff-83cb-54d55b952537 | note | Acceptance Criteria - Pipe not damaged during installation
8e638562-cd86-5a3b-be24-0307489a992a | note | ○ Pipe is centrally located within trench
e73b0fad-b8bf-5e7a-b7f4-1772229b311c | note | ○ Pipe levels are within tolerance and according to the drawings
d5171e5b-976b-54ad-ba43-18655abea28e | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
e0f7eaa6-3014-5f2b-966d-0bf358f31031 | note | Frequency - During installation
e2bae9d8-bb93-5ed3-83f4-763b7bc2f35e | note | Inspection Type (Visual, other) - Visual
99d91fc2-4f31-56f1-9757-19f5ef2c4d2f | note | Inspection: Key - V
af27ac75-f95b-5f61-b8a2-d2a4c6c3aa9f | note | Inspection: By (Role Key) - SP/CR
e218c4ee-20df-441c-8260-b00ea4cb68e4 | checkpoint | 4.4 - Embedment zone
8b30e71a-cb69-5aaf-a1af-c626fd205963 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
07d0267d-2ab3-5117-8bdc-dd85406b762d | note | Acceptance Criteria - min 100mm bedding
b6282fee-7d53-5665-aba1-02f3d7aa4baa | note | ○ 150mm overlay
9aad9c11-b498-54cf-9c7a-2ac55fb10507 | note | Verifying Document - Photos
92e86f03-df2c-5a1c-a8c6-1bb22536d76e | note | Frequency - During Installation
a6d8abd2-7ed4-56ba-ae16-025cde52d5c1 | note | Inspection Type (Visual, other) - Visual
7e420b6e-786e-570c-a46c-a6e8ec3417ac | note | Inspection: Key - V
705f4932-55a0-5e54-b4e4-ed85610fca53 | note | Inspection: By (Role Key) - SP/CR
19626b44-e8af-4081-902d-c827a42c5548 | checkpoint | 4.5 - Backfill and Compact
17d75cf7-9d1e-5757-80fd-6f94d199d5d8 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
8bb4341b-66fa-5272-99ed-9b08ef70e733 | note | ○ Compaction testing one test every two layers as required
a993e94d-a26a-5b41-bf9a-2972adc783e8 | note | ○ Conductive signal strip to be laid at 300mm above pipe
d8c07221-044d-5eb6-b701-a0619ab4737d | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
286747d0-0372-5d74-b115-9f6fd49ab79d | note | Verifying Document - Photos, compaction test results
37d86a0b-6c2e-590f-afd5-3055915776d3 | note | Frequency - During Installation, compaction testing per 50m of pipeline
ad9f1e90-c583-51ae-97b5-abd30fc05117 | note | Inspection Type (Visual, other) - Visual, On site test
0a0a23e5-f239-507b-b46f-dc3a8f027776 | note | Inspection: Key - H
d1fb5f57-85b6-5d2b-8381-ab87e8a30010 | note | Inspection: By (Role Key) - SP/CR/IR
12d55e2f-9a95-440e-99a8-aa7b0f5face4 | signoff | AUTHORITY HOLDPOINT
ea93abc3-9307-4143-a8f5-a11a36a6e995 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
fa9ebf08-1ebd-48da-88b8-64502d82ccfb | checkpoint | 5.1 - Pressure Testing (PE pipeline)
2162240a-04b7-5b72-b94d-c9013a4bad61 | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
0f0a901c-51c5-58a5-90d0-e98abaca1937 | note | Acceptance Criteria - Specification Attachment C, clause 4.7.5
fa0d249e-55ad-59ad-b1aa-770fe9e1261e | note | ○ No Thrust block failures,
f0764170-181b-580d-abb3-94e4a70667b3 | note | ○ No visible leaks,
59575665-f211-5124-8b29-45854b44710e | note | ○ Do not exceed make-up water limit
b138172f-1995-584f-904e-1ce16d81d720 | note | Verifying Document - Test Records
c92933b7-f564-5eb1-bc26-a06c158b372f | note | Frequency - Before commissioning
af919c80-d709-571b-8a97-9466feb0d073 | note | Inspection Type (Visual, other) - On-Site Test
c2601147-60c9-5d13-8faf-39c71e544f08 | note | Inspection: Key - H
55a1133d-992f-54c8-938c-1a50de540332 | note | Inspection: By (Role Key) - CR/IP/DR
6010d167-17ca-4165-b07f-8976d7ea2b99 | signoff | AUTHORITY HOLDPOINT
fb0ddb36-e896-4093-8781-5885f0d9384e | checkpoint | 5.2 - Disinfection
f5286d86-1677-5b42-8559-fe531d178bbc | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
11f89b41-76b4-5e9e-8aea-4f601d2a532d | note | Acceptance Criteria - Specification Attachment C, clause 4.12
25762d04-d059-529e-881c-b7b735ea0dc2 | note | Verifying Document - Test Records
73c92cdc-e7da-51f4-ba74-80998f5aeb6f | note | Frequency - Before commissioning
26d1a395-42cc-5864-92d0-6f4eb5a608f7 | note | Inspection Type (Visual, other) - On-Site Test
f20884fc-b602-5294-a2f3-6d59ca1ffcba | note | Inspection: Key - H
9e8914ba-f47a-52ea-b0f2-92aa6f5a6966 | note | Inspection: By (Role Key) - CR/IP/DR
0f1e5a85-e8a5-440d-ae07-0449260f5e2b | signoff | AUTHORITY HOLDPOINT
a6dfdd57-87d2-4f03-950f-9ddd3efcb9ec | checklist | ITP 561462-DOW-ITP-CV-03 EF Welding | itp | ITP 561462-DOW-ITP-CV-03 EF Welding
fb3e9d4b-f310-4812-98ac-3eaa60d4c7ab | section | SECTION 3 – RECEIVING INSPECTIONS
643802b1-1718-4168-a964-12a44b023865 | checkpoint | 3.1 - Material delivery
606b51ed-74c2-5b80-bf39-2ce98632e537 | note | Inspection Point: Quality Control Activity - each pipe welding location check pipes to be welded
420fc781-4dfc-570a-be8e-40ef3668da22 | note | ○ each EF fitting
f05de4bc-4764-5acc-8588-647b4372441b | note | ○ check bags undamaged and sealed
c83c4c99-0c5b-590d-885c-67065435444d | note | Acceptance Criteria - Pipes shall be DN250 HDPE PE100 PN20
63734ffc-8a47-5163-8ff9-d18f6ebeee7c | note | ○ EF fittings correct size, SDR, PE100 and pressure rating.
e41a2990-e26e-5d39-868b-cd48e507e6b9 | note | Verifying Document - Photo of markings and labels on pipe.
02862db4-a3f1-54f2-a0e5-cb2c1c58fb6b | note | ○ Delivery docket/ packing slip
d82ab758-9c5b-502c-aa77-5704f6318a51 | note | ○ Scan bar code on fitting
1615272d-5258-58f0-83e9-64eff480a2a9 | note | Frequency - On delivery
027c168d-bef2-58e9-89a9-eef33834a467 | note | Inspection Type (Visual, other) - Visual
77260fff-dedd-5cb5-b9e3-247add229299 | note | Inspection: Key - V
fa9608d7-b365-519b-802e-4a5c31b8e301 | note | Inspection: By (Role Key) - CR, IP
525b4a9e-d300-43f6-8592-b1d3620991fa | checkpoint | 3.2 - Certification of welding equipment
206b0a11-4f70-5e0e-9e02-7e86076c89d3 | note | Inspection Point: Quality Control Activity - Confirming just one EF welding machine in use during life of project.
ee5fb4ab-9b88-5e21-adbd-91f10aa032d8 | note | Acceptance Criteria - Accepted by Client as suitable for use
da099b34-c89b-5cf3-bb62-23907311d72e | note | Verifying Document - Current calibration certificate/service record
b5d22fdb-154a-5cb1-a69c-f98fe60b4b78 | note | Frequency - Prior to commencement of works
6cb59442-faa1-5aab-bd68-bb83f0b55a5d | note | Inspection Type (Visual, other) - Hold point
dd9e09e4-d41f-5b5b-9953-b6bceef53ba2 | note | Inspection: Key - H
f37d3a12-0492-539b-b3b9-4d8aed817a81 | note | Inspection: By (Role Key) - IP
be9e23fd-f91e-4efe-8691-daea78d87239 | section | SECTION 4 – IN-PROCESS INSPECTIONS
ccb0b120-64ef-4c48-9059-3793b1aff9b6 | checkpoint | 4.1 - PE Welding – Operator and Equipment
f143198a-2ffb-5661-9883-f0d696a4b77c | note | Inspection Point: Quality Control Activity - Competency certificate of welder and certificate of fitness for welding equipment
696af1c4-afec-5c2f-9067-ff1c42134eef | note | ○ Generator capacity adequate for the EF fittings.
15a9166d-ec99-534b-988f-f262dacaae15 | note | Acceptance Criteria - Have peel decohesion test of weld samples carried out by an IANZ accredited laboratory.
76599832-4acb-59b3-a5b9-d425049ed259 | note | Verifying Document - Current welding certificates of operatives
ef6695b7-e9ce-5f3d-bf96-b818d8cf3548 | note | ○ Current calibration record of welding Equipment
e5c92d03-f618-5ebc-9111-2c1ed8dfa872 | note | ○ Peel decohesion test results
b4b6486b-9b38-5afd-be31-7909a575b342 | note | Frequency - During Installation
4fd4e378-f094-5f67-91e7-20b1ff629e80 | note | Inspection Type (Visual, other) - Inspection, Examine
562606c9-8f2a-5f97-85b9-98b1ecf65f5a | note | Inspection: Key - I, E
46e5c2fd-c12c-5a62-8d47-63a453b7598b | note | Inspection: By (Role Key) - CR, IP
c2886351-0112-4d1b-9b1f-1073bc04181e | checkpoint | 4.2 - Test Sampling
fb96ea3a-9ce0-516e-ab62-58d86ed233f5 | note | Inspection Point: Quality Control Activity - one pre-qualification per operator, one pilot weld per machine/per DN.
4c28603b-19ca-5faa-b1ef-7dd8f43e868c | note | Acceptance Criteria - Pass/Fail
176891a6-431b-54fb-b003-e848facc9eea | note | ○ ISO 13953 (Testing)
1566a6b0-2b1e-5eaf-8edd-41dacdabadf0 | note | Verifying Document - Peel decohesion test results from Kiwi Mechanical Ltd
edb271b6-320b-5c02-b438-23e812138713 | note | Frequency - Every 20 welds per operator (or as requested by Client).
a323e5f0-b95f-5cf4-9d2b-d7ea0b087a3a | note | ○ Test frequency to be reduced in response to consistent pass results, with Engineers approval.
4a2df689-ce35-5ad3-b1de-6f3cb219de34 | note | Inspection Type (Visual, other) - Operation, Review
5eede8e6-6c87-597e-bcb8-ca6cf58f6c50 | note | Inspection: Key - O, R
d831355e-bda9-5f73-ad15-f41cd8dd16e1 | note | Inspection: By (Role Key) - WS/CR, IP
2a844d83-e28d-4b5e-9dda-e353561c51f5 | checkpoint | 4.3 - Weld Completion
ee48fd27-edb7-5e97-a49c-bda6a7da2243 | note | Inspection Point: Quality Control Activity - Weld completed to required standard and specification.
b04fb1df-4adc-535a-b4b4-28ee032123f5 | note | ○ Only move strings after EF’s have cooled!
912b3f55-79c3-5742-972a-4978a977427a | note | Acceptance Criteria - Pass/Fail
298beacf-c150-5bb1-a2d3-6369d27247f4 | note | ○ PIPA POP001 version 8.1 2021 and POP014
31c3b62e-2a2c-5ef3-81e6-df7decb1c917 | note | ○ EF controller printout for all EF joints
cf08f9bb-d61f-5749-bfbe-71f7e0a8ea30 | note | Verifying Document - Power App or manual records
33bece26-4099-59df-8a22-a552c3b71e00 | note | ○ Data log from welding equipment
f17b9125-79a6-5a95-b115-22b3afc4a309 | note | ○ Photo Log
6e3290a6-c747-5252-822a-8500844cb5f0 | note | Frequency - Each weld
ae66e2c0-9e1f-53ad-88c8-e306aa365e01 | note | Inspection Type (Visual, other) - Check, Dimension Inspection
ac9a07b2-c843-5f88-9551-63a3dae06f96 | note | Inspection: Key - C, D, R
1ba28bed-c9c6-5164-b5de-93245937d7fe | note | Inspection: By (Role Key) - WS/CR, IP
171f9cb1-3af9-4187-adca-323b393ca90d | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
29b5874f-007e-4c8f-a3b2-95189e45636d | checkpoint | 5.1 - Completion of QA
b5f56d21-c4a4-5388-a888-2572167959a7 | note | Inspection Point: Quality Control Activity - Ensure QA package complete.
353e07ce-2c9b-5077-836e-a0450bba90f0 | note | Acceptance Criteria - all necessary documents including HDPE welding compiled and handed over to ER in completeness.
a19c6c48-19e6-55d7-86d6-1173ec0b44d1 | note | Verifying Document - Excel spreadsheet exported from Power App, includes weld photos and weld date from weld equipment.
61a496a2-39ce-5501-9846-b584ad75f65d | note | Frequency - Before practical completion
9f776f98-65a6-5d4b-a447-594e3c079bc4 | note | Inspection Type (Visual, other) - Inspection, Monitor on Random Basis
8aa4f9e1-80dc-5ff7-8f01-87a78bfa8a51 | note | Inspection: Key - I, M
47ba6668-3482-5b40-8799-1dab452b529b | note | Inspection: By (Role Key) - CR, IP