## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - MT GRAND to WINGATUI | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561483 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | CM | Construction Manager | Stephen Vorgers
Contract Number: | DCC11014-WPS004 | [5 empty] | C | Check | CR | Cust. Representative | Joff Riley / Mark Todd
Area/ Sub-System: | Air Valves Installation - MT GRAND to WINGATUI |  |  | Lot ID Number: | N/A |  | D | Dimension Inspection | IP | Inspection Personnel | Jason Bell
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | 561483-ITP-001.2 |  |  | Version: | DRAFT |  | H | Hold Point | OP | Operations Manager
ITP Description: | Air Valves - Delivery & Installation | [5 empty] | I | Inspection | PM | Project Manager | Matt Paterson
Discipline: | Air Valves | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Mt Grand to Wingatui Project Ref: 12581908-GHD-PS-MG-DRG-GN Drawings: G0001, M0001, M0002, M0011, S0001 & S0002 | [5 empty] | S | Subcontractor | SP | Supervisor | Bruce Allan
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Matt Paterson |  |  | Date: | 15-10-24 |  | W | Witness Point | SV | Surveyor
Quality Specified: | None - As per Specification | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Matt Paterson/Aaron Sutherland |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson/Stephen Vorgers |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Joff Riley / Mark Todd |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Take delivery of air valve 2 | Check that Make/Model/Dimensions are correct | Matches Design Drawings/Documents | Drawings & Specifications | Once | Visual + electronic | H | IP/PM
3.2 | Inspection of Air valve for any sign of transit damage | Visual check for paint coating damage and or any mechanical damage | No chips to protective coating od any mechanical damage | This ITP | Once | Visual + Inspection | I | IP
3.3 | Fitment - Spatial constraints | Verify air valves will physically fit into existing locations | Measure & Check | This ITP. Notify Engineer of any locations where this is not achievable | Once | Visual + Inspection + Photograph + Written (if applicable) | I | CR
Note: It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve. Downer to notify Engineer once confirmed.

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Remove redundant Air Valve & Isolating Valve - Valves 2 | Inspect condition of BSP50mm thread to accept new valve & air vent | Thread is in good condition | Visual Assessment | once | Visual + Photographs + docket | I | IP
4.2 | Isolating Valve Installation - Valve 2 | Install new Stainless Steel 50mm BSP Nipple & Ball Valve 2 | Ensure valve is installed so that it can be isolated with out interference | As per drawings/Specifications & Best Practice | once | Visual + Photographs | I | IP
4.3 | Stainless Steel 50mm BSP Nipple & Air Valve 2 | Install new Stainless Steel 50mm BSP Nipple & Air Valve 2 | Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed | Visual Assessment | once | Visual + Photographs | I | IP
4.4 | Isolating valve 2 - Off position | Pressure test | Ensure all isolating valves are in the off position | This ITP | once | Visual + Photographs | I | IP/CR
4.5 | Security | Reinstate valve cover for safety & Security | Valve covers are replaced and securely in position | This ITP | once | Visual + Photograph | I | IP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Red pen Mark up | Record Serial Numbers (if applicable) in comments section below | At completion of all items on this ITP identifying Air vent 2 make & Model at each location | Red line mark up drawing / This ITP | once | Visual + Document + Photograph | I | IP
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: