## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - MT GRAND to WINGATUI | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561483 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | CM | Construction Manager | Stephen Vorgers
Contract Number: | DCC11014-WPS004 | [5 empty] | C | Check | CR | Cust. Representative | Joff Riley / Mark Todd
Area/ Sub-System: | Pump Installation - Mt Grand to Wingatui |  |  | Lot ID Number: | N/A |  | D | Dimension Inspection | IP | Inspection Personnel | Aaron Sutherland
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | 561483-ITP-007.4 |  |  | Version: | DRAFT |  | H | Hold Point | OP | Operations Manager
ITP Description: | Installation of Pump 3 isolating valves - Inspection Test Plan | [5 empty] | I | Inspection | PM | Project Manager | Matt Paterson
Discipline: | Pumps | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Mt Grand to Wingatui Project Ref: 12581908-GHD-PS-MG-DRG-GN Drawings: G0001, M0001, M0011,S0001 & S0002 and various other as-built drawings | [5 empty] | S | Subcontractor | SP | Supervisor | Bruce Allan
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Matt Paterson |  |  | Date: | 19-12-24 |  | W | Witness Point | SV | Surveyor
Quality Specified: | None - As per Specification requirements | [7 empty] | WS | Welding Supervisor | Matt York
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Bruce Allan |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson/Stephen Vorgers |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Mark Todd / Iain Partington |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 3 | Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP
3.2 | Delivery of Dress Sets to site from Downer storage facility - Pump 3 | Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct | Must be on the Approved Products list | Specification - Approved Materials list | Once | Visual | C | IP
3.3 | Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6 | Application via NTE and discuss methodology | Upon approval from Client & Engineering team | Written approval | Once | other | R | CR

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Shutdown the pumping system (all pumps) | Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained | Ensure reservoir tanks are full before proceeding | Advice from DCC Operations | Once | Visual + Written + Verbal | C | CR
4.2 | Removal of suction side isolation valve to pump 3 (wafer type). Inspect pump flange and valve flange | Ensure no residual gasket material remains on flange surfaces. Clean if necessary | Surfaces are clean | Visual | Once | Visual + Document | A | QE
4.3 | Removal of discharge side isolation valve to pump 3 (wafer type). Inspect pump flange and valve flange | Ensure no residual gasket material remains on flange surfaces. Clean if necessary | Surfaces are clean | Visual | Once | Visual + Document | A | QE
4.4 | Suction side valve installation | Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation | All valve bolts are tightened and M16 bolts are torqued to 80N.m | This ITP | Once | Visual + Photograph | I | IP
4.5 | Discharge side valve installation | Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation | All valve bolts are tightened and M16 bolts are torqued to 80N.m | This ITP | Once | Visual + Photograph | I | IP
Note: All valves to be left in closed position

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Returning existing pump 3 for duty | Purge pump 3 of any entrained air | All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present | Visual | once | Visual + Document | I | IP
5.2 | Power reinstatement to pump 3 | Remove lock out tag pump 3 | Completion of 5.1 above | This ITP | once | Visual + Document | I | IP
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: