## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - MT GRAND to WINGATUI | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561483 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | CM | Construction Manager | Stephen Vorgers
Contract Number: | DCC11014-WPS004 | [5 empty] | C | Check | CR | Cust. Representative | Joff Riley / Mark Todd
Area/ Sub-System: | VFD Installation - Mt Grand to Wingatui |  |  | Lot ID Number: | N/A |  | D | Dimension Inspection | IP | Inspection Personnel | Aaron Sutherland
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | 561483-ITP-009.6 |  |  | Version: | DRAFT |  | H | Hold Point | OP | Operations Manager
ITP Description: | Installation of VFD 6 (Pump 6) - Inspection Test Plan | [5 empty] | I | Inspection | PM | Project Manager | Matt Paterson
Discipline: | Electrical | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Mt Grand to Wingatui Project Ref: 12581908-GHD-PS-MG-DRG-GN Drawings: G0001, M0001, M0011,S0001 & S0002 and various other as-built drawings | [5 empty] | S | Subcontractor | SP | Supervisor | Bruce Allan
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Matt Paterson |  |  | Date: | 2024-12-19 |  | W | Witness Point | SV | Surveyor
Quality Specified: | None - As per Specification requirements | [7 empty] | WS | Welding Supervisor | Matt York
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Bruce Allan |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson/Stephen Vorgers |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Mark Todd / Iain Partington |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Delivery of VFDs to site from Downer storage facility - VFD 6 | Check and verify that correct VFD is delivered | VFD is damage free | 1. VFD delivery docket. 2. VFD storage ITP | Once | Visual | C | IP
3.2 | Delivery of Ancillaries to site from Downer storage facility - VFD 6 | Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct | Approved Products list and approved for use | Specification - Approved Materials list | Once | Visual | C | IP
3.3 | Arrange with client and Engineering team to shut down the system | Application via NTE and discuss methodology | Upon approval from Client & Engineering team | Written approval | Once | other | R | CR

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | Electrically Isolate Pump 6 at Control Cabinet. Ensure no issues with Grundfos Controller. | Isolation is applied to Pump 6 and existing VFD | VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes) | This ITP | Once | Visual | I | IP
4.2 | Electrically disconnect Pump 6 | All electrical connections are removed | Remaining 5 pumps are functioning correctly, Pump 6 disconnected, no voltage on cabling. | This ITP | Once | Visual | I | IP
4.3 | Remove Pump 6 Cable from Motor to VFD | Cables Disconnected from Drive and Pump 6, Cable Removed From Support System | All mechanical & Electrical disconnections are completed (Pump 6). | This ITP | Once | Visual | I | IP
4.6 | Remove Pump 6 VFD | VFD Removed from Wall and redundant fasteners removed | Wall is clear of obstructions in preparation for new VFD install | This ITP | Once | Visual | I | IP
4.7 | Mount new Pump 6 VFD | new VFD mounted to wall on Unistrut | VFD mounted securely, Spacings compliant with manufacturers requirements. | This ITP | Once | Visual | I | IP
4.8 | Remove VFD 6 Feed Cabling and Isolators | Cabling Removed From Cabinet and cable trays. | Cables Removed, isolators disconnected and removed from wall. | This ITP | Once | Visual | I | IP
4.9 | Install new supply cabling and isolators for VFD 6 | Cables installed and run into cabinet, isolators and VFD 6 is prepped and tested | Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests. | Cable Test Sheets | Once per pump | Visual | I | IP
4.10 | Terminate Cabling for VFD 6 | Cables fitted off into VFD 6 isolators and supply cabinet. | Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 6 | Cable Test Sheets | Once per pump | Visual | I | IP
4.11 | Remove isolations | Drives motors and isolators fit off, all covers replaced. | isolations removed circuits re-energised | Lock-out Tag out Register | Once per pump | Visual | I | IP
4.12 | Configure VFD 6 | VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps | VFD configured correctly, controller setup adjusted | VFD test sheets | Once per VFD | Visual | I | IP
4.13 | Confirm correct operation of VFD 6 and pump | VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps | VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller | VFD test sheets | Once per VFD | Visual | I | IP
Note: Electrical connection of pumps and commissioning are covered in separate ITP's

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Stage 6 Changeover Complete (Mechanical) | Pump 6 in service | Pump 6 is installed. Valves installed to Pump 6 are installed | Grundfos commissioning report | once per pump | Visual + Document | I | IP
5.2 | Stage 6 Changeover Complete (Electrical) | VFD 6 in service | VFD 6 is installed and parameters set by Grundfos | Grundfos commissioning report | once per pump | Visual + Document | I | IP
Note: Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: