## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561483-ITP-001.1 - Air Valves - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.1 - DRAFT - Installation of Stoney Knowe Air Valve1 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 1
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Inspection of Air valves for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating or any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
label | Downer to notify Engineer once confirmed.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valve 1
label | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
label | Acceptance Criteria - Thread is in good condition
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + docket
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Isolating Valve Installation - Valve 1
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 1
label | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
label | Verifying Document - As per drawings/Specifications & Best Practice
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 1
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 1
label | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Isolating valve 1 - Off position
label | Inspection Point: Quality Control Activity - Pressure test
label | Acceptance Criteria - Ensure all isolating valves are in the off position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
checkpoint | 4.5 - Security
label | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & security
label | Acceptance Criteria - Valve covers are replaced and securely in position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 1 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-001.2 - Air Valves - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.2 - DRAFT - Installation of Stoney Knowe Air Valve2 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 2
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating od any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
label | Downer to notify Engineer once confirmed.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 2
label | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
label | Acceptance Criteria - Thread is in good condition
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + docket
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Isolating Valve Installation - Valve 2
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 2
label | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
label | Verifying Document - As per drawings/Specifications & Best Practice
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 2
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 2
label | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Isolating valve 2 - Off position
label | Inspection Point: Quality Control Activity - Pressure test
label | Acceptance Criteria - Ensure all isolating valves are in the off position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
checkpoint | 4.5 - Security
label | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
label | Acceptance Criteria - Valve covers are replaced and securely in position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 2 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-001.3 - Air Valves - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.3 - DRAFT - Installation of Stoney Knowe Air Valve3 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 3
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating od any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
label | Downer to notify Engineer once confirmed.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 3
label | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
label | Acceptance Criteria - Thread is in good condition
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + docket
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Isolating Valve Installation - Valve 3
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 3
label | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
label | Verifying Document - As per drawings/Specifications & Best Practice
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 3
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 3
label | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Isolating valve 3 - Off position
label | Inspection Point: Quality Control Activity - Pressure test
label | Acceptance Criteria - Ensure all isolating valves are in the off position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
checkpoint | 4.5 - Security
label | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
label | Acceptance Criteria - Valve covers are replaced and securely in position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 3 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-001.4 - Air Valves - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.4 - DRAFT - Installation of Stoney Knowe Air Valve4 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 4
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating or any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valve will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
label | Downer to notify Engineer once confirmed.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 4
label | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
label | Acceptance Criteria - Thread is in good condition
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + docket
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Isolating Valve Installation - Valve 4
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 4
label | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
label | Verifying Document - As per drawings/Specifications & Best Practice
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 4
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 4
label | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Isolating valve 4 - Off position
label | Inspection Point: Quality Control Activity - Pressure test
label | Acceptance Criteria - Ensure all isolating valves are in the off position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
checkpoint | 4.5 - Security
label | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
label | Acceptance Criteria - Valve covers are replaced and securely in position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 4 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-001.5 - Air Valves - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.5 - DRAFT - Installation of Stoney Knowe Air Valve5 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 5
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Inspection of Air valve for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating and any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | It was observed during our inspection that potentially there will be a spatial issue (height) with a least 1No air valve.
label | Downer to notify Engineer once confirmed.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Remove redundant Air Valve & Isolating Valve - Valves 5
label | Inspection Point: Quality Control Activity - Inspect condition of BSP50mm thread to accept new valve & air vent
label | Acceptance Criteria - Thread is in good condition
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + docket
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Isolating Valve Installation - Valve 5
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Ball Valve 5
label | Acceptance Criteria - Ensure valve is installed so that it can be isolated with out interference
label | Verifying Document - As per drawings/Specifications & Best Practice
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Stainless Steel 50mm BSP Nipple & Air Valve 5
label | Inspection Point: Quality Control Activity - Install new Stainless Steel 50mm BSP Nipple & Air Valve 5
label | Acceptance Criteria - Ensure that Air Valve is installed free of obstruction and is not sitting proud of road surface and steel cover can be installed
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Isolating valve 5 - Off position
label | Inspection Point: Quality Control Activity - Pressure test
label | Acceptance Criteria - Ensure all isolating valves are in the off position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
checkpoint | 4.5 - Security
label | Inspection Point: Quality Control Activity - Reinstate valve cover for safety & Security
label | Acceptance Criteria - Valve covers are replaced and securely in position
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 5 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-001.6 - Air Valve - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.6 - DRAFT - Installation of Wingatui Chamber Air Valve1 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 1
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Take delivery of valve position inticator 1
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.3 - Inspection of Air valve for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating and any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.4 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | Air Valve 1 & Valve Position Indicator 1 are to be fitted to Control Valve 1 (200mm dia)
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Connection to Wingatui Valve Chamber - Valve 1
label | Inspection Point: Quality Control Activity - Air Valve 1 is installed in vertical position
label | Acceptance Criteria - Air Valve is installed leak free & free of obstruction. Installation as per Manufacturers instructions
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Connection to Wingatui Valve Chamber - Valve 1
label | Inspection Point: Quality Control Activity - Valve Position Indicator 1 is installed in vertical position
label | Acceptance Criteria - Valve position Indicator is installed leak free & free of obstruction. Installation as per Manufacturers instructions
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 1 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Valve Position Indicator 1 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Air Release Valve / Valve position indicator
textbox | Air Release Valve - Manufacturer:
textbox | Air Release Valve - Model:
textbox | Air Release Valve - Serial:
textbox | Valve position indicator - Manufacturer:
textbox | Valve position indicator - Model:
textbox | Valve position indicator - Serial:
checklist | 561483-ITP-001.7 - Air Valve - Delivery & Installation | itp |  |  |  |  | 561483-ITP-001.7 - DRAFT - Installation of Wingatui Chamber Air Valve2 - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of air valve 2
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.2 - Take delivery of valve position inticator 2
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint | 3.3 - Inspection of Air valve for any sign of transit damage
label | Inspection Point: Quality Control Activity - Visual check for paint coating damage and or any mechanical damage
label | Acceptance Criteria - No chips to protective coating and any mechanical damage
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.4 - Fitment - Spatial constraints
label | Inspection Point: Quality Control Activity - Verify air valves will physically fit into existing locations
label | Acceptance Criteria - Measure & Check
label | Verifying Document - This ITP. Notify Engineer of any locations where this is not achievable
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph + Written (if applicable)
label | Inspection: Key - I
label | Inspection: By - CR
checkpoint-no-status | Note:
label | Air Valve 2 & Valve Position Indicator 2 are to be fitted to Control Valve 2 (250mm dia)
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Connection to Wingatui Valve Chamber - Valve 2
label | Inspection Point: Quality Control Activity - Air Valve 2 is installed in vertical position
label | Acceptance Criteria - Air Valve is installed leak free & free of obstruction. Installation as per Manufacturers instructions
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Connection to Wingatui Valve Chamber - Valve 2
label | Inspection Point: Quality Control Activity - Valve Position Indicator 2 is installed in vertical position
label | Acceptance Criteria - Valve position Indicator is installed leak free & free of obstruction. Installation as per Manufacturers instructions
label | Verifying Document - Visual Assessment
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Air vent 2 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Red pen Mark up
label | Inspection Point: Quality Control Activity - Record Serial Numbers (if applicable) in comments section below
label | Acceptance Criteria - At completion of all items on this ITP identifying Valve Position Indicator 2 make & Model at each location
label | Verifying Document - Red line mark up drawing / This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Air Release Valve / Valve position indicator
textbox | Air Release Valve - Manufacturer:
textbox | Air Release Valve - Model:
textbox | Air Release Valve - Serial:
textbox | Valve position indicator - Manufacturer:
textbox | Valve position indicator - Model:
textbox | Valve position indicator - Serial:
checklist | 561483-ITP-002.1 - Valve - Delivery & Installation | itp |  |  |  |  | 561483-ITP-002.1 - DRAFT - Wingatui Valve 1 Valve installation - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of valve 1 assembly
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint | 3.2 - Take Delivery of Valve position indicator
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint | 3.3 - Take Delivery of Air Release Valve
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint-no-status | Note:
label | Downer HS&E to assess as to whether Valve chamber is Confined Space.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown preparation
label | Inspection Point: Quality Control Activity - Arrange with Client & Engineer for shutdown
label | Acceptance Criteria - Acceptance from client & Engineer
label | Verifying Document - Written, via email or NTC
label | Frequency - once
label | Inspection Type (Visual, other) - Written + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Valve position indicator
label | Inspection Point: Quality Control Activity - Correct installation of valve position indicator and fittings
label | Acceptance Criteria - As per manufacturers installation instructions. No leaks and orientation is correct
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Air Release Valve
label | Inspection Point: Quality Control Activity - Correct installation of air release valve and fittings
label | Acceptance Criteria - As per ClaVal installation instructions
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - System reinstatement
label | Inspection Point: Quality Control Activity - Open main valve to reinstate wate rsupply
label | Acceptance Criteria - Completion of item 4.2
label | Verifying Document - Inspection and this ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Adjust
label | Inspection Point: Quality Control Activity - Adjust the pilot valve to obtain the correct flow 113m Head.
label | Acceptance Criteria - Obtain specified flow rate ClaVal technician
label | Verifying Document - Specification flowrate
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP. Document upgrade and record new flow rate & pilot valve position setting
label | Acceptance Criteria - As per specified pressure & flow or client requirements
label | Verifying Document - Red line mark up drawing. This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Head / Flow
label | Head
label | Head - Specified: 113m
textbox | Head - Recorded:
label | Flow
label | Flow - Specified: 130L/sec
textbox | Flow - Recorded:
checklist | 561483-ITP-002.2 - Pilot Valve - Delivery & Inatallation | itp |  |  |  |  | 561483-ITP-002.2 - DRAFT - Wingatui Valve 2 Pilot Valve installation - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of pilot valve assembly
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint | 3.2 - Take Delivery of Valve position indicator
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint | 3.3 - Take Delivery of Air Release Valve
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint | 3.4 - Valve Assessment
label | Inspection Point: Quality Control Activity - Internal valve component inspection
label | Acceptance Criteria - ClaVal Assessment
label | Verifying Document - Claval report and verification
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint-no-status | Note:
label | Downer HS&E to assess as to whether Valve chamber is Confined Space.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown preparation
label | Inspection Point: Quality Control Activity - Arrange with Client & Engineer for shutdown
label | Acceptance Criteria - Acceptance from client & Engineer
label | Verifying Document - Written, via email or NTC
label | Frequency - once
label | Inspection Type (Visual, other) - Written + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Pilot Valve
label | Inspection Point: Quality Control Activity - Install new pilot valve and ancillary items
label | Acceptance Criteria - As per manufacturers installation instructions. ClaVal technician
label | Verifying Document - ClaVal Technician sign off
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Valve Position indicator
label | Inspection Point: Quality Control Activity - Correct installation of valve position indicator and fittings
label | Acceptance Criteria - As per manufacturers installation instructions. No leaks and orientation is correct
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Air Release Valve
label | Inspection Point: Quality Control Activity - Correct installation of air release valve and fittings
label | Acceptance Criteria - As per ClaVal installation instructions
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - System reinstatement
label | Inspection Point: Quality Control Activity - Open main valve to reinstate water supply
label | Acceptance Criteria - Completion of item 4.2
label | Verifying Document - Inspection and this ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Adjust
label | Inspection Point: Quality Control Activity - Adjust the pilot valve to obtain the correct flow 8.5m Head & 130L/sec
label | Acceptance Criteria - Obtain specified flow rate ClaVal technician
label | Verifying Document - Specification flowrate
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP. Document upgrade and recored new flow rate & pilot valve position setting
label | Acceptance Criteria - As per specified pressure & flow or client requirements
label | Verifying Document - Red line mark up drawing. This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Head / Flow
label | Head
label | Head - Specified: 8.5m
textbox | Head - Recorded:
label | Flow
label | Flow - Specified: 130L/sec
textbox | Flow - Recorded:
checklist | 561483-ITP-002.3 - Pilot Valve - Delivery & Inatallation | itp |  |  |  |  | 561483-ITP-002.3 - DRAFT - Stoney Knowe Valve Pilot Valve installation - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Take delivery of pilot valve assembly
label | Inspection Point: Quality Control Activity - Check that Make/Model/Dimensions are correct and all components are delivered and are damage free
label | Acceptance Criteria - Matches Design Drawings/Documents
label | Verifying Document - Drawings & Specifications. Advice from ClaVal
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - I
label | Inspection: By - IP/PM
checkpoint | 3.2 - Valve Assessment
label | Inspection Point: Quality Control Activity - Internal valve component inspection
label | Acceptance Criteria - ClaVal Assessment
label | Verifying Document - Claval report and verification
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + electronic
label | Inspection: Key - H
label | Inspection: By - IP/PM
holdpoint | HOLD POINT
checkpoint-no-status | Note:
label | Note: Valve chamber is Confined Space.
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.2 - Pilot Valve
label | Inspection Point: Quality Control Activity - Install new pilot valve and ancillary items
label | Acceptance Criteria - As per manufacturers installation instructions. ClaVal technician
label | Verifying Document - ClaVal Technician sign off
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - System reinstatement
label | Inspection Point: Quality Control Activity - Open main valve to reinstate water supply
label | Acceptance Criteria - Completion of item 4.2
label | Verifying Document - Inspection and this ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection + Photographs
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Adjust
label | Inspection Point: Quality Control Activity - Adjust the pilot valve to obtain the correct flow 8.5m Head & 70L/sec
label | Acceptance Criteria - Obtain specified flow rate ClaVal technician
label | Verifying Document - Specification flowrate
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photographs
label | Inspection: Key - I
label | Inspection: By - IP/CR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Red pen Mark up
label | Inspection Point: Quality Control Activity - At completion of all items on this ITP. Document upgrade and recored new flow rate & pilot valve position setting
label | Acceptance Criteria - As per specified pressure & flow or client requirements
label | Verifying Document - Red line mark up drawing. This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Head / Flow
label | Head
label | Head - Specified: 8.5m
textbox | Head - Recorded:
label | Flow
label | Flow - Specified: 70L/sec
textbox | Flow - Recorded:
checklist | 561483-ITP-003 - Pipeline Flushing | itp |  |  |  |  | 561483-ITP-003 - DRAFT - Stoney Knowe Pipeline Flushing
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Adaptor to pipeline
label | Inspection Point: Quality Control Activity - Manufacture adapter spool to connect Downer pumping equipment onto pipe
label | Acceptance Criteria - All air valves installed and isolating valves on off position
label | Verifying Document - None
label | Frequency - Once
label | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Excavate to expose
label | Inspection Point: Quality Control Activity - Break existing flange and connect temporary spool
label | Acceptance Criteria - HS&E documentation. Traffic Management Plan. Shoring (if applicable). Ground disturbance.
label | Verifying Document - Downer HS&E Documentation
label | Frequency - Once
label | Inspection Type (Visual, other) - Permit issuer
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Flushing
label | Inspection Point: Quality Control Activity - Flush pipeline to remove any loose material
label | Acceptance Criteria - Flush line until water runs clean
label | Verifying Document - This ITP. Client Engineer witness.
label | Frequency - once
label | Inspection Type (Visual, other) - Visual - monitor any excess debris
label | Inspection: Key - A / E / I
label | Inspection: By - SP / PM / CR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pipeline Flushed to Engineer approval
label | Inspection Point: Quality Control Activity - Pipeline Flush - Pass
label | Acceptance Criteria - Engineer / Client Approval
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Action/Visual/Issued document containing results/ Photograph
label | Inspection: Key - O
label | Inspection: By - IP / CR
checkpoint | Timestamped photographs of flushing & short video clip as evidence - Engineer to Approve
checkpoint | 5.2 - reinstatement
label | Inspection Point: Quality Control Activity - Disconnect Temporary Flushing Spool
label | Acceptance Criteria - Flushing acceptance. Engineer / Client Approval
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Verbal / Visual
label | Inspection: Key - O
label | Inspection: By - IP / CR
checklist | 561483-ITP-004 - Pressure testing to re-commissioned water main | itp |  |  |  |  | 561483-ITP-004 - DRAFT - Stoney Knowe pressure test - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - System Primary Flush
label | Inspection Point: Quality Control Activity - Completion of system flush
label | Acceptance Criteria - Completion of ITP 3
label | Verifying Document - ITP3
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photo + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - System Pressure Pre -Test
label | Inspection Point: Quality Control Activity - Ball valves to air vents are in the closed position
label | Acceptance Criteria - 4.6.6 of Specification
label | Verifying Document - Appendix E Specification
label | Frequency - Once
label | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
label | Inspection: Key - I
label | Inspection: By - IP / CR
checkpoint | 3.3 - System Pressure Test
label | Inspection Point: Quality Control Activity - Ball valves to air vents are in the closed position
label | Acceptance Criteria - 4.6.6 of Specification
label | Verifying Document - Appendix E Specification
label | Frequency - Once
label | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
label | Inspection: Key - I
label | Inspection: By - IP / CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - System Pre- test
label | Inspection Point: Quality Control Activity - Pre pressure test
label | Acceptance Criteria - Pressure test - Pass.
label | ○ Pressure test value be determined by Engineer.
label | ○ Use method as outlined in specification section 4.6.6.1
label | Verifying Document - Watermain Pressure test record - Attached
label | Frequency - once
label | Inspection Type (Visual, other) - Visual - monitor any pressure drop/time. Report any issues or concerns to Engineer
label | Inspection: Key - A
label | Inspection: By - PS / CR
checkpoint | 4.2 - System Pressure Test
label | Inspection Point: Quality Control Activity - Pressure test
label | Acceptance Criteria - Pressure test - Pass.
label | ○ Pressure test value be determined by Engineer.
label | ○ Use method as outlined in specification section 4.6.6.1
label | Verifying Document - Watermain Pressure test record - Attached
label | Frequency - once
label | Inspection Type (Visual, other) - Visual - monitor any pressure drop/time
label | Inspection: Key - A
label | Inspection: By - PS / CR
checkpoint-no-status | Note:
label | Client or Clients Representative to be present to witness pressure testing. Test pressure to be confirmed by the Engineer
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - System Pressure Testing
label | Inspection Point: Quality Control Activity - System Pressure Test - Pass
label | Acceptance Criteria - Pressure drop is less than specified value
label | Verifying Document - Watermain Pressure Test Record - Submitted
label | Frequency - once
label | Inspection Type (Visual, other) - Action/Visual/Issued document containing results/ Photograph
label | Inspection: Key - A
label | Inspection: By - IP / QE / CR
checkpoint | Timestamped photographs of pressure gauge at critical stages to be submitted as evidence - Engineer to Approve
checklist | 561483-ITP-005 - Re-Commissioned Water Main Disinfection | itp |  |  |  |  | 561483-ITP-005 - DRAFT - Pipeline disinfection - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - System Pressure Test
label | Inspection Point: Quality Control Activity - Completed installation Check all unions & Fittings are tight and leak free
label | Acceptance Criteria - 4.6.7 of Specification
label | Verifying Document - Appendix E Specification
label | Frequency - Once - After Pre system commission checks have been observed
label | Inspection Type (Visual, other) - Specification - Water Main Pressure Test Record
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Drain pipeline of pressure test water
label | Inspection Point: Quality Control Activity - Upon completion of pressure test
label | Acceptance Criteria - 4.6.7 of Specification
label | Verifying Document - Appendix E Specification
label | Frequency - Post Pressure testing
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Arrange for client attendance/witness
label | Inspection Point: Quality Control Activity - During Disinfection process
label | Acceptance Criteria - Client representative availability
label | Verifying Document - DCC Approved Flushing & Disinfection of Water Mains - Document
label | Frequency - Once - After completed checks
label | Inspection Type (Visual, other) - Attached Flushing & Disinfection Document
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Ensure all pipe fittings, valves & other connections are tight and leak free (as per pressure test)
label | Inspection Point: Quality Control Activity - At completiion of installation and prior to pressure testing
label | Acceptance Criteria - Installation complete
label | Verifying Document - Check list. Initial & Verification on the Schematic drawing
label | Frequency - once
label | Inspection Type (Visual, other) - Visual - monitor any pressure drop/time
label | Inspection: Key - A
label | Inspection: By - IP / SP
checkpoint | 4.2 - Prepare to flush and disinfect new pipe, Fittings & pump
label | Inspection Point: Quality Control Activity - Post pressure testing
label | Acceptance Criteria - Pressure test - Pass
label | Verifying Document - Pressure test - Pass
label | ○ Flushing & Disinfection of Water Mains Document
label | Frequency - once
label | Inspection Type (Visual, other) - Closed loop circulation as installed by Bruce Allan
label | Inspection: Key - A
label | Inspection: By - IP / SP
checkpoint | 4.3 - Calculate system volume to determine required chemical quantity.
label | Inspection Point: Quality Control Activity - Pre-disinfect process
label | Acceptance Criteria - Watermeter or calculation
label | Verifying Document - NZS4404:2010
label | Frequency - once
label | Inspection Type (Visual, other) - Visual - Document volumes on client provided tdocumentation
label | Inspection: Key - A
label | Inspection: By - IP / SP
checkpoint | 4.4 - Undertake disinfection process
label | Inspection Point: Quality Control Activity - Monitor circulation
label | Acceptance Criteria - Monitor values (this may need done more than once due to age) to achieve acceptable level
label | Verifying Document - Client FLUSHING & DISINFECTION OF WATERMAIN DOCUMENT
label | Frequency - once - or more as required
label | Inspection Type (Visual, other) - Visual, Document and photograph
label | Inspection: Key - A
label | Inspection: By - IP / SP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - System Flush & Disinfect
label | Inspection Point: Quality Control Activity - Upon successful pressure test
label | Acceptance Criteria - NZS4404:2010
label | Verifying Document - DCC Standard Flushing & Disinfection of Watermain document
label | Frequency - once
label | Inspection Type (Visual, other) - Action/ Visual/ Time/ Photograph
label | Inspection: Key - O
label | Inspection: By - QE / CR
checkpoint | Video footage of pump and disinfection process in action - Engineer to Approve
checklist | 561483-ITP-007.1 - Installation of Pump 1 isolating valves - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-007.1 - Pump 1 Isolation Valves Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 1
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 1
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown the pumping system (all pumps)
label | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
label | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Removal of suction side isolation valve to pump 1 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.3 - Removal of discharge side isolation valve to pump 1 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.4 - Suction side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Discharge side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | All valves to be left in closed position
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Returning existing pump 1 for duty
label | Inspection Point: Quality Control Activity - Purge pump 1 of any entrained air
label | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
label | Verifying Document - Visual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Power reinstatement to pump 1
label | Inspection Point: Quality Control Activity - Remove lock out tag pump 1
label | Acceptance Criteria - Completion of 5.1 above
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP