## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561483-ITP-007.2 - Installation of Pump 2 isolating valves - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-007.2 - Pump 2 Isolation Valves Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 2
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 2
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown the pumping system (all pumps)
label | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
label | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Removal of suction side isolation valve to pump 2 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.3 - Removal of discharge side isolation valve to pump 2 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.4 - Suction side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Discharge side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | All valves to be left in closed position
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Returning existing pump 2 for duty
label | Inspection Point: Quality Control Activity - Purge pump 2 of any entrained air
label | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
label | Verifying Document - Visual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Power reinstatement to pump 2
label | Inspection Point: Quality Control Activity - Remove lock out tag pump 2
label | Acceptance Criteria - Completion of 5.1 above
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-007.4 - Installation of Pump 3 isolating valves - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-007.3 - Pump 3 Isolation Valves Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 3
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 3
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown the pumping system (all pumps)
label | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
label | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Removal of suction side isolation valve to pump 3 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.3 - Removal of discharge side isolation valve to pump 3 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.4 - Suction side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Discharge side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | All valves to be left in closed position
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Returning existing pump 3 for duty
label | Inspection Point: Quality Control Activity - Purge pump 3 of any entrained air
label | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
label | Verifying Document - Visual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Power reinstatement to pump 3
label | Inspection Point: Quality Control Activity - Remove lock out tag pump 3
label | Acceptance Criteria - Completion of 5.1 above
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-007.4 - Installation of Pump 4 isolating valves - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-007.4 - Pump 4 Isolation Valves Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 4
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 4
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown the pumping system (all pumps)
label | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
label | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Removal of suction side isolation valve to pump 4 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.3 - Removal of discharge side isolation valve to pump 4 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.4 - Suction side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Discharge side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | All valves to be left in closed position
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Returning existing pump 4 for duty
label | Inspection Point: Quality Control Activity - Purge pump 4 of any entrained air
label | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
label | Verifying Document - Visual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Power reinstatement to pump 4
label | Inspection Point: Quality Control Activity - Remove lock out tag pump 4
label | Acceptance Criteria - Completion of 5.1 above
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-007.5 - Installation of Pump 5 isolating valves - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-007.5 - Pump 5 Isolation Valves Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 5
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 5
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown the pumping system (all pumps)
label | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
label | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Removal of suction side isolation valve to pump 5 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.3 - Removal of discharge side isolation valve to pump 5 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.4 - Suction side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Discharge side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | All valves to be left in closed position
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Returning existing pump 5 for duty
label | Inspection Point: Quality Control Activity - Purge pump 5 of any entrained air
label | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
label | Verifying Document - Visual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Power reinstatement to pump 5
label | Inspection Point: Quality Control Activity - Remove lock out tag pump 5
label | Acceptance Criteria - Completion of 5.1 above
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-007.6 - Installation of Pump 6 isolating valves - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-007.6 - Pump 6 Isolation Valves Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Valves (Suction & Discharge) to site from Downer storage facility - Pump 6
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Dress Sets to site from Downer storage facility - Pump 6
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Must be on the Approved Products list
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system to replace suction & discharge isolating valves for pumps 1 through 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown the pumping system (all pumps)
label | Inspection Point: Quality Control Activity - Isolate pumps 1 through 6 Electrically & Mechanically and residual water in manifolds drained
label | Acceptance Criteria - Ensure reservoir tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Removal of suction side isolation valve to pump 6 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.3 - Removal of discharge side isolation valve to pump 6 (wafer type). Inspect pump flange and valve flange
label | Inspection Point: Quality Control Activity - Ensure no residual gasket material remains on flange surfaces. Clean if necessary
label | Acceptance Criteria - Surfaces are clean
label | Verifying Document - Visual
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 4.4 - Suction side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Discharge side valve installation
label | Inspection Point: Quality Control Activity - Install valve ensuring gaskets are not deformed and there is sufficient clearance for handle operation
label | Acceptance Criteria - All valve bolts are tightened and M16 bolts are torqued to 80N.m
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | All valves to be left in closed position
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Returning existing pump 6 for duty
label | Inspection Point: Quality Control Activity - Purge pump 6 of any entrained air
label | Acceptance Criteria - All air is removed and water is visible through bleed valve and suction and discharge valves are open and no leaks present
label | Verifying Document - Visual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Power reinstatement to pump 6
label | Inspection Point: Quality Control Activity - Remove lock out tag pump 6
label | Acceptance Criteria - Completion of 5.1 above
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-008.1 - Delivery & Installation of Pump 1 | itp |  |  |  |  | 561483-ITP-008.1 - Pump 1 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Pump 1 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
label | Acceptance Criteria - Pumps are damage free
label | Verifying Document - 1. Pump delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 1
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown Pump 1
label | Inspection Point: Quality Control Activity - Isolate Pump 1 Electrically & Mechanically and release any residual pressure.
label | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Remove Pump 1 base plate - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Remove fixings from floor
label | Acceptance Criteria - Pump 1 is removed
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Install New Proprietary baseplate for Pump 1 - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Check dimensions
label | Acceptance Criteria - Plinth is in suitable condition
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Pump 1 Installation
label | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 1 into position & bolt down
label | Acceptance Criteria - Pump base plate mounted in correct position
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Install gaskets & dress sets
label | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
label | Acceptance Criteria - Torque to 80N.m
label | Verifying Document - NZ Water Standards
label | Frequency - Once per bolt
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Preparation to run Pump 1
label | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
label | Acceptance Criteria - Water visible from purging valve
label | Verifying Document - This ITP
label | Frequency - Once/per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 1 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Check for any leaks
label | Acceptance Criteria - No visible leaks
label | Verifying Document - As per methodology
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - VFD 1 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - Power to VFD1
label | Acceptance Criteria - Completion of VFD1 ITP
label | Verifying Document - 561483-ITP-009.1
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-008.2 - Delivery & Installation of Pump 2 | itp |  |  |  |  | 561483-ITP-008.2 - Pump 2 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Pump 2 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. Pump delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 2
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown Pump 2
label | Inspection Point: Quality Control Activity - Isolate Pump 2 Electrically & Mechanically and release any residual pressure.
label | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Remove Pump 2 base plate - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Remove fixings from floor
label | Acceptance Criteria - Pump 2 is removed
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Install New Proprietary baseplate for Pump 2 - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Check dimensions
label | Acceptance Criteria - Plinth is in suitable condition
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Pump 2 Installation
label | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 2 into position & bolt down
label | Acceptance Criteria - Pump base plate mounted in correct position
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Install gaskets & dress sets
label | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
label | Acceptance Criteria - Torque to 80N.m
label | Verifying Document - NZ Water Standards
label | Frequency - Once per bolt
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Preparation to run Pump 2
label | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
label | Acceptance Criteria - Water visible from purging valve
label | Verifying Document - This ITP
label | Frequency - Once/per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 2 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Check for any leaks
label | Acceptance Criteria - No visible leaks
label | Verifying Document - As per methodology
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - VFD 2 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - Power to VFD2
label | Acceptance Criteria - Completion of VFD2 ITP
label | Verifying Document - 561483-ITP-009.2
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-008.3 - Delivery & Installation of Pump 3 | itp |  |  |  |  | 561483-ITP-008.3 - Pump 3 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Pump 3 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. Pump delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 3
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown Pump 3
label | Inspection Point: Quality Control Activity - Isolate Pump 3 Electrically & Mechanically and release any residual pressure.
label | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Remove Pump 3 base plate - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Remove fixings from floor
label | Acceptance Criteria - Pump 3 is removed
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Install New Proprietary baseplate for Pump 3 - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Check dimensions
label | Acceptance Criteria - Plinth is in suitable condition
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Pump 3 Installation
label | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 3 into position & bolt down
label | Acceptance Criteria - Pump base plate mounted in correct position
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Install gaskets & dress sets
label | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
label | Acceptance Criteria - Torque to 80N.m
label | Verifying Document - NZ Water Standards
label | Frequency - Once per bolt
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Preparation to run Pump 3
label | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
label | Acceptance Criteria - Water visible from purging valve
label | Verifying Document - This ITP
label | Frequency - Once/per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 3 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Check for any leaks
label | Acceptance Criteria - No visible leaks
label | Verifying Document - As per methodology
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - VFD 3 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - Power to VFD3
label | Acceptance Criteria - Completion of VFD3 ITP
label | Verifying Document - 561483-ITP-009.3
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-008.4 - Delivery & Installation of Pump 4 | itp |  |  |  |  | 561483-ITP-008.4 - Pump 4 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Pump 4 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. Pump delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 4
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown Pump 4
label | Inspection Point: Quality Control Activity - Isolate Pump 4 Electrically & Mechanically and release any residual pressure.
label | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Remove Pump 4 base plate - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Remove fixings from floor
label | Acceptance Criteria - Pump 4 is removed
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Install New Proprietary baseplate for Pump 4 - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Check dimensions
label | Acceptance Criteria - Plinth is in suitable condition
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Pump 4 Installation
label | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 4 into position & bolt down
label | Acceptance Criteria - Pump base plate mounted in correct position
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Install gaskets & dress sets
label | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
label | Acceptance Criteria - Torque to 80N.m
label | Verifying Document - NZ Water Standards
label | Frequency - Once per bolt
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Preparation to run Pump 4
label | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
label | Acceptance Criteria - Water visible from purging valve
label | Verifying Document - This ITP
label | Frequency - Once/per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 4 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Check for any leaks
label | Acceptance Criteria - No visible leaks
label | Verifying Document - As per methodology
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - VFD 4 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - Power to VFD4
label | Acceptance Criteria - Completion of VFD4 ITP
label | Verifying Document - 561483-ITP-009.4
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-008.5 - Delivery & Installation of Pump 5 | itp |  |  |  |  | 561483-ITP-008.5 - Pump 5 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Pump 5 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. Pump delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 5
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown Pump 5
label | Inspection Point: Quality Control Activity - Isolate Pump 5 Electrically & Mechanically and release any residual pressure.
label | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Remove Pump 5 base plate - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Remove fixings from floor
label | Acceptance Criteria - Pump 5 is removed
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Install New Proprietary baseplate for Pump 5 - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Check dimensions
label | Acceptance Criteria - Plinth is in suitable condition
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Pump 5 Installation
label | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 5 into position & bolt down
label | Acceptance Criteria - Pump base plate mounted in correct position
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Install gaskets & dress sets
label | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
label | Acceptance Criteria - Torque to 80N.m
label | Verifying Document - NZ Water Standards
label | Frequency - Once per bolt
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Preparation to run Pump 5
label | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
label | Acceptance Criteria - Water visible from purging valve
label | Verifying Document - This ITP
label | Frequency - Once/per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 5 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Check for any leaks
label | Acceptance Criteria - No visible leaks
label | Verifying Document - As per methodology
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - VFD 5 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - Power to VFD 5
label | Acceptance Criteria - Completion of VFD 5 ITP
label | Verifying Document - 561483-ITP-009.5
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-008.6 - Delivery & Installation of Pump 6 | itp |  |  |  |  | 561483-ITP-008.6 - Pump 6 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of Pump 6 to site from Downer storage facility
label | Inspection Point: Quality Control Activity - Check and verify that correct pumps are delivered
label | Acceptance Criteria - Pump is damage free
label | Verifying Document - 1. Pump delivery docket.
label | 2. Pump storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Arrange with client and Engineering team to shut down Pump 6
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team. New lugged isolation valves are installed
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Shutdown Pump 6
label | Inspection Point: Quality Control Activity - Isolate Pump 6 Electrically & Mechanically and release any residual pressure.
label | Acceptance Criteria - Ensure reservoir supply tanks are full before proceeding
label | Verifying Document - Advice from DCC Operations
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Written + Verbal
label | Inspection: Key - C
label | Inspection: By - CR
checkpoint | 4.2 - Remove Pump 6 base plate - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Remove fixings from floor
label | Acceptance Criteria - Pump 6 is removed
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Install New Proprietary baseplate for Pump 6 - This may have to be cut into individual sections to accommodate each pump
label | Inspection Point: Quality Control Activity - Check dimensions
label | Acceptance Criteria - Plinth is in suitable condition
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Pump 6 Installation
label | Inspection Point: Quality Control Activity - Lifting & Mounting Pump 6 into position & bolt down
label | Acceptance Criteria - Pump base plate mounted in correct position
label | Verifying Document - 1.Grundfos documentation.
label | 2. Project Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Install gaskets & dress sets
label | Inspection Point: Quality Control Activity - Tighten bolts in correct opposing sequence
label | Acceptance Criteria - Torque to 80N.m
label | Verifying Document - NZ Water Standards
label | Frequency - Once per bolt
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Preparation to run Pump 6
label | Inspection Point: Quality Control Activity - Open isolation valves and purge pumps of air
label | Acceptance Criteria - Water visible from purging valve
label | Verifying Document - This ITP
label | Frequency - Once/per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pump 6 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Check for any leaks
label | Acceptance Criteria - No visible leaks
label | Verifying Document - As per methodology
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - VFD 6 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - Power to VFD 6
label | Acceptance Criteria - Completion of VFD 6 ITP
label | Verifying Document - 561483-ITP-009.6
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-009.1 - Installation of VFD 1 (Pump 1) - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-009.1 - VFD 1 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 1
label | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
label | Acceptance Criteria - VFD is damage free
label | Verifying Document - 1. VFD delivery docket.
label | 2. VFD storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 1
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Approved Products list and approved for use
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Electrically Isolate Pump 1 at Control Cabinet. Ensure no issues with Grundfos Controller.
label | Inspection Point: Quality Control Activity - Isolation is applied to Pump 1 and existing VFD
label | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Electrically disconnect Pump 1
label | Inspection Point: Quality Control Activity - All electrical connections are removed
label | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 1 disconnected, no voltage on cabling.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Remove Pump 1 Cable from Motor to VFD
label | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 1, Cable Removed From Support System
label | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 1).
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Remove Pump 1 VFD
label | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
label | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Mount new Pump 1 VFD
label | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
label | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Remove VFD 1 Feed Cabling and Isolators
label | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
label | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Install new supply cabling and isolators for VFD 1
label | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD1 is prepped and tested
label | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Terminate Cabling for VFD 1
label | Inspection Point: Quality Control Activity - Cables fitted off into VFD 1 isolators and supply cabinet.
label | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 1
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Remove isolations
label | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
label | Acceptance Criteria - isolations removed circuits re-energised
label | Verifying Document - Lock-out Tag out Register
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Configure VFD 1
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD configured correctly, controller setup adjusted
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Confirm correct operation of VFD 1 and pump
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Stage 1 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Pump 1 in service
label | Acceptance Criteria - Pump 1 is installed. Valves installed to Pump 1 are installed
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Stage 1 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - VFD 1 in service
label | Acceptance Criteria - VFD 1 is installed and parameters set by Grundfos
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
checklist | 561483-ITP-009.2 - Installation of VFD 2 (Pump 2) - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-009.2 - VFD 2 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 2
label | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
label | Acceptance Criteria - VFD is damage free
label | Verifying Document - 1. VFD delivery docket.
label | 2. VFD storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 2
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Approved Products list and approved for use
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Electrically Isolate Pump 2 at Control Cabinet. Ensure no issues with Grundfos Controller.
label | Inspection Point: Quality Control Activity - Isolation is applied to Pump 2 and existing VFD
label | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Electrically disconnect Pump 2
label | Inspection Point: Quality Control Activity - All electrical connections are removed
label | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 2 disconnected, no voltage on cabling.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Remove Pump 2 Cable from Motor to VFD
label | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 2, Cable Removed From Support System
label | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 2).
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Remove Pump 2 VFD
label | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
label | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Mount new Pump 2 VFD
label | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
label | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Remove VFD 2 Feed Cabling and Isolators
label | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
label | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Install new supply cabling and isolators for VFD 2
label | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD2 is prepped and tested
label | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Terminate Cabling for VFD 2
label | Inspection Point: Quality Control Activity - Cables fitted off into VFD 2 isolators and supply cabinet.
label | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 2
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Remove isolations
label | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
label | Acceptance Criteria - isolations removed circuits re-energised
label | Verifying Document - Lock-out Tag out Register
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Configure VFD 2
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD configured correctly, controller setup adjusted
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Confirm correct operation of VFD 2 and pump
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Stage 2 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Pump 2 in service
label | Acceptance Criteria - Pump 2 is installed. Valves installed to Pump 2 are installed
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Stage 2 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - VFD 2 in service
label | Acceptance Criteria - VFD 2 is installed and parameters set by Grundfos
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
checklist | 561483-ITP-009.3 - Installation of VFD 3 (Pump 3) - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-009.3 - VFD 3 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 3
label | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
label | Acceptance Criteria - VFD is damage free
label | Verifying Document - 1. VFD delivery docket.
label | 2. VFD storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 3
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Approved Products list and approved for use
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 4.1 - Electrically Isolate Pump 3 at Control Cabinet. Ensure no issues with Grundfos Controller.
label | Inspection Point: Quality Control Activity - Isolation is applied to Pump 3 and existing VFD
label | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Electrically disconnect Pump 3
label | Inspection Point: Quality Control Activity - All electrical connections are removed
label | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 3 disconnected, no voltage on cabling.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Remove Pump 3 Cable from Motor to VFD
label | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 3, Cable Removed From Support System
label | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 3).
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Remove Pump 3 VFD
label | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
label | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Mount new Pump 3 VFD
label | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
label | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Remove VFD 3 Feed Cabling and Isolators
label | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
label | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Install new supply cabling and isolators for VFD 3
label | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 3 is prepped and tested
label | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Terminate Cabling for VFD 3
label | Inspection Point: Quality Control Activity - Cables fitted off into VFD 3 isolators and supply cabinet.
label | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 3
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Remove isolations
label | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
label | Acceptance Criteria - isolations removed circuits re-energised
label | Verifying Document - Lock-out Tag out Register
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Configure VFD 3
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD configured correctly, controller setup adjusted
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Confirm correct operation of VFD 3 and pump
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 5.1 - Stage 3 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Pump 3 in service
label | Acceptance Criteria - Pump 3 is installed. Valves installed to Pump 3 are installed
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Stage 3 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - VFD 3 in service
label | Acceptance Criteria - VFD 3 is installed and parameters set by Grundfos
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
checklist | 561483-ITP-009.4 - Installation of VFD 4 (Pump 4) - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-009.4 - VFD 4 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 4
label | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
label | Acceptance Criteria - VFD is damage free
label | Verifying Document - 1. VFD delivery docket.
label | 2. VFD storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 4
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Approved Products list and approved for use
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Electrically Isolate Pump 4 at Control Cabinet. Ensure no issues with Grundfos Controller.
label | Inspection Point: Quality Control Activity - Isolation is applied to Pump 4 and existing VFD
label | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Electrically disconnect Pump 4
label | Inspection Point: Quality Control Activity - All electrical connections are removed
label | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 4 disconnected, no voltage on cabling.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Remove Pump 4 Cable from Motor to VFD
label | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 4, Cable Removed From Support System
label | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 4).
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Remove Pump 4 VFD
label | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
label | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Mount new Pump 4 VFD
label | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
label | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Remove VFD 4 Feed Cabling and Isolators
label | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
label | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Install new supply cabling and isolators for VFD 4
label | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 4 is prepped and tested
label | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Terminate Cabling for VFD 4
label | Inspection Point: Quality Control Activity - Cables fitted off into VFD 4 isolators and supply cabinet.
label | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 4
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Remove isolations
label | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
label | Acceptance Criteria - isolations removed circuits re-energised
label | Verifying Document - Lock-out Tag out Register
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Configure VFD 4
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD configured correctly, controller setup adjusted
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Confirm correct operation of VFD 4 and pump
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Stage 4 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Pump 4 in service
label | Acceptance Criteria - Pump 4 is installed. Valves installed to Pump 4 are installed
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Stage 4 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - VFD 4 in service
label | Acceptance Criteria - VFD 4 is installed and parameters set by Grundfos
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
checklist | 561483-ITP-009.5 - Installation of VFD 5 (Pump 5) - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-009.5 - VFD 5 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 5
label | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
label | Acceptance Criteria - VFD is damage free
label | Verifying Document - 1. VFD delivery docket.
label | 2. VFD storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 5
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Approved Products list and approved for use
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 4.1 - Electrically Isolate Pump 5 at Control Cabinet. Ensure no issues with Grundfos Controller.
label | Inspection Point: Quality Control Activity - Isolation is applied to Pump 5 and existing VFD
label | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Electrically disconnect Pump 5
label | Inspection Point: Quality Control Activity - All electrical connections are removed
label | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 5 disconnected, no voltage on cabling.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Remove Pump 5 Cable from Motor to VFD
label | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 5, Cable Removed From Support System
label | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 5).
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Remove Pump 5 VFD
label | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
label | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Mount new Pump 5 VFD
label | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
label | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Remove VFD 5 Feed Cabling and Isolators
label | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
label | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Install new supply cabling and isolators for VFD 5
label | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 5 is prepped and tested
label | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Terminate Cabling for VFD 5
label | Inspection Point: Quality Control Activity - Cables fitted off into VFD 5 isolators and supply cabinet.
label | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 5
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Remove isolations
label | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
label | Acceptance Criteria - isolations removed circuits re-energised
label | Verifying Document - Lock-out Tag out Register
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Configure VFD 5
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD configured correctly, controller setup adjusted
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Confirm correct operation of VFD 5 and pump
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 5.1 - Stage 5 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Pump 5 in service
label | Acceptance Criteria - Pump 5 is installed. Valves installed to Pump 5 are installed
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Stage 5 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - VFD 5 in service
label | Acceptance Criteria - VFD 5 is installed and parameters set by Grundfos
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)
checklist | 561483-ITP-009.6 - Installation of VFD 6 (Pump 6) - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-009.6 - VFD 6 Delivery & Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Delivery of VFDs to site from Downer storage facility - VFD 6
label | Inspection Point: Quality Control Activity - Check and verify that correct VFD is delivered
label | Acceptance Criteria - VFD is damage free
label | Verifying Document - 1. VFD delivery docket.
label | 2. VFD storage ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.2 - Delivery of Ancillaries to site from Downer storage facility - VFD 6
label | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client. Check quantities are correct
label | Acceptance Criteria - Approved Products list and approved for use
label | Verifying Document - Specification - Approved Materials list
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.3 - Arrange with client and Engineering team to shut down the system
label | Inspection Point: Quality Control Activity - Application via NTE and discuss methodology
label | Acceptance Criteria - Upon approval from Client & Engineering team
label | Verifying Document - Written approval
label | Frequency - Once
label | Inspection Type (Visual, other) - other
label | Inspection: Key - R
label | Inspection: By - CR
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Electrically Isolate Pump 6 at Control Cabinet. Ensure no issues with Grundfos Controller.
label | Inspection Point: Quality Control Activity - Isolation is applied to Pump 6 and existing VFD
label | Acceptance Criteria - VFD confirmed to no longer have a voltage on input, sufficient time has passed to allow stored energy to dissipate. (Estimated time 10 minutes)
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Electrically disconnect Pump 6
label | Inspection Point: Quality Control Activity - All electrical connections are removed
label | Acceptance Criteria - Remaining 5 pumps are functioning correctly, Pump 6 disconnected, no voltage on cabling.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Remove Pump 6 Cable from Motor to VFD
label | Inspection Point: Quality Control Activity - Cables Disconnected from Drive and Pump 6, Cable Removed From Support System
label | Acceptance Criteria - All mechanical & Electrical disconnections are completed (Pump 6).
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Remove Pump 6 VFD
label | Inspection Point: Quality Control Activity - VFD Removed from Wall and redundant fasteners removed
label | Acceptance Criteria - Wall is clear of obstructions in preparation for new VFD install
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Mount new Pump 6 VFD
label | Inspection Point: Quality Control Activity - new VFD mounted to wall on Unistrut
label | Acceptance Criteria - VFD mounted securely, Spacings compliant with manufacturers requirements.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Remove VFD 6 Feed Cabling and Isolators
label | Inspection Point: Quality Control Activity - Cabling Removed From Cabinet and cable trays.
label | Acceptance Criteria - Cables Removed, isolators disconnected and removed from wall.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Install new supply cabling and isolators for VFD 6
label | Inspection Point: Quality Control Activity - Cables installed and run into cabinet, isolators and VFD 6 is prepped and tested
label | Acceptance Criteria - Cables run and secured correctly, cables verified via point to point testing, insulation and resistance tests.
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Terminate Cabling for VFD 6
label | Inspection Point: Quality Control Activity - Cables fitted off into VFD 6 isolators and supply cabinet.
label | Acceptance Criteria - Cables terminated. lugs used as appropriate, Cable glands installed correctly, isolators rated for Full load current of VFD 6
label | Verifying Document - Cable Test Sheets
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Remove isolations
label | Inspection Point: Quality Control Activity - Drives motors and isolators fit off, all covers replaced.
label | Acceptance Criteria - isolations removed circuits re-energised
label | Verifying Document - Lock-out Tag out Register
label | Frequency - Once per pump
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Configure VFD 6
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD configured correctly, controller setup adjusted
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Confirm correct operation of VFD 6 and pump
label | Inspection Point: Quality Control Activity - VFD configured with assistance from Grundfos representative, pump controller adjusted for new pumps
label | Acceptance Criteria - VFD ramp and regulate flow rates correctly. pumps rotate in correct direction, VFDs operate correctly on controller
label | Verifying Document - VFD test sheets
label | Frequency - Once per VFD
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Electrical connection of pumps and commissioning are covered in separate ITP's
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Stage 6 Changeover Complete (Mechanical)
label | Inspection Point: Quality Control Activity - Pump 6 in service
label | Acceptance Criteria - Pump 6 is installed. Valves installed to Pump 6 are installed
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Stage 6 Changeover Complete (Electrical)
label | Inspection Point: Quality Control Activity - VFD 6 in service
label | Acceptance Criteria - VFD 6 is installed and parameters set by Grundfos
label | Verifying Document - Grundfos commissioning report
label | Frequency - once per pump
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Engineer & Client to determine the sequencing of the changeover based on the demand for the water. This work will likely occur during off peak demand period (night work)