## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561483-ITP-010 - Electrical Installation, Generator Changeover & Switchboard installation | itp |  |  |  |  | 561483-ITP-010 - Electrical & Controls Installation
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Inspection of Generator Changeover Switch Cabinet
label | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Verifying Document - Email or NTE to report
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.2 - Inspection of Generator Connection Enclosure.
label | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Verifying Document - Email or NTE to report
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + inspection
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.3 - Delivery of Generator Changeover Switch Cabinet to Site
label | Inspection Point: Quality Control Activity - Check and verify that the Generator Changeover Switch Cabinet has been delivered damage free
label | Acceptance Criteria - Cabinet is damage free
label | Verifying Document - Switchboard Builder Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + inspection
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.4 - Delivery of Generator Connection Cabinet to site
label | Inspection Point: Quality Control Activity - Check and verify that the Generator Connection Cabinet has been delivered damage free
label | Acceptance Criteria - Cabinet is damage free
label | Verifying Document - Switchboard Builder Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + inspection
label | Inspection: Key - C
label | Inspection: By - IP
checkpoint | 3.5 - Inspection of Switchboard
label | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
label | Acceptance Criteria - Visual check and report any defects or areas of concern
label | Verifying Document - Email or NTE to report
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - C
label | Inspection: By - IP/B
checkpoint | 3.6 - Delivery of Switchboard to site
label | Inspection Point: Quality Control Activity - Check and verify that the Switchboard has been delivered damage free
label | Acceptance Criteria - Switchboard is damage free
label | Verifying Document - Switchboard Builder Delivery Docket
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + inspection
label | Inspection: Key - C
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Mount Support Brackets To Hand rails for Cabinet
label | Inspection Point: Quality Control Activity - Support Brackets mounted to Handrail
label | Acceptance Criteria - Mounts are secure and firm, with no excessive deflection
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Mount Generator Change over Cabinet to Mounts.
label | Inspection Point: Quality Control Activity - Cabinet Mounted
label | Acceptance Criteria - Cabinet is mounted securely, all bolts tight, seals intact and in good condition
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Mount Generator Connection Cabinet on outside of Building
label | Inspection Point: Quality Control Activity - Cabinet Mounted
label | Acceptance Criteria - Cabinet Mounted Securely to wall
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Install Cable Supports for generator Change over
label | Inspection Point: Quality Control Activity - Cable ladder installed securely, with adequately spaced supports.
label | Acceptance Criteria - Cable ladder mounted correctly.
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - Mount Generator Connection Cabinet on outside of Building
label | Inspection Point: Quality Control Activity - Cabinet Mounted
label | Acceptance Criteria - Cabinet Mounted Securely to wall
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Install Cable Supports for generator Change over Cabling
label | Inspection Point: Quality Control Activity - Cable ladder installed securely, with adequately spaced supports.
label | Acceptance Criteria - Cable ladder mounted correctly.
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Install Cabling Between Generator Connection Cabinet and Generator Change over Cabinet
label | Inspection Point: Quality Control Activity - Cabling installed, secured to support systems, no excessively tight bends on cables.
label | Acceptance Criteria - Cables adequately Secured, Cable Ties cut off clean with no sharp edges.
label | Verifying Document - This ITP
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Terminate cables into Generator Connection Cabinet
label | Inspection Point: Quality Control Activity - Cables fit off into cabinet.
label | Acceptance Criteria - Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated
label | Verifying Document - Cable/Cabinet ITR's
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Isolate Supply to Pump Station at WTP Switchboard.
label | Inspection Point: Quality Control Activity - Supply isolated
label | Acceptance Criteria - power to Pump Station isolated, no voltage/ current present on cables
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - W
label | Inspection: By - SP
checkpoint | 4.10 - Disconnect Mains Supply from Pump Station Switchboard and relocated to Changeover Cabinet
label | Inspection Point: Quality Control Activity - Cables disconnected and routed to changeover enclosure
label | Acceptance Criteria - Cables clearly identified for origin/phase.
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - W
label | Inspection: By - SP
checkpoint | 4.11 - Terminate cables into Generator Changeover Cabinet
label | Inspection Point: Quality Control Activity - Cables fit off into cabinet.
label | Acceptance Criteria - Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated to correct terminals on Changeover Switch.
label | Verifying Document - Cable/Cabinet ITR's
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Install New Cables Between Changeover Switch And Switchboard
label | Inspection Point: Quality Control Activity - Cables installed and secured to existing cable trays
label | Acceptance Criteria - Cables are correctly sized, secured adequately to cable trays.
label | Verifying Document - Cable/Cabinet ITR's
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.13 - Terminate Cables into Switchboard
label | Inspection Point: Quality Control Activity - Cables fit off into Switchboard and Generator Changeover.
label | Acceptance Criteria - Cables enter into Enclosures through appropriately sized glands, cables fit off correctly and terminated
label | Verifying Document - Cable/Cabinet ITR's
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.14 - Mount Switchboard
label | Inspection Point: Quality Control Activity - Cabinet Mounted
label | Acceptance Criteria - Cabinet is mounted securely, all bolts tight, seals intact and in good condition
label | Verifying Document - This ITP
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.15 - Terminate cables into Switchboard
label | Inspection Point: Quality Control Activity - Cables fit off into cabinet.
label | Acceptance Criteria - Cables enter into Enclosure through appropriately sized glands, cables fit off correctly and terminated
label | Verifying Document - Cable/Cabinet ITR's
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Inspection
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Switchboard
label | Inspection Point: Quality Control Activity - New Cables installed, insulation, continuity and polarity tests completed, phase rotation confirmed
label | Acceptance Criteria - Electrical Testing completed, board Livened and operating as prior to modification.
label | Verifying Document - Cable ITR's/ COC
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Generator Changeover
label | Inspection Point: Quality Control Activity - Cabling installed and terminated. changeover tested and inability for back feeding of supply confirmed.
label | Acceptance Criteria - Changeover operation Verified as satisfactory. unable to live test due to lack of a suitably sized Generator
label | Verifying Document - Cable/Cabinet ITR's, COC, ROI From Inspector
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.3 - Generator Connection Cabinet
label | Inspection Point: Quality Control Activity - Generator Connection Cabinet mounted, cabling fit off, testing completed.
label | Acceptance Criteria - Cabinet Mounted Securely, polarity of connections correct,
label | Verifying Document - Cable/Cabinet ITR's, COC
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-011 - Commissioning Pumps 1 through 6 | itp |  |  |  |  | 561483-ITP-011 - Pumps 1 through 6 Commissioning - HOLD POINT
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint-no-status | Note:
label | Pumps have been set to match the existing pump performance temporarily. This ITP is for the final commissioning of the system
checkpoint | 3.1 - Pump 1
label | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
label | Acceptance Criteria - VFD 1 configured to match existing pump performance
label | Verifying Document - 561483-ITP-009.1
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Pump 2
label | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
label | Acceptance Criteria - VFD 2 configured to match existing pump performance
label | Verifying Document - 561483-ITP-009.2
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Pump 3
label | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
label | Acceptance Criteria - VFD 3 configured to match existing pump performance
label | Verifying Document - 561483-ITP-009.3
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.4 - Pump 4
label | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
label | Acceptance Criteria - VFD 4 configured to match existing pump performance
label | Verifying Document - 561483-ITP-009.4
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.5 - Pump 5
label | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
label | Acceptance Criteria - VFD 5 configured to match existing pump performance
label | Verifying Document - 561483-ITP-009.5
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.6 - Pump 6
label | Inspection Point: Quality Control Activity - Set Pump Flowrate and establish communication with Grundfos Main controller
label | Acceptance Criteria - VFD 6 configured to match existing pump performance
label | Verifying Document - 561483-ITP-009.6
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Pump 1
label | Inspection Point: Quality Control Activity - Set pump 1 final pressure and flowrates
label | Acceptance Criteria - Pump 1 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
label | Verifying Document - Grundfos controller display/Commissioning sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - O/W
label | Inspection: By - Grundfos Commissioning Engineer
checkpoint | 4.2 - Pump 2
label | Inspection Point: Quality Control Activity - Set pump 2 final pressure and flowrates
label | Acceptance Criteria - Pump 2 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
label | Verifying Document - Grundfos controller display/Commissioning sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - O/W
label | Inspection: By - Grundfos Commissioning Engineer
checkpoint | 4.3 - Pump 3
label | Inspection Point: Quality Control Activity - Set pump 3 final pressure and flowrates
label | Acceptance Criteria - Pump 3 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
label | Verifying Document - Grundfos controller display/Commissioning sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - O/W
label | Inspection: By - Grundfos Commissioning Engineer
checkpoint | 4.4 - Pump 4
label | Inspection Point: Quality Control Activity - Set pump 4 final pressure and flowrates
label | Acceptance Criteria - Pump 4 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
label | Verifying Document - Grundfos controller display/Commissioning sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - O/W
label | Inspection: By - Grundfos Commissioning Engineer
checkpoint | 4.5 - Pump 5
label | Inspection Point: Quality Control Activity - Set pump 5 final pressure and flowrates
label | Acceptance Criteria - Pump 5 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
label | Verifying Document - Grundfos controller display/Commissioning sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - O/W
label | Inspection: By - Grundfos Commissioning Engineer
checkpoint | 4.6 - Pump 6
label | Inspection Point: Quality Control Activity - Set pump 6 final pressure and flowrates
label | Acceptance Criteria - Pump 6 Delivery head and flowrate is as per specified values (153 Litres/sec combined)
label | Verifying Document - Grundfos controller display/Commissioning sheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - O/W
label | Inspection: By - Grundfos Commissioning Engineer
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Pumps 1 through 6
label | Inspection Point: Quality Control Activity - Full pumping duty is restored from Mt Grand to Wingatui Reservoir
label | Acceptance Criteria - Flow rates equal the specified design value (130 L/sec High flow)
label | Verifying Document - View on Grundfos Controller
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - W / H
label | Inspection: By - CR
holdpoint | HOLD POINT
checkpoint | 5.2 - Pumps 1 through 6
label | Inspection Point: Quality Control Activity - Pumping duty is restored to Stoney Knowe Reservoir
label | Acceptance Criteria - Flow rates equal the specified design value (70 L/sec High flow)
label | Verifying Document - View on Grundfos Controller
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual / Photograph
label | Inspection: Key - W / H
label | Inspection: By - CR
holdpoint | HOLD POINT
checklist | 561483-ITP-012.1 - Pipe Spool & Control Valve - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-012.1 - Wingatui Control Valve 1 final commissioning
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Pipe Spool Installation
label | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.1
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Control Valve 1 Installation
label | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.1
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Control Valve 2 & ancillaries
label | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.2
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.4 - Pumps 1 through 6 are installed and commissioned
label | Inspection Point: Quality Control Activity - Verify commissioning is complete via Grundfos
label | Acceptance Criteria - Completion of Commissioning
label | Verifying Document - Grundfos report
label | Frequency - Once
label | Inspection Type (Visual, other) - Inspection + Documentation
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Commission Control Valve 1
label | Inspection Point: Quality Control Activity - Set to achieve correct flow rate
label | Acceptance Criteria - 130 litres/sec achieved
label | Verifying Document - Commissioning Methodology/Claval Commissioning sheet
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Valve chamber will need to be assessed by Downer HS&E to determine as to whether is a confined space
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Record Value
label | Inspection Point: Quality Control Activity - At completion of valve commissioning
label | Acceptance Criteria - When consistent results are achieved
label | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Set Lock nut on pilot valve
label | Inspection Point: Quality Control Activity - At completion of valve commissioning
label | Acceptance Criteria - When consistent results are achieved
label | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-012.2 - Pipe Spool & Control Valve - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-012.2 - Wingatui Control Valve 2 final commissioning
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Pipe Spool Installation
label | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.1
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Control Valve 1 Installation
label | Inspection Point: Quality Control Activity - Installation completion. All bolts are tightened and torqued to their correct values
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.1
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Control Valve 2 & ancillaries
label | Inspection Point: Quality Control Activity - Valve assessment. All bolts are tightened and torqued to their correct values
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.2
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.4 - Pumps 1 through 6 are installed and commissioned
label | Inspection Point: Quality Control Activity - Verify commissioning is complete via Grundfos
label | Acceptance Criteria - Completion of Commissioning
label | Verifying Document - Grundfos report
label | Frequency - Once
label | Inspection Type (Visual, other) - Inspection + Documentation
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Commission Control Valve 2
label | Inspection Point: Quality Control Activity - Set to achieve correct flow rate
label | Acceptance Criteria - 130 litres/sec achieved
label | Verifying Document - Commissioning Methodology/Clavel Commissioning sheet
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Solenoid function test
label | Inspection Point: Quality Control Activity - Test function of solenoid shut-off
label | Acceptance Criteria - Shut off when reservoir is full
label | Verifying Document - Reservoir levels
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Valve chamber will need to be assessed by Downer HS&E to determine as to whether is a confined space
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Record Value
label | Inspection Point: Quality Control Activity - At completion of valve commissioning
label | Acceptance Criteria - When consistent results are achieved
label | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Record solenoid valve feedback values
label | Inspection Point: Quality Control Activity - At completion of valve commissioning
label | Acceptance Criteria - When consistent results are achieved
label | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checklist | 561483-ITP-012.3 - Pipe Spool & Control Valve - Inspection Test Plan | itp |  |  |  |  | 561483-ITP-012.3 - Stoney Knowe Control Valve final commissioning
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Control Pilot Valve Installation
label | Inspection Point: Quality Control Activity - Installation completion. All valves & Unions installed
label | Acceptance Criteria - Completion of ITP
label | Verifying Document - ITP-002.3
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Stoney Knowe Pipeline
label | Inspection Point: Quality Control Activity - Pressure testing
label | Acceptance Criteria - Pressure test pass
label | Verifying Document - ITP-004
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.3 - Stoney Knowe Pipeline
label | Inspection Point: Quality Control Activity - Pipeline disinfection
label | Acceptance Criteria - Pipeline disinfection pass
label | Verifying Document - ITP-005
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual + Inspection + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.4 - Pumps 1 through 6 are installed and commissioned
label | Inspection Point: Quality Control Activity - Verify commissioning is complete via Grundfos
label | Acceptance Criteria - Completion of Commissioning
label | Verifying Document - Grundfos report
label | Frequency - Once
label | Inspection Type (Visual, other) - Inspection + Documentation
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Commission Stoney Knowe Control Valve
label | Inspection Point: Quality Control Activity - Set to achieve correct flow rate
label | Acceptance Criteria - 70 litres/sec achieved
label | Verifying Document - Commissioning Methodology/Clavel Commissioning sheet
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Solenoid function test
label | Inspection Point: Quality Control Activity - Test function of solenoid shut-off
label | Acceptance Criteria - Shut off when reservoir is full
label | Verifying Document - Reservoir levels
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Photographs + document
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint-no-status | Note:
label | Valve chamber will need to be assessed by Downer HS&E to determine as to whether is a confined space
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Record Value
label | Inspection Point: Quality Control Activity - At completion of valve commissioning
label | Acceptance Criteria - When consistent results are achieved
label | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 5.2 - Record solenoid valve feedback values
label | Inspection Point: Quality Control Activity - At completion of valve commissioning
label | Acceptance Criteria - When consistent results are achieved
label | Verifying Document - Commissioning record sheet / Operation & Maintenance Manual
label | Frequency - once
label | Inspection Type (Visual, other) - Visual + Document + Photograph
label | Inspection: Key - I
label | Inspection: By - IP