## MEL07
CONQA:
Project Name: | Microsoft MEL07
EXTERNAL WATERPROOFING
Balcony
|  |  |  | Membrane to Balcony 07.02.203 (floor + 150mm upturn) | Enviro BLV + Enviro 700x
Top Roof Slab (above Roof Lift Lobby)
|  |  |  | PVC sheet to Kingspan Roof | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
|  |  |  | Upturn to Lift 3 Overrun Precast Concrete Wall (Ref MEL07- A-K-013-0 det 8) | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
|  |  |  | Ditto, Flashing installed at Lift Lid Interface | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
|  |  |  | Ditto, Restrained Angle Termination to Junction Between Slab and Wall (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
|  |  |  | Flashing Connecting PVC Membrane to the Gutter | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
|  |  |  | Membrane Strap to the Gutter | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
Lift Lids (Lift 1, 2 + 3)
|  |  |  | PVC sheet to Precast Concrete Roof Slab | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
|  |  |  | Overhob Termination to Perimeter | Fatrafol Accessories: (Fatranyl PVC Lined Steel Flashing , Fatranyl Internally Coated PVC Angle 40x40
Exposed Concrete Lift Shaft Wall Area
|  |  |  | Membrane to Lift 3 Exposed Concrete Lift shaft Wall ne 8.5m High (RL 68.525 - RL 60) | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
ROOF WATERPROOFING
Membrane to Kingspan Roof
Colos Roof
[5 empty] | PVC sheet to Kingspan Roof - Colos | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Membrane to Walkways - 650mm strip | Fatra Walkway System incl Fatrabond 9356 Contact Adhesive
[5 empty] | Ditto, upturn ne 600mm H to air shafts, mech gallery shafts and parapet walls | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and all Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Upstand Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | 2x Membrane Strap Termination to Box Gutter as per MEL07-A-K-010-0 Det 1 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Flashing Connecting PVC Membrane to the Gutter | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ridge Flashing incl Fatrafol Membrane | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Angle to Internal and External Corners to Upturn / Downturn (ne 600mm H) (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Detailing to Tapered Insulation (NB supply and installation of tapered cricket to be by others) | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Detailing to Roof Ladder Base | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
Air Shafts Roof
[5 empty] | PVC sheet to Kingspan Roof - Air Shafts | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Membrane Strap Termination to Perimeter as per MEL07- A-K-014-0 det 1 and 2 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Fatranyl PVC Flashing to perimeter edge | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
Mech Galleries Shafts Roof
[5 empty] | PVC sheet to Kingspan Roof - Mech Galleries Shafts | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Membrane Strap Termination to Perimeter as per MEL07- A-K-014-0 det 1 and 2 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Fatranyl PVC Flashing to perimeter edge | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
Admin Roof
[5 empty] | PVC sheet to Kingspan Roof - Admin Roof | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Ditto, upturn ne 200mm H to Colos side walls | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Ditto, upturn ne 500mm H to lift 1-2 lids | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and adjacent Upstand Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Upstand Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | 2x Membrane Strap Termination to Box Gutter as per MEL07-A-K-012-0 Det 4 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Flashing Connecting PVC Membrane to the Gutter | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ridge Flashing / Roll End Strip incl Fatrafoil Membrane | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Angle to Internal and External Corners to Upturn / Downturn (200mm H generally; 500mm H to lifts 1-2 lid) (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
Admin L2 Western Canopy
[5 empty] | PVC sheet to Kingspan Roof - Admin L2 Western Canopy | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Ditto, upturn ne 200mm H to Office / Corridor side walls | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and adjacent Upstand Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Upstand Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | 2x Membrane Strap Termination to Box Gutter as per MEL07-A-K-012-0 Det 4 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Flashing Connecting PVC Membrane to the Gutter | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ridge Flashing / Roll End Strip incl Fatrafoil Membrane | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Angle to Internal and External Corners to Upturn / Downturn (200mm H) incl door subsill (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
Admin L2 Eastern Canopy
[5 empty] | PVC sheet to Kingspan Roof - Admin L2 Eastern Canopy (NB No membrane allowances to plant deck) | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Ditto, upturn ne 200mm H to Office / Corridor side walls | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and adjacent Upstand Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Upstand Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | 2x Membrane Strap Termination to Box Gutter as per MEL07-A-K-012-0 Det 4 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Flashing Connecting PVC Membrane to the Gutter | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ridge Flashing / Roll End Strip incl Fatrafoil Membrane | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Angle to Internal and External Corners to Upturn / Downturn (200mm H) incl door subsill (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
Pipe Penetrations (Round and Square)
Admin L1 Eastern and Western Canopies
[5 empty] | PVC sheet to Kingspan Roof - Admin L1 Eastern and Western Canopies | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | 2x Membrane Strap Termination to Box Gutter assumed same detail as MEL07-A-K-012-0 Det 4 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Flashing Connecting PVC Membrane to the Gutter | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | 2x Membrane Strap Termination to Box Gutter assumed same detail as MEL07-A-K-012-0 Det 4 | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and adjacent Upstand Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Upstand Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing adjacent to Fascia / Kingspan Verge | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ditto, Membrane Strap to Termination Flashing | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
Staircase Roofs :[6 Nos]
[5 empty] | PVC sheet to Kingspan Roof - Staircase Roofs :[6 Nos] | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Membrane Strap Termination to Perimeter / Gutter - TBC detail | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Fatranyl PVC Flashing to Perimeter / Gutter - TBC detail | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Angle to Internal Corners to Upturn / Downturn (200mm H) (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
Small Roofs next to Staircase :[4 Nos]
[5 empty] | PVC sheet to Kingspan Roof - Small Roofs next to Staircase :[4 Nos] | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Ditto, upturn ne 200mm H to walls | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and adjacent Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Membrane Strap Termination to Perimeter / Gutter - TBC detail | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
[5 empty] | Fatranyl PVC Flashing to Perimeter / Gutter - TBC detail | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing adjacent to Fascia | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ditto, Membrane Strap to Termination Flashing | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
SCV :[4 Nos]
[5 empty] | PVC sheet to Kingspan Roof - SCV :[4 Nos] | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
[5 empty] | Ditto, upturn ne 200mm H to walls | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
[5 empty] | Restrained Angle Termination to Junction Between King Span Roof and adjacent Walls (Fatra Ancillary) | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing to Walls | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Termination Flashing adjacent to Fascia | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
[5 empty] | Ditto, Membrane Strap to Termination Flashing | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing

## ITPs Checklists - Rev 08
type | name | values
checklist-flat | Delivery Checklist
checkpoint | Check correct materials are received at least 24 hours prior to commencing work on site
text | Batch No.
label | Specification / Standard: AS4654.1-2012; Manufacturer’s Technical Data Sheet
label | Attach Delivery Docket
checklist-flat | Enviro HP1200
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+800TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Top Coat - Mix and Apply Enviro 800TC with brush or new roller (spray application optional) Re-apply as required or determined by the Specification
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+850TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Top Coat - Mix and Apply Enviro 850TC with brush or new roller (spray application optional) Re-apply as required or determined by the Specification
label | Attach Photo
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+900+850TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro 700X using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro 700X using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 200P
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro 200P using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro 200P using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Flex 2 Part
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro Flex 2 Part using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro Flex 2 Part using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Epoxy RC / Ultra Tuff
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Cutting - Make sure that adjoining ends of intersecting waterstop segments are cut extremely straight
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Epoxy Application (1st coat) - Apply Enviro Epoxy RC / Enviro Ultra Tuff with a brush, roller or spray
label | (If no aggregate is required, 1st coat of epoxy can be dilluted with 10% xylene
label | If aggregate is required, broadcast at correct coverage while 1st coat has been applied and is in it's wet state prior to curing
checkpoint | Epoxy Application (2nd Coat) - Apply Enviro Epoxy RC / Enviro Ultra Tuff with a brush, roller or spray
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Hydrostatic 1
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS4654.2-2012, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Primer application - Lightly Spray areas to receive Hydrostatic 1
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Mix Enviro Hydrostatic 1 thoroughly using a mechanical mixer. Apply first coat of Enviro Hydrostatic 1 by brush or roller Use Enviro Joint Band in floor-wall junctions and general movement joints
checkpoint | Membrane Application (2nd coat) - Mix Enviro Hydrostatic 1 thoroughly using a mechanical mixer. Apply second coat of Enviro Hydrostatic 1 by brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Clad
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS4654.2-2012, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Primer Application - Pending Substrate Condition, Apply Enviro Prime WB using a brush or roller
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Mix and Apply Enviro Clad as a first coat to the thicknesses prescribed by the specifications
checkpoint | Membrane Application (2nd coat) - Mix and Apply Enviro Clad as a second coat to the thicknesses prescribed by the specifications
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X + 200P
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Apply primer (Enviro Shield/Enviro prime P2 or Enviro Epoxy B-LV) by brush/roller
label | Attach Photo
checkpoint | Caulking. Apply Enviro Flex FC junction fillets (where applicable)
label | Attach Photo
checkpoint | Mixing and Application. Mix Enviro 700X thoroughtly using mechanical mixer. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT.
label | Attach Photo
checkpoint | Testing. Flood test when applicable.
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder.
checkpoint | Check Screed (moisture test if required).
checkpoint | Apply primer (Enviro Shield/Enviro Shield or Prime WB by brush/roller
label | Attach Photo
checkpoint | Apply first coat of Enviro 200P Ultra with a brush or roller.
label | Attach Photo
checkpoint | Apply second coat of Enviro 200P Ultra with a brush or roller. Achieve 0.8mm WFT and 1.0mm DFT.
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro CSH
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate. (moisture test if oncrete not fully cured) and prepare surface using a scraper or grinder and vacuum or sweep residual debris.
checkpoint | Check for cracks/defect in concrete.
label | Attach Photo
checkpoint | Perform mechanical profiling / shot blasting to concrete
label | Visual
checkpoint | Spray Enviro CSH concrete surface hardener and moisture barrier, first application
label | Visual
checkpoint | Spray Enviro CSH concrete surface hardener and moisture barrier, second application
label | Visual
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
label | Attach Photo.
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X + 800TC
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X.
label | Attach Photo
checkpoint | Priming. Apply primer (Enviro Epoxy B-LV / Enviro Prime P2 / Enviro Shield) using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X.
label | Attach Photo
checkpoint | Mixing and Application. Enviro 700X should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT. (2 coats).
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed Enviro 700X to ensure the membrane is not damaged.
checkpoint | Top Coat. Enviro 800 TC should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat.
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Shield / Prime P2 / Epoxy B-LV
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Screed (moisture test if required, Enviro Shield is moisture tolerant.)
label | Attach Photo
checkpoint | Apply first coat of Enviro Shield with a brush or roller.
label | Visual
checkpoint | Apply second coat of Enviro Shield with a brush or roller.
label | Attach photo
checkpoint | Protection board. Install Elmich Versidrain 8 Geo. Applicable to planters only
label | Attach photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+Shield
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) and prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Check label on drum(s) to ensure correct material is being used
checkpoint | Apply primer (Enviro prime P2 or Enviro Epoxy B-LV) by brush/roller
label | Attach Photo
checkpoint | Caulking/ Joints. Apply bondbreaker at junctions
label | Attach Photo
checkpoint | Mixing. Mix HP 1200. Mixing by way of 1:1 mix ratio (by volume) in heated plural component spray equipment such as Graco E-10 or EXP-2. Both low and high pressure spray equipment can be used for the application of Enviro HP1200.
label | Attach Photo
checkpoint | Application. Spray on Enviro HP1200. Achieve 1.5mm DFT.
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over if applicable.
checkpoint | Check Screed (areas where applicable) moisture test if required, Enviro Shield is moisture tolerant.
checkpoint | Apply first coat of Enviro Shield with a brush or roller.
label | Attach Photo
checkpoint | Apply second coat of Enviro Shield with a brush or roller.
label | label
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+900
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo of substrate
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo.
checkpoint | Moisture Content Test.
label | Attach Photo of moiture reading or enter moisture reading in comment section
checkpoint | Check label on drum to ensure correct material is being used
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Visual inspection, ensure adequately cured.
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
checkpoint | Mixing. Mix HP 1200. Mixing by way of 1:1 mix ratio (by volume) in heated plural component spray equipment such as Graco E-10 or EXP-2. Both low and high pressure spray equipment can be used for the application of Enviro HP1200.
checkpoint | Apply Enviro HP1200 using a spray gun. Achieve 1.5mm DFT.
label | Attach photo.
checkpoint | Curing
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | DFT Testing
label | Attach Photo. Enter DFT reading on comment section.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 200P Secondary
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Screed (moisture test if required).
label | Attach Photo
checkpoint | Apply Primer. Enviro Shield or Enviro Prime WB.
label | Visual
checkpoint | Apply first coat of Enviro 200P with a brush or roller.
label | Visual
checkpoint | Apply first coat of Enviro 200P with a brush or roller. Achieve 0.8mm WFT and 1.0mm DFT.
label | Attach Photo of WFT reading. Enter WFT reading on comment section.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Patching and Handover to Bondek
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check membrane - Check for damages to membrane.
label | Attach Photo of damages
checkpoint | Patching. Apply Enviro HP1200 using a spray gun. Achieve 1.5mm DFT. Or Apply Enviro 700X.
label | Attach photo of patching.
checkpoint | Lapping to blockwork prior to bondek being laid. Apply Enviro HP1200 using a spray gun. Achieve 1.5mm DFT. Or Apply Enviro 700X.
label | Attach Photo of lap to blockwork.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist | Pre-Inspection Checklist
section | General Area
checkpoint | Has the builder provided a marked up plan on each area to be waterproofed?
label | Marked up plan has to be numbered if more than one area at a time is to be completed
checkpoint | Has the concrete been cured for 28 days, date of pour to be provided?
checkpoint | Has concrete moisture test been carried out and the result was provided for the locations on a marked up plan?
label | The moisture level should be around 7%
checkpoint | Is the concrete finished to an acceptable steel trowel class finish?
checkpoint | Have all tape, steel wire, nails, plywood or formwork, bracing, dyna bolt and/or steel brackets been removed and patched?
checkpoint | Is there any cracking in the substrate? If yes, an engineer’s report will need to be provided or the builder must sign off prior to commencement of works
checkpoint | Has any chemicals been used in the concrete process that may affect the membrane adhesion?
section | Hobbs
checkpoint | Spalling
checkpoint | Laitance
checkpoint | Boney Concrete
checkpoint | Prework was under standard
checkpoint | Form Ply Ridges
section | Wall
checkpoint | Spalling
checkpoint | Laitance
checkpoint | Boney Concrete
checkpoint | Prework was under standard
checkpoint | Form Ply Ridges
section | Floor
checkpoint | Spalling
checkpoint | Laitance
checkpoint | Boney Concrete
checkpoint | Prework was under standard
checkpoint | Form Ply Ridges
section | Access
checkpoint | Puddle flanges used or installed must be recessed flush to the top of the concrete surface
holdpoint | Builder to check correct falls to drains
checkpoint | Patching to be completed 3 days prior to waterproofing proposed start date and/or second inspection required
checkpoint | Adequate spacing to seal around each one for Cast in items (conduit, water pipes etc). No flexible conduits permitted
checkpoint | Would recommend using Enviro mortar 45 for all pin holes, overfilled then stoned back when dry
checklist-flat | Enviro HP1200 + 700X
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply primer (Enviro Epoxy B-LV / Enviro Prime P2 / Enviro Shield) using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X
label | Attach Photo
checkpoint | Mixing and Application. HP1200 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT. (2 coats)
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed Enviro 700X to ensure the membrane is not damaged
checkpoint | Top Coat. Enviro 700X should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro P2 + HP1200
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply P2 using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X
label | Attach Photo
checkpoint | Mixing and Application. HP1200 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed waterproofing system to ensure the membrane is not damaged
checkpoint | Top Coat. should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BSM
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. Blinding sound and level, Trowel finished, no voids or leftover formwork or sharp edges. NCR any unacceptable items
label | Attach Photo
checkpoint | Free substrate of Dirt and Debris where required.
label | Attach Photo
checkpoint | Reinspect substrate. Polyseal applicator - Area clean and dry, ready to instal sheet membrane
label | Attach Photo
checkpoint | Lay BSM - Overlap as per manufacturers instructions, stragger cut joins where possible, detail strip to be installed at cut joins.
label | Attach Photo
checkpoint | Apply Hp 1600 to Dwall BEFORE bars ensure lap down onto BSM
label | Attach Photo
checkpoint | Following bar install, bar to be detailed with flex fc, 700x to be applied with a 50mm return on the bar, bars to be epoxied in by others (generous amount of epoxy required)
label | Attach Photo
checkpoint | epoxy incapulation to pipe penos, Pile cap to be incapsulated with epoxy grout 50mm finished height
label | Attach Photo
checkpoint | InspecInspection of Membrane - Pre Reo (Polyseal & Client & Enviro systems )tion of Membrane, All Elements to be reinspected. Corner terminations, overlaps, pile heads
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BSM + Liquid Membrane / Epoxy Termination
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. Blinding sound and level, Trowel finished, no voids or leftover formwork or sharp edges. NCR any unacceptable items
label | Attach Photo
checkpoint | Free substrate of Dirt and Debris where required.
label | Attach Photo
checkpoint | Reinspect substrate. Polyseal applicator - Area clean and dry, ready to instal sheet membrane
label | Attach Photo
checkpoint | Lay BSM - Overlap as per manufacturers instructions, stragger cut joins where possible, detail strip to be installed at cut joins.
label | Attach Photo
checkpoint | Apply Hp 1600 to Dwall BEFORE bars ensure lap down onto BSM
label | Attach Photo
checkpoint | Following bar install, bar to be detailed with flex fc, 700x to be applied with a 50mm return on the bar, bars to be epoxied in by others (generous amount of epoxy required)
label | Attach Photo
checkpoint | epoxy incapulation to pipe penos, Pile cap to be incapsulated with epoxy grout 50mm finished height
label | Attach Photo
checkpoint | InspecInspection of Membrane - Pre Reo (Polyseal & Client & Enviro systems )tion of Membrane, All Elements to be reinspected. Corner terminations, overlaps, pile heads
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1600
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1600 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV + HP1200
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply BLV using a brush or roller. Allow primer to fully cure before proceeding with the application of HP1200
label | Attach Photo
checkpoint | Mixing and Application. HP1200 should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed waterproofing system to ensure the membrane is not damaged
checkpoint | Top Coat. should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
Checklist-flat | Combiflex
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Measure and Temporarily fix ElastoFlex or Combiflex
label | Attach Photo
checkpoint | Install ElastoFlex or Combiflex to Movement Joint locations
label | Attach Photo
checkpoint | Remove Push Pins and Patch holes
label | Attach Photo
checkpoint | Inspect Length of Combiflex material
label | Attach Photo
checkpoint | Inspect Length of epoxy anchor
label | Attach Photo
checkpoint | Carry ouf sprinkler testing
label | Attach Photo
checkpoint | Check Substrate & Repair defects
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro HP1200+900+800TC
checkpoint | Relevant Australian Standards Checked
label | AS4654.2-2012; Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Shield + 700X
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate/Work Area, Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Apply primer (Enviro Shield/Enviro prime P2 or Enviro Epoxy B-LV) by brush/roller
label | Attach Photo
checkpoint | Caulking. Apply Enviro Flex FC junction fillets (where applicable)
label | Attach Photo
checkpoint | Mixing and Application. Mix Enviro 700X thoroughtly using mechanical mixer. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT.
label | Attach Photo
checkpoint | Carry out Dry Film Thickness test & Holiday Testing & Pull Off Test, Repair any defects found using patch and repair method specified in procedures.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist | Enviro Epoxy Screed / Rapid Screed
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Mixing - using horizontal forced action mixers or screed pumps, mix 20kg Enviro Rapid Screed with 100kg Gravel Mix 0 – 4mm; gradually add 9.5 – 11L of clean water (mixing water may vary depending on the moisture content of the Gravel Mix). Mixing time is 2 minutes.
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
checkpoint | Check Substrate - The surface must be clean, dry and free from all loose particles
checkpoint | Apply Screeding to Substrate in accordance with documentations and desired falls.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
Hold point | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X + 250NS
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X.
label | Attach Photo
checkpoint | Priming. Apply primer (Enviro Epoxy B-LV / Enviro Prime P2 / Enviro Shield) using a brush or roller. Allow primer to fully cure before proceeding with the application of Enviro 700X.
label | Attach Photo
checkpoint | Mixing and Application. Enviro 700X should be thoroughly mixed with a mechanical mixer at low speed (less than 400 RPM) prior to application. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT. (2 coats).
label | Attach Photo
checkpoint | Curing. Allow product to cure for 12 hours before recoating. Care should be taken when walking over newly installed Enviro 700X to ensure the membrane is not damaged.
checkpoint | Top Coat. Enviro 250NS should be thoroughly mixed using a mechanical mixer at low speed prior to application. Do not mix in air. APPLICATION: In exposed areas, do not apply if rain is expected within 6hours. Enviro 250 NS can be applied using a roller (6mmnap recommended). Apply 2 coats of Enviro 250 NS (each coat at a wet film thickness of 0.6mm), to achieve a 0.6mm Dry Film Thickness (DFT). Do not apply as one heavy coat. Preferably, apply at 90° to the direction of the previous coat. Ensure that all areas receive a sufficient coating thickness and are free of all defects such as pinholes. Allow each coat to sufficiently dry before proceeding to the next coat. Thicker coats will take longer to dry.
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Hydrotite (waterstop) including Leakmaster
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Hydrophilic expanding waterstops shall be placed at the joints in the concrete at the locations shown on the drawings in accordance with the equirement of the specification. Waterstops where shown on drawings shall be Enviro Hydrotite Hydrophilic Waterstops.
label | Attach Photo
checkpoint | The waterstop shall consist of non-expansive black chloroprene rubber, co-extruded with a blue hydrophilic rubber, which is capable of swelling by approximately eight times by volume.
label | Attach Photo
checkpoint | The waterstop shall be treated with a delay coating to prevent premature expansion and be able to change colour upon expansion which acts as a visual alert that the waterstop has started to expand. The waterstop is to be installed strictly in accordance with the manufacturer’s recommendations
label | Attach Photo
checkpoint | LEAKMASTER Leakmaster is a water swelling gun grade waterstop with excellent and unique physical properties. It can he used in places where the standard extruded profiles are not suitable in areas such as rough concrete surfaces or as a back-up to these profiles in complex junctions.
label | Attach Photo
checkpoint | Testing. Carry out Testing . Repair pinholes and imperfections. Areas marked indicate the location of Test.
label | Attach Photo
checkpoint | Final signoff and handover. Visually inspect and ensure adequately cured. Check for any pinholes and bubbles. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV+900+800TC
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply BLV using a brush or roller. Allow primer to fully cure before proceeding with the application of HP1200
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro 700X + Enviro Hydrotite
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate - The surface must be clean, dry and free from all loose particles
label | Attach Photo
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Apply Enviro 700X using a brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Membrane Application (2nd coat) - Apply Enviro 700X using a brush or roller
checkpoint | Flood Testing (if required)
label | Attach Photo
checkpoint | Hydrophilic expanding waterstops shall be placed at the joints in the concrete at the locations shown on the drawings in accordance with the equirement of the specification. Waterstops where shown on drawings shall be Enviro Hydrotite Hydrophilic Waterstops.
label | Attach Photo
checkpoint | The waterstop shall consist of non-expansive black chloroprene rubber, co-extruded with a blue hydrophilic rubber, which is capable of swelling by approximately eight times by volume.
label | Attach Photo
checkpoint | The waterstop shall be treated with a delay coating to prevent premature expansion and be able to change colour upon expansion which acts as a visual alert that the waterstop has started to expand. The waterstop is to be installed strictly in accordance with the manufacturer’s recommendations
label | Attach Photo
checkpoint | LEAKMASTER Leakmaster is a water swelling gun grade waterstop with excellent and unique physical properties. It can he used in places where the standard extruded profiles are not suitable in areas such as rough concrete surfaces or as a back-up to these profiles in complex junctions.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Sika Sarnafil
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | Apply Sarnacol. Record atmospheric & substrate conditions & notate in QA Documents. Humidity <85%, Delta >3⁰, Air Temp 5-40⁰.
label | Attach Photo
checkpoint | Apply Sarnafil. Overlap as per manufacturers instructions,75mm, stagger cut joins where possible, detail strip to be installed at cut joins.
label | Attach Photo
checkpoint | Weld all joins, Ensure PPE, Respirator, fire extuinguisher within vicinity. Weld overlap in one direction to avoid ribbons --Ensure 75mm overlap
label | Attach Photo
checkpoint | Install Pressure Bar, Install as instructed by builder to finish termination height. Install sealant is placed above pressure bar. Every second hole on pressure bar to be drilled. 1 hole overlap on edge of termination bar
label | Attach Photo
checkpoint | Check all welds with spatula/screwdriver for lifts. Use blunt pointed object to ensure all welds correctly sealed. Any lifts, circle to return to weld
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any potential defects. Sign-off from builder.
checkpoint | Inspection of welds. All Elements to be inspected. Corner terminations, overlaps, lifts, burns, joins, and pressure seal
checkpoint | Test Welds. All Elements to be reinspected. Corner terminations, overlaps, pile heads. ensure all action items from previous inspection have been resolved.
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | SikaRoof® MTC-12 UV (SIKA Sikalastic 100 EP + 488 +622)
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check Substrate Check for cracks/defect in concrete. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns).
label | Attach Photo
checkpoint | Prepare Substrate. (moisture test if required) prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris.
label | Attach Photo
checkpoint | PRIMER: 2:1 mix ratio (Part A: Part B) mixed for a minimum of 2 minutes - Prior the application of SikaRoof® MTC-12 UV the priming coat if used must have cured tack-free.. For the Waiting Time / Overcoating please refer to the PDS of the appropriate primer. Damageable areas (handrails etc.) have to be protected with tape or plastic wrapping. Please note, always begin with details prior to the installation of the horizontal surface
label | Attach Photo
checkpoint | 1. Apply first coat of Sikalastic®-488. Please refer to the Sikalastic®-488 product data sheet for application rates and drying times; 2 coats will be required to acheive the DFT of 1.2mm
label | Attach Photo
checkpoint | 2. Apply the top coat of Sikalastic®-622 Excel Top PLUS. If a non-slip finish is required, two coats will need be installed with the non-slip finish being broadcast into the first coat of Sikalastic®-622 Excel Top PLUS. Once first coat is cured, the coating should be broomed/vacummed of excess material and the subsequent top coat applied within 24 hours.
label | Attach Photo
checkpoint | First signoff. Visually inspect and ensure adequately cured. Check for any potential defects. Sign-off from builder.
checkpoint | Inspection of welds. All Elements to be inspected. Corner terminations, overlaps, lifts, burns, joins, and pressure seal
checkpoint | Test Welds. All Elements to be reinspected. Corner terminations, overlaps, pile heads. ensure all action items from previous inspection have been resolved.
label | Attach Photo
checkpoint | Final signoff. Visually inspect and ensure adequately cured. Sign-off from builder and hand-over
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV + Enviro 700x
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply BLV using a brush or roller. Allow primer to fully cure before proceeding with the application of 700x
label | Attach Photo
checkpoint | Caulking. Apply Enviro Flex FC junction fillets (where applicable)
label | Attach Photo
checkpoint | Mixing and Application. Mix Enviro 700X thoroughtly using mechanical mixer. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT.
label | Attach Photo
checkpoint | Carry out Dry Film Thickness test & Holiday Testing & Pull Off Test, Repair any defects found using patch and repair method specified in procedures.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV + Enviro 700x + Enviro 800TC
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Priming. Apply BLV using a brush or roller. Allow primer to fully cure before proceeding with the application of 700X
label | Attach Photo
checkpoint | Caulking. Apply Enviro Flex FC junction fillets (where applicable)
label | Attach Photo
checkpoint | Mixing and Application. Mix Enviro 700X thoroughtly using mechanical mixer. Apply Enviro 700X using brush/roller achieving 1.6mm WFT / 1.5mm DFT.
label | Attach Photo
checkpoint | Carry out Dry Film Thickness test & Holiday Testing & Pull Off Test, Repair any defects found using patch and repair method specified in procedures.
label | Attach Photo
checkpoint | Top Coat. Enviro 800 TC should be thoroughly mixed using a mechanical mixer at low speed prior to application.Add Part B to Part A and mix to a uniform colour and consistency for a minimum of 3 minutes. Allow to react for 10 minutes before application. Allow to react for 15 minutes when thinning with Enviro Thinner No.8 before application. Do not apply in damp or wet conditions. Allow each coat to sufficiently dry before proceeding to the next coat.
label | Attach Photo
checkpoint | Testing. Carry out Spark Testing and adhesion tests. Repair pinholes and imperfections. Areas marked indicate location of Test.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV + HP1200 + 900 + 800TC
checkpoint | Relevant Australian Standards Checked
text | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
label | Attach Photo
checkpoint | Substrate Preparation and Caulking. Prepare surface to accept primer using a scraper or grinder and vacuum or sweep residual debris. Remove all sharp edges including screws, nails and concrete/mortar projections. Apply a suitable and approved joint sealant such as Enviro Flex Pro or Enviro Flex FC to all joints and connecting building parts prior to the application of Enviro 700X
label | Attach Photo
checkpoint | Priming. Apply BLV using a brush or roller. Allow primer to fully cure before proceeding with the application of HP1200
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Mixing
checkpoint | Apply Enviro HP1200 using a spray gun
checkpoint | Curing
checkpoint | Pin Hole Detection Test of area with holiday tester Pull Off Adhesion Testing shall not be less than 1MPa. Thickness shall not be less than 1.5mm
label | Attach Photo
checkpoint | Wear Coat - Mix and Apply Enviro 900 with brush or new roller (spray application optional) Broadcast aggregate uniformly to the wet Enviro 900 within the timeframes specified
label | Attach Photo
checkpoint | Top Coat Mix and Apply Enviro 850 with brush or new roller (second coat optional pending specification)
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro BLV + Epoxy Ultra Tuff
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Moisture Content Test
label | Attach Photo
checkpoint | Cutting - Make sure that adjoining ends of intersecting waterstop segments are cut extremely straight
label | Attach Photo
checkpoint | Apply primer using a brush or roller
label | Attach Photo
checkpoint | Epoxy Application (1st coat) - Apply Enviro Ultra Tuff with a brush, roller or spray
label | (If no aggregate is required, 1st coat of epoxy can be dilluted with 10% xylene
label | If aggregate is required, broadcast at correct coverage while 1st coat has been applied and is in it's wet state prior to curing
checkpoint | Epoxy Application (2nd Coat) - Apply Enviro Ultra Tuff with a brush, roller or spray
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured.
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Fatrafol 807V PVC Sheet incl Fatrabond 1215 MCPU Adhesive
checkpoint | Relevant Australian Standards Checked
label | Specification / Standard: AS4654.1-2012; AS3740 - 2010, Manufacturer’s Technical Data Sheet
checkpoint | Check substrate. The surface must be clean, dry and free from all loose particles including dust, laitance, grease, coatings, curing compounds and any other foreign matter. Check critical areas (puddle flanges, penetrations, expansion joints, rebates/setdowns)
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | moisture test if required
label | Attach Photo
checkpoint | Application of 1215 Adhesion Adhesive should be applied to sub deck surface, allowed to dry (2-6 minutes or until dry with touch) then parts mated under pressure. Bonds should be made as soon as practically possible. If adhesive is left to dry for over 15 minutes, parts should be recoated. Surface should be clean off any dust, dirt or debris. Pour and roller/squeegee apply to entire surface area (porous surfaces may need a second coat). Roll Fatra 807/807v fleece back membrane over the covered area. Any air pockets should be rolled out from the PVC membrane should this occur using a heavy duty roller. Consolidate substrates to prevent any air entrapment.
label | Attach Photo
checkpoint | Application: The laying of Fatrafol 807v can be made by specialised and for this purpose trained firms at the constructions. The membrane is applied under conformity with fundamentals being set and described in a Construction and Technologic Instruction of the producer, being valid in the time of waterproofing.
label | Attach Photo
checkpoint | The membrane must be adhered to a stable part of the substrate/coating by sticking (polyurethane adhesives).
label | Attach Photo
checkpoint | The membrane is mutually jointed by welding of hot air. The laying and jointing can be carried out in temperatures up to -5 degrees celsius.
label | Attach Photo
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Fatrafol 810V PVC Membrane incl Fatrabond 9356 Contact Adhesive
SECTION | DETAILS
Checkpoint | Attach any relevant documents or photos
text | ITP No.
text | Revision No. & Date
text | Prepared By
text | Reviewed By
text | Approved By
SECTION | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
Checkpoint | FatraBond Adhesive
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor and Site Engineer/Foreman sign off
SECTION | PRE COMMENCEMENT- EACH LOCATION
Checkpoint | Samples Submitted
Label | Submit samples for approval as per Specific Material Requirements.
Label | Sample Approval Ref.
Checkpoint | First Of Type Inspection
Label | First of type of inspection conducted prior to commencment of works taking place.
Label | Document Ref.
HOLDPOINT | Sample Submission / First of type inspection - Site Engineer Sign Off
SECTION | APPLICATION - EACH LOCATION
Checkpoint | FatraBond Adhesive
Label | Apply adhesive consistently over required area using squeegee/rollers
Label | Adhesive is applied consistently and evenly across the surface to achieve correct adhesion
Label | Adhesive does not spill onto membrane, weldable laps or surrounding areas that can potentially contaminate welds
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Install Fatrafol PVC Membrane
Label | Install Fatrafol to coincide with the falls of the roof
Label | Ensure the membrane laps run with the fall of the roof to minimise negative laps on the roof
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Builders Application Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
SECTION | DETAILING - EACH LOCATION
Checkpoint | Hot Air Fusion Welding of PVC membrane.
Label | Hot air fusion weld overlaps.
Label | Achieve a minimum 40mm wide weld width on all hot air seam welds to achieve sufficient weld strength
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Installation of PVC Coated Angles
Label | Fixing Fatranyl PVC coated termination angles using relevant fixings
Label | All termination metals are aligned correctly and are not disjointed or protruding
Label | Fixings centres do not exceed 200mm centres
Label | PVC coated termination angles are installed with a minimum 2mm gap between each angle to allow for structural movement and expansion
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Builders Detailing Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
Section | QA TESTING - EACH LOCATION
Checkpoint | Inspection
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
Label | Records - time stamped photograph
select | Inspection | Surveillance point, Witness point
checklist-flat | Fatrafol Accessories: (Fatranyl Internally / Externally Coated PVC Angle 40x40 / Fatranyl PVC Termination K-Flashing incl polyurethane sealant / Fatranyl PVC Lined Steel Flashing)
SECTION | DETAILS
Checkpoint | Attach any relevant documents or photos
text | ITP No.
text | Revision No. & Date
text | Prepared By
text | Reviewed By
text | Approved By
SECTION | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
Checkpoint | FatraBond Adhesive
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor and Site Engineer/Foreman sign off
SECTION | PRE COMMENCEMENT- EACH LOCATION
Checkpoint | Samples Submitted
Label | Submit samples for approval as per Specific Material Requirements.
Label | Sample Approval Ref.
Checkpoint | First Of Type Inspection
Label | First of type of inspection conducted prior to commencment of works taking place.
Label | Document Ref.
HOLDPOINT | Sample Submission / First of type inspection - Site Engineer Sign Off
SECTION | APPLICATION - EACH LOCATION
Checkpoint | FatraBond Adhesive
Label | Apply adhesive consistently over required area using squeegee/rollers
Label | Adhesive is applied consistently and evenly across the surface to achieve correct adhesion
Label | Adhesive does not spill onto membrane, weldable laps or surrounding areas that can potentially contaminate welds
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Install Fatrafol PVC Membrane
Label | Install Fatrafol to coincide with the falls of the roof
Label | Ensure the membrane laps run with the fall of the roof to minimise negative laps on the roof
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Builders Application Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
SECTION | DETAILING - EACH LOCATION
Checkpoint | Hot Air Fusion Welding of PVC membrane.
Label | Hot air fusion weld overlaps.
Label | Achieve a minimum 40mm wide weld width on all hot air seam welds to achieve sufficient weld strength
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Installation of PVC Coated Angles
Label | Fixing Fatranyl PVC coated termination angles using relevant fixings
Label | All termination metals are aligned correctly and are not disjointed or protruding
Label | Fixings centres do not exceed 200mm centres
Label | PVC coated termination angles are installed with a minimum 2mm gap between each angle to allow for structural movement and expansion
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Builders Detailing Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
Section | QA TESTING - EACH LOCATION
Checkpoint | Inspection
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
Label | Records - time stamped photograph
select | Inspection | Surveillance point, Witness point
checklist-flat | Fatrafol 804 Detail - 150mm strip / Fatrafol 810V PVC Membrane 400mm strip over galvanized metal flashing
SECTION | DETAILS
Checkpoint | Attach any relevant documents or photos
text | ITP No.
text | Revision No. & Date
text | Prepared By
text | Reviewed By
text | Approved By
SECTION | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
Checkpoint | FatraBond Adhesive
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor and Site Engineer/Foreman sign off
SECTION | PRE COMMENCEMENT- EACH LOCATION
Checkpoint | Samples Submitted
Label | Submit samples for approval as per Specific Material Requirements.
Label | Sample Approval Ref.
Checkpoint | First Of Type Inspection
Label | First of type of inspection conducted prior to commencment of works taking place.
Label | Document Ref.
HOLDPOINT | Sample Submission / First of type inspection - Site Engineer Sign Off
SECTION | APPLICATION - EACH LOCATION
Checkpoint | FatraBond Adhesive
Label | Apply adhesive consistently over required area using squeegee/rollers
Label | Adhesive is applied consistently and evenly across the surface to achieve correct adhesion
Label | Adhesive does not spill onto membrane, weldable laps or surrounding areas that can potentially contaminate welds
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Install Fatrafol PVC Membrane
Label | Install Fatrafol to coincide with the falls of the roof
Label | Ensure the membrane laps run with the fall of the roof to minimise negative laps on the roof
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Builders Application Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
SECTION | DETAILING - EACH LOCATION
Checkpoint | Hot Air Fusion Welding of PVC membrane.
Label | Hot air fusion weld overlaps.
Label | Achieve a minimum 40mm wide weld width on all hot air seam welds to achieve sufficient weld strength
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Installation of PVC Coated Angles
Label | Fixing Fatranyl PVC coated termination angles using relevant fixings
Label | All termination metals are aligned correctly and are not disjointed or protruding
Label | Fixings centres do not exceed 200mm centres
Label | PVC coated termination angles are installed with a minimum 2mm gap between each angle to allow for structural movement and expansion
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Builders Detailing Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
Section | QA TESTING - EACH LOCATION
Checkpoint | Inspection
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
Label | Records - time stamped photograph
select | Inspection | Surveillance point, Witness point
checklist-flat | Fatra Walkway System incl Fatrabond 9356 Contact Adhesive
SECTION | DETAILS
Checkpoint | Attach any relevant documents or photos
text | ITP No.
text | Revision No. & Date
text | Prepared By
text | Reviewed By
text | Approved By
SECTION | BATCH DETAIL NUMBER OF PRODUCTS - EACH DELIVERY
Checkpoint | FatraBond Adhesive
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor and Site Engineer/Foreman sign off
SECTION | PRE COMMENCEMENT- EACH LOCATION
Checkpoint | Samples Submitted
Label | Submit samples for approval as per Specific Material Requirements.
Label | Sample Approval Ref.
Checkpoint | First Of Type Inspection
Label | First of type of inspection conducted prior to commencment of works taking place.
Label | Document Ref.
HOLDPOINT | Sample Submission / First of type inspection - Site Engineer Sign Off
SECTION | APPLICATION - EACH LOCATION
Checkpoint | FatraBond Adhesive
Label | Apply adhesive consistently over required area using squeegee/rollers
Label | Adhesive is applied consistently and evenly across the surface to achieve correct adhesion
Label | Adhesive does not spill onto membrane, weldable laps or surrounding areas that can potentially contaminate welds
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Install Fatrafol PVC Membrane
Label | Install Fatrafol to coincide with the falls of the roof
Label | Ensure the membrane laps run with the fall of the roof to minimise negative laps on the roof
Label | Records - Time stamped photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Builders Application Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
SECTION | DETAILING - EACH LOCATION
Checkpoint | Hot Air Fusion Welding of PVC membrane.
Label | Hot air fusion weld overlaps.
Label | Achieve a minimum 40mm wide weld width on all hot air seam welds to achieve sufficient weld strength
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
SIGNOFF | Subcontractor Inspection - Sign Off
Checkpoint | Installation of PVC Coated Angles
Label | Fixing Fatranyl PVC coated termination angles using relevant fixings
Label | All termination metals are aligned correctly and are not disjointed or protruding
Label | Fixings centres do not exceed 200mm centres
Label | PVC coated termination angles are installed with a minimum 2mm gap between each angle to allow for structural movement and expansion
Label | Records - Time Stamped Photograph
select | Inspection | Surveillance point, Witness point
Checkpoint | Builders Detailing Review
SIGNOFF | Site Engineer/ Foreman Inspection - Sign Off
Section | QA TESTING - EACH LOCATION
Checkpoint | Inspection
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required.
Label | Records - time stamped photograph
select | Inspection | Surveillance point, Witness point