## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Sleeves ITP |  |  |  |  | Yes | Sleeves ITP | 063583d8-c393-4b83-8f99-0353cdad90b3
checkpoint-status |  |  | checkpoint | Penetration sleeves installed in accordance with applicable, TFP/Combined approved drawings
checkpoint-status |  |  | checkpoint | Cast in pipework/sleeves as per approved engineer detail
label | a26abc1f-b201-550a-a994-1e159c6d75ad |  | note | Comment Notes relevant to inspection below
checklist-sectioned |  |  | checklist | MASDS ITP |  |  |  |  | Yes | MASDS ITP | 2858faed-3a5c-4b74-a7fa-5d331d87fcd0
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, SAPN, Telstra and Austel regulations
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with labels - Please attach photos
checkpoint-status |  |  | checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables
checkpoint-status |  |  | checkpoint | MASDS Sampling Conduits, sampling points, MASDS detection unit and MASDS control modules installed in accordance with applicable drawings and I.E.I recommendations
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Final cleaning - check MASDS protection area to ensure it is dust free. Obtain confirmation from Builders site representative that no further works are to proceed within MASDS protected area after cleaning
checkpoint-status |  |  | checkpoint | Conducted MASDS testing procedures
checkpoint-status |  |  | checkpoint | Arrange formal SAMFs inspection and system testing
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
holdpoint |  |  | signoff | Request Builder Sign Off
checklist-flat |  |  | checklist | Sprinkler System First Fix |  |  |  |  | Yes | Sprinkler System First Fix | 4beae0f6-0bea-48fd-998c-fb1ad8289141
checkpoint-status |  |  | checkpoint | Pipework installed in accordance with applicable TFP approved drawings
checkpoint-status |  |  | checkpoint | First fix sprinkler pipework, hangers, seismic fixings, guards, air bleed vents, drain valves fitted in accordance with AS2118
checkpoint-status |  |  | checkpoint | First Fix Pressure Test
checklist-sectioned |  |  | checklist | Hydrant Mains Risers ITP |  |  |  |  | Yes | Hydrant Mains Risers ITP | 53a13434-9222-4417-8dad-0a8c85e263fb
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Pipework installed in accordance with appliance standards, seismic fixings & specifications
checkpoint-status |  |  | checkpoint | Hydrant & hose reel pipework cleaned & capped for transport to site
label | d92be647-4c88-5d94-8d26-1973f4ef7c66 |  | note | Hydrant & hose reels located in accordance with AS2419
checkpoint-status |  |  | checkpoint | First fix hydrant pipework, hangers, seismic fixings, drain valves fitted in accordance with AS2419
label | 21d2ffeb-0115-55d0-ae9b-209caa52ba62 |  | note | Hydrant seismic hanging systems to be installed to AS1170.4 & include engineers sign off & supporting documentation
checkpoint-status |  |  | checkpoint | Hydrants installed in accordance with AS2419 and SA water requirements
checkpoint-status |  |  | checkpoint | Hydrant caps and chains fitted
checkpoint-status |  |  | checkpoint | Hydrant valve wheels or oval spindles fitted as specified
checkpoint-status |  |  | checkpoint | Hydrant hose connection checked for SAMFs approved thread
checkpoint-status |  |  | checkpoint | Inspection carried out by Engineer - Attached/Any relevant comments added below
label | 22d9f61e-859c-5512-b142-c153618f6a35 |  | note | Sign-off attached below as applicable
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with labels - Please attach photos
button | 4c215e87-9fd8-527c-a46b-fdec1aa86360 |  | button | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | 96423357-2408-5580-b5a8-2ddd428ff7ba |  | note | Sign-off attached below as applicable
checkpoint-status |  |  | checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
button | bf101e7f-f644-5191-92c1-f2400f8ea92c |  | button | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | 29db943c-7c0b-5e21-a5a8-35b182af5799 |  | note | Sign-off attached below as applicable
checkpoint-status |  |  | checkpoint | Hose reels located in accordance with approved drawing and in accordance with AS2441
checkpoint-status |  |  | checkpoint | All above ground pipework securely fixed and plugged off and isolating valves closed
checkpoint-status |  |  | checkpoint | Inspection carried out - Detail any corrective action for non-conformance Inspections
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Review inspection details above to verify that all inspections are satisfactory and test procedures can now follows
checkpoint-status |  |  | checkpoint | Connect air compressor to above ground pipework to be tested. Fill pipework with compressed air to 100kpa. Inspect above ground pipework for obvious leakage. Re-check pressure gauge and if no major pressure loss, pump up to 200kpa
label | da8b287a-a1ac-5cad-bf80-4f4812dcde27 |  | note | Hold at 200kpa for 10 minutes. If no obvious air leakage from pipework being tested, release air pressure via control valve on compressor, and fill pipework with water to towns main pressure
checkpoint-status |  |  | checkpoint | Connect pressure test pump to water filled section of pipework being tested. Pump to 1000kpa and hold pressure for 5 minutes
label | bac16056-e6a3-56cc-87c6-84ac252db709 |  | note | If no obvious loss of pressure, pump to 1500kpa. if no obvious loss of pressure pump to 1700kpa and hold at this test pressure for at least two hours
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist-sectioned |  |  | checklist | Sprinkler System Second Fix |  |  |  |  | Yes | Sprinkler System Second Fix | 562f52cb-fe66-4070-8bb5-be982de1cbdb
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Second fix sprinkler pipework, hangers, seismic fixings, guards, air bleed vents, drain valves fitted in accordance with AS2118
checkpoint-status |  |  | checkpoint | Second Fix Pressure Test
checkpoint-status |  |  | checkpoint | Sprinkler seismic hanging systems to be installed to AS1170.4 & include engineers sign off & supporting documentation
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system with the location indicated on as builts with labels - Please attach photos
checkpoint-status |  |  | checkpoint | Sprinkler head spacings & temperature ratings checked to comply with AS2118
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Connect air compressor to above ground pipework to be tested. Fill pipework with compressed air to 100kpa
label | 617ceedb-be25-5584-a55b-033ba7a72959 |  | note | Inspect above ground pipework for obvious leakage. Re-check pressure gauge and if no major pressure loss, pump up to 200kpa. Hold at 200kpa for 10 minutes. If no obvious air leakage from pipework being tested, release air pressure via control valve on compressor, and fill pipework with water to towns main pressure and set up TFP pressure test pump
checkpoint-status |  |  | checkpoint | Notify builders supervisor that fire services pipework is to be pressure tested
checkpoint-status |  |  | checkpoint | If no obvious loss of pressure pump switch on TFP pressure test pump and pump to 1600kpa and hold at this test pressure for at least two hours as specified
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist-sectioned |  |  | checklist | Pre Action System ITP |  |  |  |  | Yes | Pre Action System ITP | 64cf8b39-1690-466d-89af-b34a478d68a6
checkpoint-group |  |  | section | Installation - First Fix
checkpoint-status |  |  | checkpoint | Pipework installed in accordance with applicable TFP approved drawings
checkpoint-status |  |  | checkpoint | First fix pipework, hangers, seismic fixings, guards, air bleed vents, drain valves fitted in accordance with AS2118
checkpoint-status |  |  | checkpoint | First Fix Pressure Test
checkpoint-group |  |  | section | Installation - Second Fix
checkpoint-status |  |  | checkpoint | Second fix pipework, hangers, seismic fixings, guards, air bleed vents, drain valves fitted in accordance with AS2118
checkpoint-status |  |  | checkpoint | Second Fix Pressure Test
checkpoint-status |  |  | checkpoint | Sprinkler seismic hanging systems to be installed to AS1170.4 & include engineers sign off & supporting documentation
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system with the location indicated on as builts with labels - Please attach photos
checkpoint-status |  |  | checkpoint | Sprinkler head spacings & temperature ratings checked to comply with AS2118
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Review inspection details above to verify that all inspections are satisfactory and test procedures can now follows. Ensure TFP chargehand carries out/supervises the pressure testing and remains with the TFP pressure test pump while tests are in progress. Do not allow TFP apprentices to carry out pressure testing without close supervision.
label | f13ca379-3f20-5392-8b64-b1baedca3caa |  | note | NOTE: Air testing is only required to be performed when there is a risk of water damage to finished floors or furnished buildings.
label | af7d047b-0591-5137-bdc0-71f613daf0de |  | note | NOTE: LL requires 24 hours notice for water and 48 hour notice for air, this will be communicated in the builder’s brief. This has been added to swms. Provide schematics, pressure source location, pressure relief device, equipment used, calibration certificates that will be used are to be included in the ITP submission to the builder's brief.
label | 4d546d6a-715d-5236-92f8-557fb71e4aff |  | note | NOTE: Ensure suitable warning signage is displayed at all entrances and exits to area of pressure testing being carried out stating “warning TFP pressure testing pipe work”. Notify builders foreman and supervisors that the relevant levels, risers or areas are being pressure tested.
checkpoint-status |  |  | checkpoint | Prior to using TFP mobile air compressor, ensure that the pre set 400kpa pressure relief valve has been fitted to the pipe work being tested as a fail safe of over pressurisation. Visually inspect the TFP air compressor being used for the test to ensure no damage to the compressor assembly and hoses. Check to ensure pressure gauge fitted to TFP test manifold is operational. Note, any air testing above 80kpa requires test plan approved by LL regional EHS manager.
checkpoint-status |  |  | checkpoint | Install TFP's certified pressure gauge with test certificate that is valid and in date to the system/area of pipe work being tested
checkpoint-status |  |  | checkpoint | Ensure TFP's air compressor test pump discharge/outlet connector is connected to the pipe work to be tested above/down stream of the main stop valve either using roll grove, gal mal screwed or high-pressure hoses.
checkpoint-status |  |  | checkpoint | Once all inspection/checks have been completed and TFP’s mobile air compressor test pump is connected, ensure pre action system main stop valve is closed, turn air compressor on and prove air is available. Open air compressor discharge/outlet valve and fill system to 100kpa, then close discharge/outlet valve. Visually walk the area under test to check for any air leaks.
checkpoint-status |  |  | checkpoint | If no obvious air leaks and pressure holding at 100kpa for a period of 20 minutes, open discharge/outlet valve on TFP's mobile air compressor test pump and pressurise to 300kpa or 1 and a 1/2 times system working pressure. Check area under test for any air leaks then hold required pressure for two hours. A TFP employee is to remain watching the testing for the entire duration.
checkpoint-status |  |  | checkpoint | After test completion ensure main stop valve is padlocked closed. Slowly reduce air pressure to 0 through the pre action system drain valve. Once pressure gauge is reading 0, disconnect TFP’s air compressor test pump from the pre action system and connect systems permanent air compressor ready for system simulation test.
checkpoint-status |  |  | checkpoint | Confirm pre action system solenoid operates on fire alarm in the protected area when smoked detector is forced into alarm with test smoke.
checkpoint-status |  |  | checkpoint | Ensuring the main stop valve is still in the closed position, re-pressurise the dry pipe pre action system with air utilising the permanent systems air compressor to its pre set systems working pressure of 200kpa of air. Then close systems down stream test valve above pre action valve set to prevent system being flooded with water. Open the main stop valve below pre action valve so system is primed and in its normal operational setting. Introduce smoke to simulate smoke detectors going into alarm and operating solenoid. Simulate a loss of air pressure through the pre action valve set drain valve, actuating the pre action system to operate and come into alarm.
checkpoint-status |  |  | checkpoint | Ensure TFP chargehand is supervising the pressure test at all times and inspects pipework while it is under test pressure. Arrange for client to witness the two-hour pressure test.
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist-flat |  |  | checklist | Fire Alarms First Fix |  |  |  |  | Yes | Fire Alarms First Fix | 6e7e5a7d-f943-4375-b1a8-37e352f492ee
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, ETSA regulations, Telstra and Austel regulations
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables
checklist-sectioned |  |  | checklist | ITP4535-004 Fire Alarms |  |  |  |  | Yes | ITP4535-004 Fire Alarms | 7f124806-0aa2-4eb8-aa9f-ebf582fe2c2e
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence
label | d6245fff-b02f-52b2-bb4b-a43fdead8125 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
text | 0436e31f-0da1-5096-9105-c64279326dad |  | textbox | Relevant Drawing & Revision #
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, ETSA regulations, Telstra and Austel regulations
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables
checkpoint-status |  |  | checkpoint | Detectors, bells, break glass alarms, automatic magnetic door holders, visual alarms, mimic panels, main FIP, data gathering panels all installed in accordance with applicable approved drawings and AS1668, AS2036, as1670,AS1603 and SAMFs requirements
checkpoint-status |  |  | checkpoint | Inspection carried out - Attached/Any relevant comments added below
checkpoint-status |  |  | checkpoint | Detail and corrective action for non-conformance Inspections
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Review inspection details above to verify that all inspections are satisfactory and test procedures can now follow
checkpoint-status |  |  | checkpoint | Ensure client and builders site representative are aware that fire alarm system is to be tested, resulting in audible alarms
label | cc8f7bb2-e82e-5ab1-9c8e-bc11c5e0a219 |  | note | Audible and visual alarms can be disconnected or isolated during test once they have been proved to be operational
checkpoint-status |  |  | checkpoint | Set SAMFs signalling device to test position
label | 7c4e6745-b978-50b4-9741-b90a13c79bb4 |  | note | Ensure all mechanical plant interface circuits are isolated or disconnected (smoke spill fans, gas solenoid, etc)
checkpoint-status |  |  | checkpoint | Connect 240 volt power to FIP and install sealed lead acid batteries
checkpoint-status |  |  | checkpoint | Review FIP block plans against actual installation and ensure detector identification numbers are correctly shown
checkpoint-status |  |  | checkpoint | Test every single smoke detector and thermal detector by introducing smoke/heat from an approved test device. Ensure FIP is reset after each detector has gone into the alarm mode
label | a24bdae8-279c-54cf-94c1-a41378edcca2 |  | note | Check to ensure above ceiling remote identification plates operate
label | 13c3b215-0a64-5e17-b702-d25e663c85f3 |  | note | Ensure alarm bells and visual device operate correctly, and that EWIS panel is activated as per zoned requirements
checkpoint-status |  |  | checkpoint | Test every single break glass alarm unit by using test key provided
label | 389c2b39-dbbc-5ff8-af81-d63008798fa9 |  | note | Ensure FIP is reset after each break glass alarm has been activated. Test fire pump controls and indications
checkpoint-status |  |  | checkpoint | Test all outputs to BMS system with bms commissioning engineer in attendance. Test automatic/manual “stop/start” of smoke spill fans and fan status indicators
checkpoint-status |  |  | checkpoint | Test every single magnetic door hoding device and prove all unites to be fully operational
checkpoint-status |  |  | checkpoint | Test all auxiliary FIP outputs to mimic panels, EWIS system, gas solenooid valve, mechanical plant, SAMFs signalling device
checkpoint-status |  |  | checkpoint | Simulated mains power failure in order to prove automatic change over to back-up batteries
label | bf849dd8-b156-545d-9ffe-2475f6fa4d97 |  | note | Carry out load test with all devices connected in order to prove correct battery capacity
checkpoint-status |  |  | checkpoint | Arrange client witness test
label | 2f0bffb6-76e4-5e15-be6c-1410b7039552 |  | note | Test of 6 smoke detectors at random chosen by client
checkpoint-status |  |  | checkpoint | Arrange formal SAMFs inspection and system testing
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | d171608d-bc73-5974-a348-e48e11cf43f4 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 4cff5abf-e87d-5da2-b4aa-78266206e83b |  | button | Area left clean & tidy | Yes, No
boolean | 13af37a2-e827-5a6d-b71c-c528859b18a6 |  | tickbox | Trojan Sign-Off (Add below)
boolean | 5b200cf5-30cb-54dc-9346-6fc6bad585f5 |  | tickbox | Builder Sign-Off (Add below)
checklist-sectioned |  |  | checklist | Fire Panel ITP |  |  |  |  | Yes | Fire Panel ITP | 97f3e1c1-b6dd-4a86-b50d-3e39399d21e0
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, etsa regulations, telstra and austel regulations.
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables.
checkpoint-status |  |  | checkpoint | Detectors, bells, break glass alarms, automatic magnetic door holders, visual alarms, mimic panels, main fip all installed in accordance with applicable approved drawings and as1668, as2036, as1670, as1603 and samfs requirements.
checkpoint-status |  |  | checkpoint | Detail and corrective action for non-conformance
checkpoint-group |  |  | section | Test procedures
checkpoint-status |  |  | checkpoint | Ensure client and builders site representative are aware that fire alarm system is to be tested, resulting in audible alarms (audible and visual alarms can be disconnected or isolated during test once they have been proved to be operational).
checkpoint-status |  |  | checkpoint | Connect 240 volt power to fip and install sealed lead acid batteries.
checkpoint-status |  |  | checkpoint | Test all auxiliary fip outputs to mimic panels, ewis system, gas solenoid valve, mechanical plant, samfs signalling device.
checkpoint-status |  |  | checkpoint | Simulated mains power failure in order to prove automatic change over to back-up batteries. Carry out load test with all devices connected in order to prove correct battery capacity.
checkpoint-status |  |  | checkpoint | Arrange formal samfs inspection and system testing.
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Inspected By Trojan Fire
checkpoint-status |  |  | checkpoint | Inspected by Client - client signoff attached
checklist-sectioned |  |  | checklist | Fire Alarms Second Fix |  |  |  |  | Yes | Fire Alarms Second Fix | b1995ae7-d054-4e14-93a6-e5de548e0f97
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Detectors, bells, break glass alarms, automatic magnetic door holders, visual alarms, mimic panels, main FIP, data gathering panels all installed in accordance with applicable approved drawings and AS1668, AS2036, as1670,AS1603 and SAMFs requirements
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Ensure client and builders site representative are aware that fire alarm system is to be tested, resulting in audible alarms
label | 700dc498-bd26-589f-b47f-42300c2b1705 |  | note | Audible and visual alarms can be disconnected or isolated during test once they have been proved to be operational
checkpoint-status |  |  | checkpoint | Conducted SAMFs signalling device test procedures
label | 2cc1db29-c27a-5df9-b8c3-72cca8e29422 |  | note | Ensure all mechanical plant interface circuits are isolated or disconnected (smoke spill fans, gas solenoid, etc)
checkpoint-status |  |  | checkpoint | Arrange formal SAMFs inspection and system testing
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
holdpoint |  |  | signoff | Request Builder Sign Off
checklist-flat |  |  | checklist | Booster Installation ITP |  |  |  |  | Yes | Booster Installation ITP | b19bcab3-8edd-4ed4-9928-c50c93696efa
checkpoint-status |  |  | checkpoint | Booster pipework cleaned & capped for transport to site
checkpoint-status |  |  | checkpoint | Booster pipework installed in accordance with applicable standards & specification utilising approved seismic fixings & bracing, approved fire penetration sealing
label | 76be64f0-ea01-5a34-9e53-a06c0a64c4ac |  | note | Boosters located in accordance with approved drawing & in accordance with AS2419
checkpoint-status |  |  | checkpoint | SAMFs approved hydrant values, hard suction & dual booster connectors fitted including pressure gauges
checkpoint-status |  |  | checkpoint | All above ground pipework securely fixed & plugged off & isolating valves closed & SAMFs required signage & block plans installed
checkpoint-status |  |  | checkpoint | Booster enclosure to be in accordance with SAMFs
checkpoint-status |  |  | checkpoint | Door hold open devices fitted & budget locks fitted as specified
checkpoint-status |  |  | checkpoint | Arrange for SAMFs to inspect fire booster assembly
checklist-flat |  |  | checklist | Fire Pumps ITP |  |  |  |  | Yes | Fire Pumps ITP | bdec4d50-5e40-48b7-83e9-ef70d0eb7495
checkpoint-status |  |  | checkpoint | Pumps & associated pipework installed in accordance with the approved drawings & AS2118. Pump room secure & lockable
checkpoint-status |  |  | checkpoint | Pump wiring installed in accordance with AS3000 & phase 3 & neutral power supply available
checkpoint-status |  |  | checkpoint | Fire water storage tank water supply available (suction) & all piping (discharge) & drains complete, pressure tested ready for use
checkpoint-status |  |  | checkpoint | Diesel engine filled with oil, fuel, batteries connected & diesel muffler & exhaust fitted to vent exhaust gases to atmosphere
checkpoint-status |  |  | checkpoint | Pump testing completed - detail any non-conformances below
checklist-flat |  |  | checklist | Fire Extinguishers ITP |  |  |  |  | Yes | Fire Extinguishers ITP | bea1fe17-74c2-4729-80f9-53906d00dab2
checkpoint-status |  |  | checkpoint | Fire extinguishers & signs installed in accordance with AS 2444 & applicable approved drawing
checkpoint-status |  |  | checkpoint | Arranged SAMFS to carry out inspection and verify quantity and location of extinguishers are acceptable
checklist-sectioned |  |  | checklist | Fire Water Tanks ITP |  |  |  |  | Yes | Fire Water Tanks ITP | c2f75b87-4206-4778-9622-487be708e21c
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Tank roof and walls assembled in accordance with approved jsa's, shop drawings and approved construction drawings
checkpoint-status |  |  | checkpoint | Tank liner Installed in accordance with manufacturers data sheets and instructions
checkpoint-status |  |  | checkpoint | Ensure all tank panels, roof sheets, anchor bolts for tank internal braces are tight and no debris is left inside tank
checkpoint-status |  |  | checkpoint | Ensure all external tank connection fittings, access ladders, manhole covers, tank contents level indicators and external wind braces (if fitted) are correctly installed, tight and operational
checkpoint-status |  |  | checkpoint | Vacuum out any debris from inside tank and check all fixings/bolts for tightness. re-fit external manhole cover to form confined space
checkpoint-status |  |  | checkpoint | Tank leak test complete
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Make a detailed inspection of external walls of tank to check for any sign of a leak
checkpoint-status |  |  | checkpoint | Check ladders and manhole covers to ensure easy access is possible
checkpoint-status |  |  | checkpoint | Check tank contents gauge and signage for correct operation
checkpoint-status |  |  | checkpoint | Check tank roof and flashings to ensure no sharp edges and roof flashings are vermin proof
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist-sectioned |  |  | checklist | Hose Reels ITP |  |  |  |  | Yes | Hose Reels ITP | de4b48a2-ecdd-4f3a-bd38-e8444790e3c2
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Fire hose reels and signs installed in accordance with AS2441
checkpoint-status |  |  | checkpoint | Fire hose reels and sign installed in accordance with applicable approved drawing
checkpoint-status |  |  | checkpoint | Hose guides and rollers installed where applicable
checkpoint-status |  |  | checkpoint | Packing tapes removed, hose vented, water flow checked at minimum flow rate of 20 litres per minute
checkpoint-status |  |  | checkpoint | Fire hose reel turns freely with no excessive force
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Confirm hose reel pipework has been inspected and pressure tested as per ITP for hose reel pipework
checkpoint-status |  |  | checkpoint | With water supply valve to hose reels open, run out hose reels to full length and flow hose reels at full flow
label | f9fb662d-cca6-5ddf-905b-41dd12dc0827 |  | note | Check hose reel assembly for leaks and secure fixings. Shut off water supply valve and rewind hoses
checkpoint-status |  |  | checkpoint | Arrange for SAMFs to carry out inspection and flow test on each hose reel
checkpoint-status |  |  | checkpoint | Arrange for client to witness SAMFs tests
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
checklist-sectioned |  |  | checklist | MASDS ITP |  |  |  |  | Yes | MASDS ITP | e10feeab-6e9c-49fe-b330-3e76f1a1db70
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, SAPN, Telstra and Austel regulations
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with labels - Please attach photos
checkpoint-status |  |  | checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables
checkpoint-status |  |  | checkpoint | MASDS Sampling Conduits, sampling points, MASDS detection unit and MASDS control modules installed in accordance with applicable drawings and I.E.I recommendations
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Final cleaning - check MASDS protection area to ensure it is dust free. Obtain confirmation from Builders site representative that no further works are to proceed within MASDS protected area after cleaning
checkpoint-status |  |  | checkpoint | Conducted MASDS testing procedures
checkpoint-status |  |  | checkpoint | Arrange formal SAMFs inspection and system testing
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
holdpoint |  |  | signoff | Request Builder Sign Off
checklist-sectioned |  |  | checklist | EWIS ITP |  |  |  |  | Yes | EWIS ITP | f98c993e-471e-40c8-bd39-a1f631d1c340
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, SAPN, Telstra and Austel regulations
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with labels - Please attach photos
checkpoint-status |  |  | checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables
checkpoint-status |  |  | checkpoint | EWIS panel loudspeakers and WPIs installed in accordance with applicable approved drawings and AS1668, AS2036, AS1670, AS1603 and SAMFs requirements
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Ensure Client and Builders representative are aware that EWIS system is to be tested. Resulting in audible alarms
checkpoint-status |  |  | checkpoint | Conducted SAMFs signalling device test procedures
checkpoint-status |  |  | checkpoint | Arrange formal SAMFs inspection and system testing
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
holdpoint |  |  | signoff | Request Builder Sign Off
checklist-sectioned |  |  | checklist | ITP4535-002 EWIS |  |  |  |  | Yes | ITP4535-002 EWIS | fb052920-b23c-44f0-86dc-4626e9051ae7
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Confirm area of work is accessible & acceptable to commence
label | bb732bfc-b3dc-5565-9653-a8f3e24dd1e0 |  | note | Attach Photos/Comments below if any issues & Send report to Builder
text | 731a9073-2d9c-5161-a68c-9be99455c9aa |  | textbox | Relevant Drawing & Revision #
checkpoint-status |  |  | checkpoint | Wiring installed in accordance with AS3000, SAPN, Telstra and Austel regulations
checkpoint-status |  |  | checkpoint | Fire penetrations to be sealed in accordance with manufacturers tested system to the locations as indicated on as built drawings complete with notes - Please attach photos
button | eac12a6e-fe9a-5b73-86b1-0853913e233b |  | button | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | d0b35a3b-ba2b-5941-9055-6674984d1ac3 |  | note | Sign-off attached below as applicable
checkpoint-status |  |  | checkpoint | Acoustic penetrations to be sealed in accordance with approved sample wall & manufacturers tested system to the locations as indicated on as builts
button | f4948b5c-20d0-5cda-b0d8-eb54d56a71ad |  | button | Inspection carried out by Engineer - Attached/Any relevant comments added below | Yes, No, N/A
label | 121b0742-21c1-5429-99cd-8f459e4ce05f |  | note | Sign-off attached below as applicable
checkpoint-status |  |  | checkpoint | Continuity and polarity checks carried out on all cables
checkpoint-status |  |  | checkpoint | EWIS panel loudspeakers and WPIs installed in accordance with applicable approved drawings and AS1668, AS2036, AS1670, AS1603 and SAMFs requirements
checkpoint-status |  |  | checkpoint | Inspection carried out - Attached/Any relevant comments added below
checkpoint-status |  |  | checkpoint | Detail and corrective action for non-conformance Inspections
checkpoint-group |  |  | section | Test Procedures
checkpoint-status |  |  | checkpoint | Review inspection details above to verify that all inspections are satisfactory and test procedures can now follow
checkpoint-status |  |  | checkpoint | Ensure Client and Builders representative are aware that EWIS system is to be tested. Resulting in audible alarms
checkpoint-status |  |  | checkpoint | Set SAMFs signalling device to test position
label | 4e6caa58-bebe-530b-b4c0-1b72a5e7599d |  | note | Ensure all mechanical plant interface circuits are isolated or disconnected (Smoke spill fans, gas solenoid, etc)
checkpoint-status |  |  | checkpoint | Connect 240 volt power to EWIS and install sealed lead acid batteries
label | 2bc48aa8-e027-5a9c-97e3-c9781389c4cf |  | note | Isolate EWIS inputs from FIP and set EWIS to "manual" position
checkpoint-status |  |  | checkpoint | Test EWIS system in "manual" mode, check audibility of all loudspeakers
label | 1caeee59-a0c8-5a72-ad5a-9f59aeaa54a4 |  | note | Check all WIPs for audible tone and clear speech
label | 55764c0b-19c3-53a7-a3c4-01e444889956 |  | note | Ensure EWIS system provides correct DB requirements to all parts of the building by using hand held DB meter
checkpoint-status |  |  | checkpoint | Once initial audibility tests have been completed ,
label | 778f00da-b630-5689-a58a-27576f992509 |  | note | Initiate "manual alert" for each floor and all floors
label | f9b6bc30-46b9-5e09-b46b-97c8be97f37e |  | note | Then initiate "manual evacuate" for each floor and all floors
checkpoint-status |  |  | checkpoint | Once all above tests have been carried out, set EWIS system to “automatic” mode
label | 54858a2d-dac8-5a72-a5ad-0ffc06f8895f |  | note | Set output from FIP to EWIS to normal mode and simulate fire alarm on FIP
label | 18db2270-b31c-558f-a5d3-ce6d2092be2f |  | note | Check to ensure EWIS system automatically sounds the “alert” tone throughout the building and sounds “evacuate” tone on floor that initiated the simulated fire alarm
checkpoint-status |  |  | checkpoint | Once EWIS system has been tested on “manual” and “automatic” mode continue to test all wip’s from each floor to EWIS control panel and between floors
label | 9864093d-33c2-58d9-af60-ad56a216f94f |  | note | Between each and every WIP
checkpoint-status |  |  | checkpoint | Simulate mains power failure in order to prove automatic change over to back-up batteries. carry out load test with all devices connected in order to prove correct battery capacity
checkpoint-status |  |  | checkpoint | Arrange for client to Witness the two hour pressure test
label | e4c2128e-894a-5432-87cd-6e6ae1ed6680 |  | note | Test of 6 EWIS zones and WIPs at random chosen by Client
checkpoint-status |  |  | checkpoint | Arrange formal SAMFs inspection and system testing
checkpoint-group |  |  | section | Sign-Off
checkpoint-status |  |  | checkpoint | Works completed to specification/drawings - Attach photos of work below
label | ccfd25d5-3774-5bd6-b036-31abd32bea84 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | 2a8f6221-26bd-5bbb-a65c-f827099d0724 |  | button | Area left clean & tidy | Yes, No
boolean | 98ca0a07-ea62-5ea5-96a7-f3700c72e57e |  | tickbox | Trojan Sign-Off (Add below)
boolean | 9a1455a8-5f0c-5602-873c-ba7afe30810c |  | tickbox | Builder Sign-Off (Add below)