## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP 004 Hydraulics – Hydrants |  |  |  |  | Yes | ITP 004 Hydraulics – Hydrants | 012db2bd-5203-493a-8cfd-530345733b5c
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade Registration
checkpoint-group |  |  | section | Set Out & Service Location
checkpoint-status |  |  | checkpoint | Mark out hydrant locations as per contract documents and compliance with AS2419.1 Fire Hydrant Installations.
checkpoint-status |  |  | checkpoint | Services in trenching area have been located or shown on documentations prior to commencing works.
checkpoint-group |  |  | section | Trenching
checkpoint-status |  |  | checkpoint | Where excavations are >1.5m deep Services Subcontractors have prepared a Safe Work Method Statement and submitted to HY and permit completed
checkpoint-status |  |  | checkpoint | A Plant Safety Verification has been conducted for all mobile plant to be used for In Ground Services Installation
checkpoint-group |  |  | section | Pipes Support
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS2419 clause 8.7. Vertical & Horizontal support as per AS2491.1 Fire Hydrant Installations. Table 8.7.7. DN80 Max spacing 5m, DN100 Max spacing 5m & >100 Max spacing 6m. underground pipework to be secured as per AS2419.1 clause 8.8
checkpoint-group |  |  | section | Valves
checkpoint-status |  |  | checkpoint | Valve to comply with AS2638.1 Gate valves for waterworks purposes ,AS2638.2 Resilient seated gate valve & AS3579 Cast Iron Wedge gate valve for general purpose.
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Pipework selection and sizes as per specifications and for construction drawings.
checkpoint-status |  |  | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | AS2419 Fire Hydrant Installations
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | Underground pipework to have identification tape installed.
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with the Australian standard
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Prior to test the system shall have all air and debris flushed from the system as per AS 2419.1 clause 10.2.1
checkpoint-status |  |  | checkpoint | Hydrostatic pressure test to AS2419.1 clause 8.4. Pressure tests at 1500 KPA or 1.5 times the design pressure whichever is the greater for duration of 2 hours. If pipe work is underground the test shall be made before covering of the joints takes place. The pipework sections will be partially backfilled for securing during test.
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Photographs of installed services prior to backfill.
checkpoint-status |  |  | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil
checkpoint-status |  |  | checkpoint | Bedding material and trench backfill is in accordance with IFC Drawings, sample submission and specification
label | b893bcd3-693e-5663-9837-a130f67e83bf |  | note | (Bedding material grading certificate to be provided)
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the water services scope of works. Excess spoil removed in accordance with contract terms
checkpoint-status |  |  | checkpoint | Excess spoil removed in accordance with contract terms
checkpoint-group |  |  | section | Final Inspection / Commission
checkpoint-status |  |  | checkpoint | System shall be commissioned as per AS2419.1 Fire Hydrant Installations clause 10.3. Details of commission attached to back of ITP.
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components. Provide verifications of testing
checklist-sectioned |  |  | checklist | ITP 008 Hydraulics – Sanitary Fixtures & Tapware |  |  |  |  | Yes | ITP 008 Hydraulics – Sanitary Fixtures & Tapware | 046f8d35-1d58-47e7-8467-6c6da0b9b7dd
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Fixture / Tapware Selection
checkpoint-status |  |  | checkpoint | Refer to schedules in specifications and design documentation.
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Generally refer to manufacturer's literature for correct installation details. Ensure that items are installed level, plumb & true. Ensure that moving parts function freely and without obstruction.
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be flushed of all foreign matter. Remove all protective coatings, stickers and clean surfaces.
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean site area affected by the fixtures & tapware scope of works
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement of contract including Dimensioned, Surveyed, Falls, Locations, Components
label | cee72f16-d854-5800-93b1-6f7d3da3852b |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 009 Hydraulics – Water Heaters |  |  |  |  | Yes | ITP 009 Hydraulics – Water Heaters | 2ef4cc42-6f52-4bd0-9bd3-75e7b443de15
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Heater Selection
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Generally refer to manufacturer's literature for correct installation details. Where applicable refer to AS5601 for gas appliance installation.
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be flushed of all foreign matter. Remove all protective coatings, stickers and clean surfaces. Where applicable test gas fired plant to AS5601 – Gas installations
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean site area affected by the Water Heaters scope of works
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement of contract including Dimensioned, Surveyed, Falls, Locations, Components
label | 321b5b26-9389-5772-98a4-7211b5e2d80b |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 007 Hydraulics – Stormwater |  |  |  |  | Yes | ITP 007 Hydraulics – Stormwater | 3a84ceff-2853-4fa8-a79b-423ec9d17f5f
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe locations and co-ordinate with other trades.
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pipe Support
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS 3500.2 Table 9.1
checkpoint-group |  |  | section | Pipe Laying
checkpoint-status |  |  | checkpoint | Pipes to be laid in straight lines between changes of directions. Pipes are to be laid on base of crushed hard rock or coarse washed sand.
checkpoint-status |  |  | checkpoint | Pipework selection and sizes as per specifications and for construction drawings and AS 3500
checkpoint-status |  |  | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework have been installed without damage
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | Underground pipework to have identification tape installed.
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with Australian Standards
checkpoint-group |  |  | section | Pits
checkpoint-status |  |  | checkpoint | Pits to have smooth, seamless finish using steel trowel or concrete cast in steel frames. Design and for construction drawings
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Test to AS 3500.3 Section 10 Clauses 10.3 .1 & 10.3.2 Hydrostatic Water Test for a period of 3min.
checkpoint-status |  |  | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
checkpoint-status |  |  | checkpoint | Inground services have been inspected by the relevant authorities/consultants prior to closing up (witness/hold point)
checkpoint-status |  |  | checkpoint | Pipe/conduit compliance record/certificate
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Pipes are to be laid on base of crushed hard rock or coarse washed sand. The balance of the trench to be filled and compacted with selected removed spoil.
checkpoint-status |  |  | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Bedding material grading certificate to be provided
checkpoint-status |  |  | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Photographs of installed services prior to backfill
checkpoint-status |  |  | checkpoint | Surfaces disturbed during services installation have been adequately reinstated/repaired
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the Stormwater scope of works
checkpoint-status |  |  | checkpoint | Excess spoil removed from site by as per contract terms
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records clean and flush entire installation
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
label | 359d21e3-35ac-562b-b4a0-6113eb0e1739 |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 013 Hydraulics – Inground Sewer Drainage |  |  |  |  | Yes | ITP 013 Hydraulics – Inground Sewer Drainage | 4a77923b-f887-490b-8913-7aa2cb7497c0
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Excavation
checkpoint-status |  |  | checkpoint | Excavate trenches to minimal size
checkpoint-status |  |  | checkpoint | Grade Trenches to Falls
checkpoint-status |  |  | checkpoint | Bed pipes on 10mm – blue metal
checkpoint-status |  |  | checkpoint | Surfaces disturbed during services installation have been adequately reinstated/repaired
checkpoint-group |  |  | section | Pipework
checkpoint-status |  |  | checkpoint | Pipework is in accordance with IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Minimum separation of underground services is achieved
checkpoint-status |  |  | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework have been installed without damage
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued
checkpoint-status |  |  | checkpoint | Pipe/conduit compliance record/certificate as per specification
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Pits
checkpoint-status |  |  | checkpoint | Adequate Protection
checkpoint-status |  |  | checkpoint | Installation as per specification
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Inground services have been inspected by the relevant authorities/consultants prior to closing up (witness/hold point)
checkpoint-status |  |  | checkpoint | Photographs of installed services prior to backfill
checkpoint-status |  |  | checkpoint | Backfill pipe with 10mm blue metal then backfill with selected excavated material
checkpoint-status |  |  | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification.
checkpoint-status |  |  | checkpoint | Bedding material grading certificate to be provided
checkpoint-status |  |  | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the Stormwater scope of works
checkpoint-status |  |  | checkpoint | Excess Spoil removed from site by others
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records clean and flush entire installation
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
label | f99cec24-1814-563d-963c-bbb2a4215f5e |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 018 Rough Ins (Cold, Hot, Warm & Recycled Water and Gas) |  |  |  |  | Yes | ITP 018 Rough Ins (Cold, Hot, Warm & Recycled Water and Gas) | 6e7dfae3-993e-4595-a5c0-8407af565639
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Valves
checkpoint-status |  |  | checkpoint | Check valves for water mark approval.
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures
checkpoint-status |  |  | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-group |  |  | section | Pipe Installation
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings. Where applicable, Infrastructure Authority requirements including applications, approvals and testing procedures and no damage to pipework
checkpoint-status |  |  | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements Pipework Joints have been appropriately treated/glued and Pipe/conduit compliance record/certificate
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | Pipework to have identification stickers applied as per AS 3500.
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with Australian standard
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be flushed of all foreign matter.
checkpoint-status |  |  | checkpoint | Hydrostatic pressure test before wall and ceiling sheeting is commenced and where applicable as per Infrastructure Authority requirements including applications, approvals and testing procedures.
checkpoint-status |  |  | checkpoint | As per AS 3500 or as specified
checkpoint-status |  |  | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
label | 325c5974-0c41-58df-bae4-0e1a9f66406f |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 016 Hydraulics – Trade Waste Drainage |  |  |  |  | Yes | ITP 016 Hydraulics – Trade Waste Drainage | 73409199-990d-4f45-b1f6-a05ead1da8e1
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-group |  |  | section | Pipe Supports
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS 3500.2 Table 9.1
checkpoint-group |  |  | section | Pipe Laying
checkpoint-status |  |  | checkpoint | Pipes to be laid in straight lines between changes of directions. Crushed rock, gravel screenings or recycled crushed concrete, roof tiles or bricks of nominal size 7-10mm. refer to AS 3500.2 Section 5 Figure 5.1 for bedding section detail. Pipes to be laid in straight lines between changes of directions.
checkpoint-status |  |  | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Pipe selection as per Table 4.1. Pipework selection and sizes as per specifications and for construction drawings. Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework have been installed without damage
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued Pipe/conduit compliance record/certificate
checkpoint-group |  |  | section | Grease Arrestor
checkpoint-status |  |  | checkpoint | Location and depth as per specifications and for construction drawings.
checkpoint-status |  |  | checkpoint | Installation as per Manufacturer's Guidelines
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Test to AS 3500.2 Section 13 Clauses 13.2 & 13.3 Hydrostatic Water Test or Air test to 30 KPA for a period of 3min.
checkpoint-status |  |  | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Backfill pipe with Crushed rock, gravel screenings or recycled crushed concrete, roof tiles or bricks of nominal size 7-10mm and fill balance of trench with selected excavated spoil and compact to standards.
checkpoint-status |  |  | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Bedding material grading certificate to be provided
checkpoint-status |  |  | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Photographs of installed services prior to backfill
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the wastewater scope of works. Excess spoil removed from site as per contract terms
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records clean and flush entire installation
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
label | 66c02ad2-e2cf-5492-8c51-4335580ec766 |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed
checklist-sectioned |  |  | checklist | ITP 003 Hydraulics – Hose Reels |  |  |  |  | Yes | ITP 003 Hydraulics – Hose Reels | 7497f815-1993-4796-867d-c0872c9e8e1a
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade Registration
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out hose reel locations as nominated on drawings in locations. Location to comply with AS2441 clause 10.
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pipe Support
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS 3500. Extra supports to be added to prevent pipe movement caused by water pressure effects
checkpoint-group |  |  | section | Hose Reels & Valves
checkpoint-status |  |  | checkpoint | Check hose reels & valves for water mark approval as per AS 1221. Selection as per clause 9 table 9
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
label | 98d365d6-7cc7-5ace-bdc4-8a1f26a83898 |  | note | AS2419.1 & AS2442 clause 6.4
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | Underground pipework to have identification tape installed.
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with Australian standard
checkpoint-group |  |  | section | Pressure Testing
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be flushed of all foreign matter.
checkpoint-status |  |  | checkpoint | Hydrostatic pressure test before backfilling, lagging & covering. Pipework with elastomeric or RRJ shall be backfilled leaving the joints exposed. Test as per AS 3500.4. 1500 KPA for 30 min. No leaks are acceptable. Some fixture cannot handle 1500 KPA.
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the water services scope of works. Excess spoil removed in accordance with contract terms
checkpoint-group |  |  | section | Final Inspection / Commission
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records Hose Reels to be commissioned as per AS2441 clause 12.
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
label | 33258d06-d4a0-58b2-8050-01f9d0e4e54f |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 017 Hydraulics – Penetrations and Core Holes |  |  |  |  | Yes | ITP 017 Hydraulics – Penetrations and Core Holes | 789a29fa-373d-45b5-a9c9-b22a82cb0d09
checkpoint-group |  |  | section | Scope of Work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
label | 366b81f3-8ac8-586b-9f75-4158b8b25ca0 |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade Registration
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out Deck. Check Hydraulic Shop Penetration Drawing is current.
checkpoint-status |  |  | checkpoint | Correct height of sleeves and or Fire collars
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Material
checkpoint-status |  |  | checkpoint | Confirm fire collars are approved for the relevant materials being used.
checkpoint-group |  |  | section | Location
checkpoint-status |  |  | checkpoint | AFC Hydraulic Penetration Drawings used
checkpoint-group |  |  | section | Check
checkpoint-status |  |  | checkpoint | Visually Check penetration are all in place against Drawing none have been damaged or removed by other trades
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with
checkpoint-group |  |  | section | Prior to Pour
checkpoint-status |  |  | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Pour
checkpoint-status |  |  | checkpoint | Person present duration of pour
checklist-sectioned |  |  | checklist | ITP 014 Hydraulics – Sanitary Plumbing |  |  |  |  | Yes | ITP 014 Hydraulics – Sanitary Plumbing | 8ee0728c-1094-4ef9-a699-237bb21560c2
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pipe Support
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS 3500.2 Table 9.1
checkpoint-group |  |  | section | Pipe Installation
checkpoint-status |  |  | checkpoint | Pipes to be installed in straight lines, vertically and horizontally, between changes of directions.
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Pipe selection as per Specifications. Pipework sizes as per for construction drawings.
checkpoint-status |  |  | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework have been installed without damage
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued
checkpoint-status |  |  | checkpoint | Pipe/conduit compliance record/certificate
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
checkpoint-status |  |  | checkpoint | Pipes to be labelled as per Specifications and AS 3500
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with the IFC drawings, sample submission and specification
checkpoint-group |  |  | section | Sewer Access Chambers
checkpoint-status |  |  | checkpoint | Chambers to be installed as per Specifications.
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Hydrostatic tests have been successfully conducted. Supporting Records to be provided
checkpoint-status |  |  | checkpoint | Test to AS 3500.2 Section 13 Clauses 13.2 & 13.3 Hydrostatic Water Test
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records clean and flush entire installation
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records clean and flush entire installation
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
label | d7daca1c-8b63-57a1-a78b-592fb68674eb |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 002 Hydraulics – Fuel Gas |  |  |  |  | Yes | ITP 002 Hydraulics – Fuel Gas | be97bc7d-fda6-455e-bb56-9f9bf4928ffa
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade Registration
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pipe Support
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS5602 clause 4.3 tablet 4.2 & 4.3
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Pipework selection and sizes as per for construction drawings.
checkpoint-status |  |  | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Minimum separation of underground services is achieved
checkpoint-status |  |  | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued, Pipeworks have been installed without damage
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage.
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Valve Boxes
checkpoint-status |  |  | checkpoint | As per specifications and for construction drawings
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | As per specifications and for construction drawings
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with the Australian standards
checkpoint-group |  |  | section | Pits
checkpoint-status |  |  | checkpoint | As per specifications and for construction drawings AS5601
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be purged of all foreign matter as per AS5601 clause 2.4 & App. D
checkpoint-status |  |  | checkpoint | Testing to be undertaken prior to the connection of appliances
checkpoint-status |  |  | checkpoint | Testing of service as per AS5602 Appendix E. Pipe work to be tested to 1.5 times the operational pressure
checkpoint-status |  |  | checkpoint | Inground services have been inspected by the relevant authorities/consultants prior to closing up (witness/hold point)
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Photographs of installed services prior to backfill
checkpoint-status |  |  | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil
checkpoint-status |  |  | checkpoint | Bedding material is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Bedding material grading certificate to be provided
checkpoint-status |  |  | checkpoint | Trench backfill material is in accordance with the IFC drawings, sample submission and specification
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the fuel gas services scope of works. Excess spoil removed in accordance with terms of the contract
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records. All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
checkpoint-status |  |  | checkpoint | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 001 Hydraulics – Cold, Heated Water & Recycled Water |  |  |  |  | Yes | ITP 001 Hydraulics – Cold, Heated Water & Recycled Water | c63f1c56-b2c9-41fd-9188-01e752948873
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade Registration
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe and fixture locations and co-ordinate with other trades. Ensure that correct fixture information is being used
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pipes Support
checkpoint-status |  |  | checkpoint | Pipes to be supported as per AS 3500. Extra supports to be added to prevent pipe movement caused by water pressure effects
checkpoint-group |  |  | section | Valves
checkpoint-status |  |  | checkpoint | Check valves for water mark approval.
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Pipework sizes as per for construction drawings.
checkpoint-status |  |  | checkpoint | Pipework is in accordance with the IFC drawings, sample submission and specification
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Minimum separation of underground services is achieved
checkpoint-status |  |  | checkpoint | Cast Ins / Penetrations / Blockouts installed to IFC detail and signed off on pre pour ITP
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework have been installed without damage
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued
checkpoint-status |  |  | checkpoint | Pipe/conduit compliance record/certificate
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Insulation
checkpoint-no-status |  |  | checkpoint | Insulation
label | 8c610b3a-dd00-5b56-a25f-7440db2202b0 |  | note | Specifications, design documentation and issued for construction drawings
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | Underground pipework to have identification tape installed.
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with Australian Standards
checkpoint-group |  |  | section | Pits
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings (AS 3500)
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be flushed of all foreign matter. Hydrostatic pressure test before backfilling, lagging & covering. Pipework with elastomeric or RRJ shall be backfilled leaving the joints exposed. Test as per AS 3500.4. 1500 KPA for 30 min. No leaks are acceptable. Some fixtures cannot handle 1500 KPA.These items are to be disconnected for the 1500 KPA test then reconnected and tested at their maximum operation pressure for 30 min
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Backfill pipe with sand and fill balance of trench with selected excavated spoil Photographs of installed services prior to backfill Bedding material is in accordance with the IFC drawings, sample submission and specification Bedding material grading certificate to be provided Trench backfill material is in accordance with the IFC drawings, sample submission and specification
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the water services scope of works. Excess spoil removed in accordance with terms of contract
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records. All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
checkpoint-status |  |  | checkpoint | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.
checklist-sectioned |  |  | checklist | ITP 019 Hydraulics – Inground & Above Ground Sewer Rising Main Pipework |  |  |  |  | Yes | ITP 019 Hydraulics – Inground & Above Ground Sewer Rising Main Pipework | ccad6402-56d0-4672-a46f-6404e060aff0
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Check levels & falls
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Mark out pipe locations and co-ordinate with other trades
checkpoint-group |  |  | section | Excavations
checkpoint-status |  |  | checkpoint | Excavate trenches to minimal size
label | 365d2d0d-7cde-527f-96f7-be978cfcbd10 |  | note | Bed pipes on 10mm – blue metal or Sand
checkpoint-group |  |  | section | Pipework Above Ground
checkpoint-status |  |  | checkpoint | Pipework installed on Bracketing with correct spacing between clips.
checkpoint-group |  |  | section | Pipework
checkpoint-status |  |  | checkpoint | UPVC Pressure Pipework / MDPE Pipework
checkpoint-status |  |  | checkpoint | Jointing methods as per specification
checkpoint-group |  |  | section | Pipework Testing
checkpoint-status |  |  | checkpoint | Pressure UPVC and MDPE pipework to be tested to 300 kPa for a min 30 mins.
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Sewer Connection
checkpoint-status |  |  | checkpoint | Connection permit received
checkpoint-status |  |  | checkpoint | Authority procedures followed
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Backfill Compaction
checkpoint-status |  |  | checkpoint | Backfill pipe with 10mm blue metal then backfill with selected excavated material
checkpoint-group |  |  | section | Final Trim / Clean Site
checkpoint-status |  |  | checkpoint | Final clean and grade site area affected by the stormwater scope of works
checkpoint-status |  |  | checkpoint | Excess Spoil removed from site by others
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections, complete records
checklist-sectioned |  |  | checklist | ITP 005 Hydraulics – Hydraulic Pumps |  |  |  |  | Yes | ITP 005 Hydraulics – Hydraulic Pumps | dff29a1a-e319-4a65-b3ea-f25afc20fd69
checkpoint-group |  |  | section | Scope of work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Review current for construction drawing for pump locations.
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pump Selection
checkpoint-status |  |  | checkpoint | Specifications, design documentation and issued for construction drawings
checkpoint-group |  |  | section | Testing & Commissioning
checkpoint-status |  |  | checkpoint | Prior to testing the system shall be flushed of all foreign matter.
checkpoint-status |  |  | checkpoint | Pumps shall be commissioned as per the manufacturer's recommendation.
checkpoint-status |  |  | checkpoint | Pump Operation – test for correct rotation
checkpoint-status |  |  | checkpoint | Automatic Changeover – Test changeover sequence under all operational combinations
checkpoint-status |  |  | checkpoint | Level Controls – Operate pumps, measure levels and adjust if necessary.
checkpoint-status |  |  | checkpoint | Safety Controls – Simulate fault for each safety control
checkpoint-status |  |  | checkpoint | Alarms – Simulate alarm condition. Verify correct alarm raised.
checkpoint-status |  |  | checkpoint | Motor: Measure motor current and adjust overloads to suit.
checkpoint-status |  |  | checkpoint | Completion test – Provide a full operational test to verify compliance.
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractor.
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
holdpoint |  |  | signoff | Hold Point - To be signed By Fluid Contracting Site Foreman and Hansen Yunken representative
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations, Components
label | a8c20f9a-2167-580e-b223-9864fe96c8e9 |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed
checklist-sectioned |  |  | checklist | ITP 015 Hydraulics - Commissioning of Plant and Equipment |  |  |  |  | Yes | ITP 015 Hydraulics - Commissioning of Plant and Equipment | f1a68478-23b7-4ca4-a756-ee5de833371c
checkpoint-group |  |  | section | Scope of Work
checkpoint-status |  |  | checkpoint | Check documents are current & for construction
checkpoint-status |  |  | checkpoint | Location of all plant and equipment will be in accordance with for construction drawings and documentation
label | c05a4e33-c7eb-54d8-a517-b15c1a5837e9 |  | note | Plant and equipment will be in accordance with the Hydraulic Services Specifications
label | 802d677c-1605-5166-a868-cba29316a8e3 |  | note | Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
checkpoint-group |  |  | section | Competency
checkpoint-status |  |  | checkpoint | Trade registration for installation. Australian certified manufacturer for pump manufacture and commission.
checkpoint-group |  |  | section | Set Out
checkpoint-status |  |  | checkpoint | Plant and equipment locations will be determined using dimensions on construction drawings and will be coordinated with all other associated trades
checkpoint-status |  |  | checkpoint | Manufacturer's details for all plant, equipment, water meters etc will be referenced during all set out procedures
checkpoint-status |  |  | checkpoint | Existing services have been located and marked out as appropriate (eg/dial before you dig drawings) and the Services Subcontractors own services scan carried out
checkpoint-group |  |  | section | Pipe Supports
checkpoint-status |  |  | checkpoint | Pipework will be supported in accordance with AS 3500 and the Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
checkpoint-group |  |  | section | Valves
checkpoint-status |  |  | checkpoint | Valves will meet the requirements of the Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
label | 8bc0e5d0-ce73-55e2-b2ae-4b307112a95e |  | note | A detailed valve schedule will be provided for easy identification and purpose
checkpoint-group |  |  | section | Piping
checkpoint-status |  |  | checkpoint | Pipe selection and Pipework sizes as per AS 3500 and Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009, sample submission and IFC Drawings.
checkpoint-status |  |  | checkpoint | Pipe has been laid to correct RL/IL's & cover over pipes is correct depth
checkpoint-status |  |  | checkpoint | Pipe/conduit locations and alignment is in accordance with design requirements
checkpoint-status |  |  | checkpoint | Pipe/conduit penetrations in accordance with approved services location.
checkpoint-status |  |  | checkpoint | Penetrations are of suitable height and have been capped where required.
checkpoint-status |  |  | checkpoint | Pipework penetration collars/isolation is in accordance with specified requirements
checkpoint-status |  |  | checkpoint | Pipework have been installed without damage
checkpoint-status |  |  | checkpoint | Pipework Joints have been appropriately treated/glued
checkpoint-status |  |  | checkpoint | Pipe/conduit compliance record/certificate
checkpoint-status |  |  | checkpoint | Thrust blocks installed as per detail
checkpoint-status |  |  | checkpoint | Protruding services have been adequately protected from future construction damage
checkpoint-group |  |  | section | Marking & Labelling
checkpoint-status |  |  | checkpoint | In accordance with AS 3500.1 and Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
checkpoint-status |  |  | checkpoint | All marking tape is in accordance with Australian standard.
checkpoint-group |  |  | section | Valve & Pump Pits or Boex
checkpoint-status |  |  | checkpoint | In accordance with AS 3500.1 and Hydraulic Services Specification reference S09168 Revision o4, Approved for Construction, 11.12.2009
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | All Authority approvals have been received with Supporting records from Services Subcontractors
checkpoint-status |  |  | checkpoint | A register of all testing equipment and calibration certificates will be provided prior to any testing and commissioning procedures commencing
checkpoint-group |  |  | section | Clean Site
checkpoint-status |  |  | checkpoint | Final clean of the site area affected by the scope of works
checkpoint-status |  |  | checkpoint | Trade waste and excess materials are to be removed from the site area
checkpoint-group |  |  | section | Final Inspection / Completion
checkpoint-status |  |  | checkpoint | Verify all inspections and complete records
checkpoint-status |  |  | checkpoint | Services Consultant(s) field inspection report(s) - Subcontractor to address all items raised by consultants and other project stakeholder
checkpoint-group |  |  | section | Record Drawings
checkpoint-status |  |  | checkpoint | Provide Requirement as per contract documentation including Dimensioned, Surveyed, Falls, Locations and Components. Provide verifications of testing
label | f7d31ef5-eb9a-52f8-b789-9bdf487b813f |  | note | Installation aligning with IFC documentation - Any deviation from the IFC documentation must first be developed and coordinated in BIM / Revit model. Subcontractor to organise clash detection review and identify any issues to the wider team, wider team to review and sign off on any changes. As-built documentation to be prepared and submitted by Services Subcontractors within 28 days of works being installed.