## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
c97cdc40-e806-4931-8e06-fa5aec13708d | checklist | ITP - Stormwater (Infrastructure) - 203 - Rev B | itp | ITP - Stormwater (Infrastructure) - 203 - Rev B
01481da8-fe46-46c6-b6f1-c7a504fd241f | section | 1.01 Stormwater Rip Rap Materials
b0080958-183a-49b8-a359-6c77e8f3d81d | checkpoint | 1.01.1 - Rip Rap Rock Source Properties
ed51c520-efd0-5f23-b1b4-3b02d1c4d22c | note | Acceptance / Conformance Criteria - The Riprap Source shall be tested for Point Load Strength, UCS Rock, Weathering Index, Crushing Resistance, and Solid Density.
69968595-06e7-598e-b9f2-665fdb3ac983 | note | Standard / Specification - PS 16.8.3
461ffacf-96c2-59b6-91df-a67b56e2ee6d | note | Verifying Document - IANZ Lab Reports
11fc442a-b136-59c9-a806-744496c34e9c | note | Frequency - 1 per 1000m3
7c06af41-028b-5caf-b9a7-2f9a2e2ab8fb | note | Verification Activity: Activity - HP
8280b98b-c4f0-5ae4-a1c2-bc041daccfdd | note | Verification Activity: By - ENG
6bf49825-1a92-4f93-a4ff-d0560e658a05 | signoff | AUTHORITY HOLDPOINT
9e7b69ff-ae61-487b-9174-93aeaed2a9db | checkpoint | 1.01.2 - D50=150mm RipRap - Grading
49e3caaa-4bb8-5a5a-9cb5-785c054978c9 | note | Acceptance / Conformance Criteria - The D50=150mm RipRap grading for the drainage design shall be in general accordance with Auckland Council Technical Report TR2013/018
61a58a57-2ca9-526b-b672-c89973310d9f | note | Standard / Specification - PS 16.8.3
934af831-c489-560f-bcd7-4431640cfd53 | note | Verifying Document - IANZ Lab Reports
92aad84e-6604-57be-9537-7fa055d304e1 | note | Frequency - 1 per 1000m3
960d05c6-0dac-5195-b2bc-bc6a2682ae10 | note | Verification Activity: Activity - HP
8be0ce6a-3702-524c-befa-c9cd7a8873d8 | note | Verification Activity: By - ENG
0a0ac000-571f-4010-9547-4441cb8a2bed | signoff | AUTHORITY HOLDPOINT
8414e82c-a52d-44ce-ad3a-004b0b6b507b | checkpoint | 1.01.3 - D50=250mm RipRap - Grading
938c8c63-8368-5530-844b-42ed9009cf45 | note | Acceptance / Conformance Criteria - The D50=250mm RipRap grading for the drainage design shall be in general accordance with Auckland Council Technical Report TR2013/018
ce99ee5e-e318-57b7-9361-3b6ab206b67a | note | Standard / Specification - PS 16.8.3
83345cdf-dd77-5530-ae0c-5443b055e6f1 | note | Verifying Document - IANZ Lab Reports
6a74d5cf-54df-5f08-9607-46defc30e290 | note | Frequency - 1 per 1000m3
56d0f4f6-f362-5a12-bf2b-62e30d651ee2 | note | Verification Activity: Activity - HP
7b2652a1-860c-54b9-b435-435734d42b3e | note | Verification Activity: By - ENG
20975d45-040b-4743-8c7c-970580eea056 | signoff | AUTHORITY HOLDPOINT
904ea5a9-dfec-40ea-91e2-c2cd488dfaae | section | 1.02 Subsoil Drainage Materials
1be206e8-0832-4215-9f45-e256275171c4 | checkpoint | 1.02.1 - Subsoil Drainage Pipe
e329b63c-1a81-585b-b910-6a746319a8dd | note | Acceptance / Conformance Criteria - Pipes shall be high density polyethylene (HDPE) smooth bore perforated corrugated plastic pipe as shown on the Drawings and shall comply with the requirements of NZTA F/5.
af2760b4-a0e4-5564-8426-3fa2de9b5328 | note | Standard / Specification - PS 16.11.1
df6dd9ad-bd89-5880-8545-c4c9fa68d2a2 | note | Verifying Document - Datasheet
84b7f776-bfc1-52d5-bd63-14c8526c6a26 | note | Frequency - Prior to use
1486c484-2ee4-5425-946c-c25c43b5fd6c | note | Verification Activity: Activity - R
4c2e6c5e-fcdd-55fd-a235-08bc46e47856 | note | Verification Activity: By - SE
334a27e1-2dbd-4c2f-9341-382c0b745f1a | checkpoint | 1.02.2 - Filter Material
8fec64a0-0167-577e-b08a-4243b2fcd83d | note | Acceptance / Conformance Criteria - Filter material shall be placed around drainage pipe as shown on the Drawings and shall comprise no fines AP20/AP40 material.
1bde53aa-20a1-5350-ab67-2d21f9250675 | note | Standard / Specification - PS 16.11.1
9fc309e7-01cd-5cdb-8b31-4cfbcd7c7958 | note | Verifying Document - Datasheet
d32c2d74-9f54-5b21-858d-b9f855629953 | note | Frequency - Prior to use
e7a6b74b-0c95-5bf2-bd7c-ed7a45ddf5b9 | note | Verification Activity: Activity - R
87542a28-6fd1-52bb-8229-36dac650de5e | note | Verification Activity: By - SE
a5045a29-f993-40f4-a604-4f5c4399a88e | section | 1.04 Stormwater Geogrid and Geofabric
fe35b0c2-4fdf-4cef-bacf-cc050800991b | checkpoint | 1.04.1 - Geofabric
64bacd62-db26-5e45-bc4d-7a320152a0fe | note | Acceptance / Conformance Criteria - The Contractor shall submit the full details of the filter fabric they propose to use to the Engineer for approval at least two weeks before commencement of the works.
9f94f8b0-3c43-5d0c-b0f1-7cdac66c26fa | note | Standard / Specification - PS 16.29.2
46f20516-fb72-5952-8826-9aa17bdcd48e | note | Verifying Document - Datasheet
65e57ff7-1909-5ca7-acd1-a134a9f75bb0 | note | Frequency - Prior to use
9344cbe3-c963-5953-a421-85176c5cd731 | note | Verification Activity: Activity - R
9bc5ea42-7ed3-5228-936e-a8c962e1bd3f | note | Verification Activity: By - SE
bc1fabf2-8958-47e5-93f6-8a52f65079e9 | checkpoint | 1.04.2 - Biaxial Geogrid
abdecd59-daf1-5540-af0b-43ff6b2cab6c | note | Acceptance / Conformance Criteria - The biaxial geogrid shall be manufactured in accordance with a management system which complies with the requirements of BS EN ISO 9001, BS 14001. The Contractor shall submit the full details of the geogrid they propose to use for approval at least 2 weeks before commencement of the works.
9caa7e88-2243-5514-8413-49d5e3f220be | note | Standard / Specification - PS16.29.3
d5f92006-a169-5c0c-889d-cca87ad1d6b5 | note | Verifying Document - Datasheet
3544734c-e7b3-5ec2-a23a-49f61d26bfa2 | note | Frequency - Prior to use
4dd3472a-ac68-56ce-bfb1-dd5b460dd04b | note | Verification Activity: Activity - HP
922a7503-415d-5399-afe2-62e78aefadd7 | note | Verification Activity: By - ENG
0a634b94-a8b1-423e-afad-ad964255e67b | signoff | AUTHORITY HOLDPOINT
779e5a60-40a7-48ca-a7e3-ef83a1dbf1ce | section | 1.05 Bioretention Soil Media
1791e0ed-67ca-4055-ac43-c11778f1cd96 | checkpoint | 1.05.1 - Bioretention Soil Media.
1ee2d439-a201-565e-a6ed-ddaad5429063 | note | Acceptance / Conformance Criteria - Test results for soil filtration media material properties are submitted to the Engineer including ASTM F1815-06 test results, pH, clay content, organics content and material grading curve.
02725417-dfc9-54cf-babf-a175005c2274 | note | Standard / Specification - PS 16.38
f61d712f-7654-5403-9198-c5cd00cc4906 | note | Verifying Document - Datasheet
9684a641-c1b7-56eb-bb84-22e8a785e407 | note | Frequency - Prior to installation
d3db63fe-ef58-543b-8911-b23e83542b15 | note | Verification Activity: Activity - W
161435cf-49ec-567c-b315-a46cf32217ba | note | Verification Activity: By - ENG
13fc025e-b0f1-4791-91d2-13ba77eab723 | section | 2.01 Services
178c31a9-0cdc-4e09-90f4-c6e4beeb3178 | checkpoint | 2.01.1 - Existing Services
66d0f0cd-29df-5906-be66-8e3abbf86711 | note | Acceptance / Conformance Criteria - The Contractor is required to identify all known utility service crossings or encroachment, within 5m horizontally, of the proposed drainage alignments.
fbcf4875-fc7f-5e58-a154-977595759c15 | note | Standard / Specification - PS 16.5.4
6e82df01-79ba-5e45-b235-ac57b869d035 | note | Verifying Document - Survey Records
16f4b699-d83c-5bf6-83c7-05ae54252d0e | note | Frequency - Prior to excavation
87c87f35-1947-5d02-8a53-58e03b68a85a | note | Verification Activity: Activity - R
61861e83-e38f-5f1f-b0d9-b52f452f2032 | note | Verification Activity: By - SE
9d376dc2-ff54-4bf2-aa7c-3b510572a23d | checkpoint | 2.01.2 - Service Support
801b1901-bd66-506d-b1bd-4352be056f53 | note | Acceptance / Conformance Criteria - The Contractor shall support all existing services affected by the works whether these services cross-or are located alongside the excavation.
3a608ab2-f424-569f-a74b-26a01a878439 | note | Standard / Specification - PS 16.5.4
6292847d-15dd-50c7-be04-e7096244a3bc | note | Verifying Document - Site Records
05e96bea-b5af-5c89-9138-5a8c95edf34b | note | Frequency - Each Occurrence
0f12c3d6-1f05-5e14-aa94-b0a6634fa2c6 | note | Verification Activity: Activity - R
cb4af978-483a-55af-9ab9-b1a0ec31fedc | note | Verification Activity: By - SE
8c810b6d-b76a-44e0-9d88-0912c7ba7acd | checkpoint | 2.01.3 - Utility Operators Approval
16e785e7-7a2e-5969-a0d3-090445d9f025 | note | Acceptance / Conformance Criteria - Prior to commencing with any construction, the Contractor shall Obtain written approval from the relevant Utility Operators for any construction activities within the vicinity of their service(s).
8a0e4fed-4502-5e61-a815-4345a7c8bc05 | note | Standard / Specification - PS 16.5.4
9fa401fc-fd0d-589d-9918-a7a3792f3e1d | note | Verifying Document - Written Approval
37360898-8217-5a1c-bbd8-694634cad343 | note | Frequency - Prior to commencing with any construction
6cbacad2-7c41-5d82-a198-ab99289fff94 | note | Verification Activity: Activity - HP
0ca93492-e25f-5559-8259-81100788d664 | note | Verification Activity: By - ENG
5640f115-2505-466f-b489-e04bd02499c5 | signoff | AUTHORITY HOLDPOINT
eac1dc0f-07ab-4666-b424-b9444ef40156 | checkpoint | 2.01.4 - Utility Operators Requirements
958f4b4d-9f44-56be-a6ff-ce1887eba5d9 | note | Acceptance / Conformance Criteria - Prior to commencing with any construction, the Contractor shall Undertake the construction activities within the vicinity of the service in compliance with the with the relevant Utility Operator’s requirements.
a557dbb3-92dd-5f85-b72a-a29c6a2ddfb8 | note | Standard / Specification - PS 16.5.4
433320ab-d892-5470-becd-8453655bea7a | note | Verifying Document - Site Records
8fca1b9a-bbef-5df3-98be-cd502bbb20db | note | Frequency - Prior to commencing with any construction
403494d8-14ba-5d63-8a96-7540106c25b6 | note | Verification Activity: Activity - HP
e34f5205-8239-5ea7-a30c-b33ddf6e6089 | note | Verification Activity: By - ENG
72ade9f0-d5e9-4557-b242-1f113d1b6e5b | signoff | AUTHORITY HOLDPOINT
449c844d-c065-4ab6-874c-e5eed127370d | checkpoint | 2.01.5 - Protection of Pipelines / Structures During Construction
8ecad00b-3292-5653-b7da-1ac2b50a52ac | note | Acceptance / Conformance Criteria - Where construction plant is required to be operated over pipelines Table B1 of AS/NZS 3725:2007 shall apply in determination of the minimum depth of fill (cover) required. A temporary embankment, extending not less than 15m on both sides of the pipe/culvert, shall be used to provide the necessary cover.
391e6af5-6965-5702-8f4e-60133425aaab | note | Standard / Specification - PS 16.5.5
fe128e4b-6036-56be-b7df-9cc1aa735319 | note | Verifying Document - Site Records
461e579d-0724-53a9-8dc2-8bd2a298e6ee | note | Frequency - Each Occurrence
9b72a4b4-0af2-58b6-9721-6df27a9b6a9b | note | Verification Activity: Activity - R
c0e28a5b-5bd8-514a-86fc-e31026d5b438 | note | Verification Activity: By - SE
1def7eac-8bbc-47c1-b9e4-19ed6917863f | section | 2.02 Stormwater General
794e6f21-80d0-4eac-945c-e6dba29f7195 | checkpoint | 2.02.1 - Setout
1bf4a666-9999-5ff6-b922-a5aa744642d5 | note | Acceptance / Conformance Criteria - Prior to the commencement of any drainage works for a particular drainage line, the Contractor shall set out the line, level, and position of the proposed drainage line, including inlet and outlet positions and levels, and present it to the Engineer for their consideration. The Contractor shall provide at least 48 hours’ notice to the Engineer ahead of set-out and allow 48 hours for the Engineer to respond prior to commencing work.
12079106-17a6-5de0-a60b-eb9e54dca9ba | note | Standard / Specification - PS 16.6.1
be379d62-8674-5319-ade0-9e4a6c2dafd5 | note | Verifying Document - Survey Records
84240b8a-fd91-5e5c-ba91-64c248aed718 | note | Frequency - Prior to the commencement
c4d18165-5b58-578b-a4d2-f1a4443fa780 | note | Verification Activity: Activity - HP
34ecccbf-d525-503e-bfae-ccff1f837fc9 | note | Verification Activity: By - ENG
44d35b7e-3d7b-4cbb-8b42-c7750d95ac73 | signoff | AUTHORITY HOLDPOINT
65198a05-3cba-4762-a837-0d99b781db8b | checkpoint | 2.02.2 - Dealing with Water
e9fc66f2-04e2-511f-b49a-b20ffbaf4f7d | note | Acceptance / Conformance Criteria - The Contractor shall maintain all trench inverts free from flowing or accumulated water. Water arising from, or draining into, the trench shall be drained or pumped. Any sumps required shall be refilled to formation level as directed by the Engineer.
91b0dcc5-a393-51e6-8482-49fd75fb95be | note | Standard / Specification - PS 16.7.1
11dc4e4d-1498-5880-9279-23a3d293ce97 | note | Verifying Document - Site Records
b8b9eaa3-ea61-5a24-9611-06aa477a090b | note | Frequency - During Works
478d13df-d3f6-5d97-b61d-ace7d35cd77d | note | Verification Activity: Activity - S
ac42600f-f1f1-5a5b-8f6a-4fa25f5c937e | note | Verification Activity: By - SE
ae0e151b-1061-436d-a497-49d3a300dfa6 | section | 2.03 Soakage Pits and Infiltration Trench
1a5e1723-510e-43b5-9e97-0f917d28cd1e | checkpoint | 2.03.1 - Soakage Pit Sealing
00683922-e8a5-537b-b46c-8cc474d86268 | note | Acceptance / Conformance Criteria - All pipe work penetrations through manhole walls shall be sealed using Epoxy Mortar or an approved equivalent type of permanent sealant.
2609c121-2edb-55b0-bcc0-3d10812526a9 | note | Standard / Specification - PS 16.12.2.2
070334da-4e91-513e-95f1-cb4f0fcd73d5 | note | Verifying Document - Site Records
dd4acbb2-8a0e-5c37-8193-250b82ef080c | note | Frequency - Each Hole
845c8737-8539-5fac-8bd5-a93b861e50e7 | note | Verification Activity: Activity - S
95901f18-3f58-5ea2-8fcc-6b0ff0d13b8f | note | Verification Activity: By - SE
34d9a40c-05a0-4ad2-92cb-39c5d4ce2e14 | checkpoint | 2.03.3 - Soakage Pit Lids
bdf1849d-6051-54de-9052-8e549d5c0e67 | note | Acceptance / Conformance Criteria - All solid cast-iron covers and frames shall be set flush with the cross fall and grade of the surrounding finished surfaces. All grates and frames shall be haunched to lids.
849e2fad-cab1-5a1e-a747-af81594a0a12 | note | Standard / Specification - PS 16.12.2.2
3c49321a-5d3d-5305-8a56-e0f0c1bc63d1 | note | Verifying Document - Site Records
246d81d3-194d-5b4c-8761-2923b5dd7bcb | note | Frequency - Each Occurrence
b0712beb-3ef8-5da7-af62-f07cfb1285be | note | Verification Activity: Activity - S
cd55e1de-3442-5e63-b951-12de650428f2 | note | Verification Activity: By - SE
96e8a663-083c-4143-ba79-486390b38cba | checkpoint | 2.03.4 - Infiltration Trench Excavation
25fc4eee-9ec9-54db-b231-d8a258f07698 | note | Acceptance / Conformance Criteria - The trench/excavation shall be free of roots and projections or obstructions. Where over excavation has occurred, the bottom shall be brought back to grade using excavated material which is only lightly compacted in position to the same extent as the undisturbed surrounding soil. No loose soil shall be left in the excavation after restoration to finished grade.
d731cafe-bcd7-59e4-b88a-468dd5911cdf | note | Standard / Specification - PS 16.12.3.1
edf87acf-3430-5f15-8b0f-898142f59df3 | note | Verifying Document - Site Records
4a7df12e-500e-5a5a-8384-beab695f9cb4 | note | Frequency - Each Trench
f3dcde60-a34a-51af-937b-cf05642817ce | note | Verification Activity: Activity - S
9637d3fd-ad3d-59f8-a5dd-69c6c81984e4 | note | Verification Activity: By - SE
0582c6aa-0b3e-4a44-8653-e497093401c9 | checkpoint | 2.03.5 - Trench Inspection
22f13e6c-e93a-5c48-8b73-bfb68373eb01 | note | Acceptance / Conformance Criteria - All trenches in existing ground shall be inspected by the Engineer prior to commencement of laying filter cloth. Any unsuitable foundation material shall be removed at the Engineers direction.
798f196a-462e-515c-ad36-1ef6a15eabf3 | note | Standard / Specification - PS 16.12.3.1
949d74a6-8fed-59bc-91a9-275b4227e8ef | note | Verifying Document - Engineers Approval
f2a16ac2-1314-58e4-964d-9f1e7b0eeee9 | note | Frequency - Prior to commencement of laying filter cloth
54358963-ffa4-57fb-996a-e80edb8bcd7c | note | Verification Activity: Activity - HP
cdd7bad0-1f7b-5bc9-9457-513a725a0cdc | note | Verification Activity: By - ENG
ff507959-ca21-49a6-a45d-4968c15e3512 | signoff | AUTHORITY HOLDPOINT
8f408c7e-e5b0-44e0-ab5a-b9e546adbf72 | checkpoint | 2.03.6 - Groundwater
6e6a8626-602e-5034-a03c-89f42aaa8291 | note | Acceptance / Conformance Criteria - If groundwater is encountered in the trench/excavation the Contractor shall seek instructions from the Engineer on how to proceed.
8b80298c-d5b0-564f-8226-ec9c8fdc3405 | note | Standard / Specification - PS 16.12.3.1
bd244ebf-a8e9-53b5-bce4-12e0523512a2 | note | Verifying Document - Site Records
258355a4-8526-542b-a70a-4089dd418a7b | note | Frequency - Each Occurrence
44d84eca-9097-56f4-8aa9-6dc2eec4b78b | note | Verification Activity: Activity - S
5405e9ad-2cab-5988-bb7f-eea54c684ac5 | note | Verification Activity: By - SE
730e999c-a36e-4815-aeae-40be2bdb93e2 | section | 2.04 Drainage Media
72cbb0eb-cbec-4530-8075-3364acc7013c | checkpoint | 2.04.1 - Placement of Drainage Media
2acd3876-2814-5294-b4cb-780afb184c79 | note | Acceptance / Conformance Criteria - The drainage media (100-150mm rock) shall be carefully placed in the clean, excavated area after the excavated material has been removed and the excavation site cleared of potentially contaminating material and the excavation lined with filter cloth. The drainage media shall be lightly and uniformly compacted. No mechanical compaction equipment shall be used. The drainage media shall not be placed or lightly compacted if the excavation is flooded or the in-situ soils saturated.
c6852124-32da-59c0-a9f5-463d63a240ab | note | Standard / Specification - PS 16.12.3.3
71b80ea7-f056-5667-b2b9-15c4595b007f | note | Verifying Document - Site Records
5b9d840c-5703-5234-8952-dc94660f1c51 | note | Frequency - Each Area
285c0cb7-d40c-5c76-b99b-b552388573e8 | note | Verification Activity: Activity - S
eb705c9f-64a7-597b-9bb0-796129711ef4 | note | Verification Activity: By - SE
b9cdce42-195d-4b29-a1b0-241493a776cc | section | 2.05 Place D50 250mm Rip Rap
22d8c033-c0d2-4c69-9fe0-f8f01c46ee75 | checkpoint | 2.05.1 - Rip Rap Placement
5768c424-c468-59c2-b62e-e6faeb7c5209 | note | Acceptance / Conformance Criteria - The Contractor shall place D50 = 250mm size rock rip rap in areas shown on the contract drawings and as instructed by the Engineer. The rock shall be placed to ensure rock is tightly knit with no movement.
b48ae758-b97d-56cf-bc8f-fc50f86fa695 | note | Standard / Specification - PS 16.14.2
1bc46f34-4307-5584-8b96-d8f0366f71d9 | note | Verifying Document - Site Records
455f1d20-892d-545d-815d-c2d5c27d6e83 | note | Frequency - Each Area
a1576b3c-8bea-587f-adf1-f8bd8780a144 | note | Verification Activity: Activity - S
98be39bf-ce0d-534e-ba21-6284bbbf801f | note | Verification Activity: By - SE
f4d1aaa8-4c5e-46ea-b4a7-f5c57cf437b2 | section | 2.06 Rip Rap Rock Flumes
e33807d6-da9d-461b-9e64-1b3c1b4b67f5 | checkpoint | 2.06.1 - Rip Rap Placement
301e7606-6281-53da-9821-d00c0a388d17 | note | Acceptance / Conformance Criteria - The Contractor shall place D50 rock rip rap in areas shown on the contract drawings and as instructed by the Engineer. The rock shall be placed to ensure rock is tightly knit with no movement.
0b05b2c2-b1ed-5f4b-9d62-9bb5a7b66d11 | note | Standard / Specification - PS 16.17.2
95b544d6-b499-5aa9-a5b6-ece304c4054b | note | Verifying Document - Site Records
0c4008f0-48d4-5017-bc69-cbf0bebbb5d2 | note | Frequency - Each Area
4517c380-b179-5d66-911b-061ec7a235ce | note | Verification Activity: Activity - S
ba4d4a10-b8be-522a-bd14-8939622b461f | note | Verification Activity: By - SE
502d3200-acb9-49ae-8866-279a798ce736 | checkpoint | 2.06.2 - Geotextile Protection
e681a4bc-1905-551b-9e88-c6f2e5084c1e | note | Acceptance / Conformance Criteria - The contractor shall minimise the height from which rock is placed on order to reduce the risk of damage to the filter fabric layer. Rock shall not be dropped from >0.5m height.
ccd48b56-c766-578b-b820-104b4784af76 | note | Standard / Specification - PS 16.17.2
0b4420af-739b-5d2f-8ae1-2c4db4fb8bee | note | Verifying Document - Site Records
1541100d-4b39-541e-b02f-cbde5b2895da | note | Frequency - Each Area
869c4c25-3f99-5a23-ac99-d9ec198bfb03 | note | Verification Activity: Activity - S
7b2f9106-7935-5100-b94a-910016a92add | note | Verification Activity: By - SE
6bc56b2d-880b-4c8e-b305-877b470980de | checkpoint | 2.06.3 - Face Alignment
49998aa8-b9b3-5a3d-b358-a9a80483cde7 | note | Acceptance / Conformance Criteria - The face of the rock rip rap shall be placed at the gradient shown on the drawings and the termination at each end against existing slopes is to be keyed into and to approximately match the adjacent slope and placed in general accordance with ‘Section 10 Filling’ of TNZ F/1:1997 to achieve a compact mass with minimal voids and good interlock of rock fragments.
d764adbc-a917-5234-b720-73b6edc6dc2b | note | Standard / Specification - PS 16.17.2
33677346-2031-55e0-82b7-6e2c6a42e71d | note | Verifying Document - Survey Records
5fd88c47-4326-5637-b994-c2cf9343180c | note | Frequency - Each Area
83e9594f-d9c5-5f93-bba9-de272ecd86d8 | note | Verification Activity: Activity - S
40341b07-7389-5d4f-96da-53dbfe298ea7 | note | Verification Activity: By - SE
3712abd4-fd03-46a4-bc4e-8277bbf13690 | section | 2.07 Geofabric
84876bf2-1413-44b8-a7a9-61a7f767ef5a | checkpoint | 2.07.1 - Geotextile Filter Fabric Protection
1cf91409-3025-56f8-bb96-b78b48b48834 | note | Acceptance / Conformance Criteria - Construction plant shall not travel over exposed fabric. A minimum cover of 200mm of fill material shall be in place before construction plant is operated above the fabric.
03142beb-318f-5331-b339-b0ae0ca312ff | note | Standard / Specification - PS 16.18.1, PS 16.12.3.2
2713b17e-915f-589b-b87a-e5463d4dce8a | note | Verifying Document - Site Records
ac926be4-8fb9-5e4d-a78f-a34d82588562 | note | Frequency - Before Trafficking
819217b2-6a6f-517d-adef-51f55f95a8fb | note | Verification Activity: Activity - S
987adb1e-b9ee-51a9-868d-cc7ffd0c3bdd | note | Verification Activity: By - SE
d9f2c955-bc0c-41f9-b3e5-89ccf72d367e | checkpoint | 2.07.2 - Geotextile Filter Fabric Lab
f4a008a1-c5ea-59c1-9970-51383ea40069 | note | Acceptance / Conformance Criteria - Geotextile filter fabric shall have a minimum overlap of 500mm at any joins.
7120d9c4-61df-5d4b-a6f3-62987ffaf026 | note | Standard / Specification - PS 16.18.1, PS 16.12.3.2
5f4b56ee-9ec0-5e9f-987e-8df6f50683a2 | note | Verifying Document - Site Records
150f2ee7-e629-58c4-81ca-49bd555c820c | note | Frequency - Each Joint
473f2d6f-73a0-5cb6-9f0b-a68accad246f | note | Verification Activity: Activity - R
eb0630a4-3d65-5877-b10a-734584e11cfa | note | Verification Activity: By - SE
d0b02502-dc5c-4ccc-a184-f9a382da60d0 | section | 2.09 Bioretention Soil Media
b159f758-fd30-49e8-84c0-1a729bc78faa | checkpoint | 2.09.1 - Exclusion Zones (Bioretention and Infiltration Devices)
ea79dbbb-ed04-569c-88c7-a049025ed63c | note | Acceptance / Conformance Criteria - The contractor is to establish fenced-off exclusion zones at the start of the works to avoid plant / machinery tracking and over-compacting bioretention and infiltration device formations such that the hydraulic conductivity of the existing ground is not compromised. The exclusion zone shall at a minimum cover the extent of the device base area.
e8bfbd96-b782-5af4-a671-fec37809e630 | note | Standard / Specification - PS 16.39.1
dd73aa6b-a178-55dd-b8d3-f995192074c7 | note | Verifying Document - Site Records
0b023dcf-fd21-59d0-8b9c-c900bfb4beb4 | note | Frequency - At the start of the works
469776d4-5f7f-534b-9f3d-a54c35ad97fa | note | Verification Activity: Activity - R
cc639aec-651d-5fba-b472-f651ff0ab7d9 | note | Verification Activity: By - SE
075b37ac-3bef-4a57-855a-4e9796253e92 | checkpoint | 2.09.2 - Interface Finish
2915d957-1ede-5dcb-acb8-354e86ef7b62 | note | Acceptance / Conformance Criteria - Bioretention devices operation as it provides a poor interface with the media. A rough finish such as that achieved with a toothed digger bucket is preferred.
b5261bab-fe0d-5304-b197-c4e1c0827ab3 | note | Standard / Specification - PS 16.21
9c78fcd3-a935-56a2-9a74-07a330a1294a | note | Verifying Document - Site Records
6b865f49-b1d1-5379-84c9-8402f5da1fa5 | note | Frequency - Each Device
8ee066f0-602f-535b-9628-1033af3d7905 | note | Verification Activity: Activity - R
594d2c13-f2ea-58cd-ac75-d8a469d93fee | note | Verification Activity: By - SE
01ac164c-942d-4702-8122-ec95db7a123f | checkpoint | 2.09.3 - Suitability of existing soil for infiltration and bioretention areas.
3202869c-357e-50a0-9ea2-e3c4af57c48a | note | Acceptance / Conformance Criteria - Bioretention device and infiltration device formations are to be inspected by the Engineer prior to laying of bioretention or filtration media to confirm the suitability of the existing ground.
4883304a-3b1c-537f-a23f-dc3c68d97f8d | note | Standard / Specification - PS 16.38
b6ac6d71-d89c-58b0-875c-b6b15961618c | note | Verifying Document - Site Records
07e3bb87-796a-5978-8755-5c1368f70b0f | note | Frequency - prior to laying of bioretention or filtration media
e3686de0-2ad7-5efb-92f2-7df1a2b33a5d | note | Verification Activity: Activity - W
0dad7320-670e-51f0-a7a9-be3e448b595e | note | Verification Activity: By - ENG
259135e2-6ae3-4f66-aa59-cb86c3327259 | checkpoint | 2.09.4 - Bioretention Soil Media placement
6322a205-97fe-558c-99a5-498b65a47d5d | note | Acceptance / Conformance Criteria - The soil media layer is required to line the invert of all bioretention devices and placed in a single lift to 50 mm above the finished level. The finished surface shall be reasonably smooth, uniform and free of obvious hollows and humps. Care shall be taken to avoid overhandling the soi
1024781f-a243-5690-8f7e-5160ab736855 | note | Standard / Specification - PS 16.21.1
2d2cdec0-5cd3-5e6e-b691-82e209b85273 | note | Verifying Document - Site Records
86006bf1-bc38-5202-a9fa-d97f8500fbba | note | Frequency - Each Device
6c8b11f3-efaa-50a7-aee9-79e24b92eba9 | note | Verification Activity: Activity - R
13ac8479-46b2-50fb-b520-f6965f9dc46b | note | Verification Activity: By - SE
739913d5-fe38-4c3d-962b-668b1d43fa48 | checkpoint | 2.09.5 - Compaction
82858d27-f26b-5a9f-9b52-84f1c3aede5b | note | Acceptance / Conformance Criteria - The soil media shall be raked without any form of mechanical compaction.
1231bccf-6cfa-5869-b20b-bbb04f2fac87 | note | Standard / Specification - PS 16.21
1cf5299a-d6da-5570-979b-2cfd3a2461ee | note | Verifying Document - Site Records
5f91f41b-02e0-510d-a08b-1b7d46cdaaf9 | note | Frequency - Each Device
4ccd23b3-7b4b-5090-acc4-0fe319def5d9 | note | Verification Activity: Activity - R
8a6e14f0-507d-55e9-bdbf-8c32c8b9a4a6 | note | Verification Activity: By - SE
09e2a9cd-5a5a-4d99-8936-49e0ff56d921 | checkpoint | 2.09.6 - Infiltration testing
2de5f8c9-57ad-500e-bd9d-76abcd0d3070 | note | Acceptance / Conformance Criteria - Once the bioretention devices have been completed, it shall be tested by double-ring infiltrometer for permeability. The rate shall be >50 mm/hr and not exceed 500 mm/hr. Alternative testing means must be approved by the Engineer.
b44e51c0-cc2e-59db-bdcc-fdfc23528ebc | note | Standard / Specification - PS 16.21.1
c6aefa10-d21d-58c9-905b-4502fa069ed4 | note | Verifying Document - Site Records
b1e8af01-930f-5218-ba88-081bd2a36f1f | note | Frequency - Each Device upon completion
b87bf458-2245-5f7d-a602-8a168d60fcce | note | Verification Activity: Activity - I
24d9dc81-20a7-5b42-b62c-2a01d7691403 | note | Verification Activity: By - SE
1ab3f34c-710a-4ea5-b587-aad9ff1c3369 | checkpoint | 2.09.7 - Landscaping Approval
0c21bcd8-386b-5e58-84b8-0da669b2031a | note | Acceptance / Conformance Criteria - Once the media is placed the Contractor shall notify the Engineer. If the Engineer is satisfied with the soil placement, they will advise the Contractor that landscaping can commence. Stabilisation with grass seed shall be carried out within seven days once approval is obtained from the Engineer.
ebb79dd7-e602-5ea0-b3ae-19ba491e8b68 | note | Standard / Specification - PS 16.21
ea56d376-07a3-5441-9870-74010c4c2cf9 | note | Verifying Document - Engineers Approval
6cfb9749-fe8d-521d-831b-4b5844507e1d | note | Frequency - Prior to Landscaping
271201fd-676d-595d-b2e6-166a905f5481 | note | Verification Activity: Activity - HP
41c04bcd-7853-5dae-bdd3-6bce805227f8 | note | Verification Activity: By - ENG
4cccbeb5-8b51-4b30-bfa7-c65ba6827520 | signoff | AUTHORITY HOLDPOINT
80459239-fc8f-4b28-be48-f1f46684725f | section | 2.12 Rock Riprap for Erosion Protection
8a4f4103-6afc-484e-aec6-bc3dd2e7d003 | checkpoint | 2.12.1 - Geotextile fabric installation
291fb202-9852-54e8-b41b-c232517433f8 | note | Acceptance / Conformance Criteria - Geotextile fabric shall be laid directly on the existing ground to protect the liner from damage due to punctures. It is assumed that the existing ground will be sand from the existing geotechnical information provided. If this is not the case the Engineer must be notified to allow for remedial treatment prior to the placement of the geofabric.
682fc2e6-003a-5147-824f-9b747e49f694 | note | Standard / Specification - PS 16.24.6
625821e3-a2c3-5047-bae1-e0f73916972a | note | Verifying Document - Site Records
a3a17cb4-b70b-571e-9621-12d92b36463b | note | Frequency - During Placement
d61a0454-4e80-5212-9ccd-b3337a9452d4 | note | Verification Activity: Activity - R
99a17e33-9554-5f99-8e20-64ccfad25722 | note | Verification Activity: By - SE
95770dbc-e51c-498e-b1ac-59972e9c4515 | checkpoint | 2.12.2 - Impermeable liner installation
a6ad1db3-fe69-5aa3-83b0-a9079f75bf4f | note | Acceptance / Conformance Criteria - An impermeable liner is required to line the entire wetland base and batters to avoid ground stability issues near the gully embankment. Particular care should be taken to ensure water tightness around inlet and outlet structures as per the Drawing details.
4217d30e-0825-505c-9133-826d182bd685 | note | Standard / Specification - PS 16.24.5
f6b61cff-f5db-5f80-b83a-e1ba6e3bd0c4 | note | Verifying Document - Site Records
7dcf4b41-a4ed-5f25-922c-ba3da3d1d2d7 | note | Frequency - During Placement
7f9c4e22-d973-508e-9f52-eb7cc104dc59 | note | Verification Activity: Activity - R
f69ad299-3732-55e5-aae2-e4e1400572b5 | note | Verification Activity: By - SE
d86b24bb-bf5d-4f42-9baf-4ce68c497b4b | section | 2.13 Rock Riprap for Erosion Protection
c7464100-f686-42b7-a5d3-d8d993743a52 | checkpoint | 2.13.1 - Organic Material Removal
bd5f0230-d354-5689-86b3-6f2ff8cc5a6d | note | Acceptance / Conformance Criteria - Prior to placement of rock riprap, all organic material is to be removed, followed by the placement and anchorage of a Class E geotextile (in accordance with TNZ Specification F/7 Geotextile).
d1917709-b988-5fde-9426-7b3ca8e111cc | note | Standard / Specification - PS 16.25.1
9d9c7ee5-0b05-53cb-b86e-0bfbe3d04419 | note | Verifying Document - Site Records
8d87c2e8-25a5-5d5e-9270-9bc2853f475d | note | Frequency - Prior to placement of rock riprap
63f60576-dcb5-5b6f-9b21-1a6d76d93ba2 | note | Verification Activity: Activity - R
d7b7777b-23d3-53d1-92c2-9aa6066d012f | note | Verification Activity: By - SE
1cd450bd-301e-49ee-aef7-90c61305b43b | section | 2.14 Void Filled Riprap
45efcec4-5e8f-463e-a839-c0beb5e0e743 | checkpoint | 2.14.1 - Rip Rap Mixing
9ffc6c9a-59b7-5001-b3d7-21d130a156cd | note | Acceptance / Conformance Criteria - Mix the material thoroughly using additional moisture and control procedures that ensure a homogenous mixture where the fines fill the inherent voids in the riprap without displacing riprap.
cd41cac6-3d62-5618-91b2-fd82d9405e9c | note | Standard / Specification - PS 16.26.3
b748d771-414e-5a55-8538-ed83ec9d66ac | note | Verifying Document - Site Records
2eeaf6a3-854a-510d-b0c6-62a0efddfcfa | note | Frequency - Prior to Placement
d147e003-6844-5161-8d86-cc606b9fe378 | note | Verification Activity: Activity - R
a80aebeb-589b-5e4e-8ce7-2eaa5bac5969 | note | Verification Activity: By - SE
e3dc8473-8753-4716-8fed-9d19fa5b5ae5 | checkpoint | 2.14.2 - Rip Rap Placement
10584e14-ec26-55d5-a99e-29c5fa8722e7 | note | Acceptance / Conformance Criteria - Place the blended mixture of approximate 2 x D50 thickness, minimising segregation of material. Some additional mixing may be required after the initial placement where there is segregation or areas that consist of smaller void fill materials.
b75936b3-69ce-5e23-8b29-e0b2debb0861 | note | Standard / Specification - PS 16.26.4
c1078f44-8809-5fcf-b997-4a031c8795ef | note | Verifying Document - Site Records
51542473-dc3d-5180-ad1b-f964ce42c35f | note | Frequency - During Placement
2904e554-4faf-5647-9c23-4d5ac869edd2 | note | Verification Activity: Activity - R
cc8854ec-bbb2-5e63-8a65-e40bcd4ed9e8 | note | Verification Activity: By - SE
a50a7398-bfee-4aa3-a49c-559ba67e1e60 | checkpoint | 2.14.3 - Rip Rap Compaction
07a42d7c-95c7-58f7-a1f4-a52716aa86bc | note | Acceptance / Conformance Criteria - The mixture shall be consolidated by driving over it with a loader or tamping with an excavator bucket to create a tight, dense interlocking mass.
45a557c4-3239-587c-a096-d0729293c941 | note | Standard / Specification - PS 16.26.5
60450cc7-51e0-558a-b5f7-67b95f2ea893 | note | Verifying Document - Site Records
fc115791-69ac-55b9-8d96-3eec5df5f6b0 | note | Frequency - During Placement
07c3386f-cff8-545e-b2d5-b8aa18334ebc | note | Verification Activity: Activity - R
329d22bc-0c90-5d33-9407-4a0e96f73353 | note | Verification Activity: By - SE
461fb2bb-427f-4ec8-b16c-0f9a7499752d | checkpoint | 2.14.4 - Rip Rap Surface
f1549920-8523-5a10-9042-2fbe3f4c8f1a | note | Acceptance / Conformance Criteria - Where a surface layer of topsoil is specified, moist topsoil shall be placed over the void filled riprap and compacted to a dense stable state. Prior to placement of topsoil, the riprap placement must be reviewed by the Engineer. Additional topsoil shall be added to any areas that settle.
51a16737-0f53-5c19-81a7-4491415bce98 | note | Standard / Specification - PS 16.26.9
6f6fa71f-6f2d-541f-beb2-89d2df3867d4 | note | Verifying Document - Engineers Approval
70ee2724-bd00-55af-81b7-4a81196e5583 | note | Frequency - Prior to placement of topsoil
fc2b8cf1-5d94-5b4e-8609-2b58049ee50a | note | Verification Activity: Activity - HP
88a3bc8b-b01c-568b-bd86-35c4c95a3bea | note | Verification Activity: By - ENG
e24caf5b-dfdc-49fb-bf68-99f6eeaf7a69 | signoff | AUTHORITY HOLDPOINT
4ead4ed0-d695-4381-b3da-bf7d7fe7e2fd | section | 2.17 Swales
6543a3c5-db5c-4840-81f7-a101308ee1d6 | checkpoint | 2.17.1 - Swale invert
1e111f86-2812-5cf0-9705-573043e7a52b | note | Acceptance / Conformance Criteria - Swale invert shall have a uniform gradient and the line and level at any point shall not vary by more than ±20mm from the vertical set-out position and ±50mm for the horizontal set-out position
a9906f95-9b3c-58ca-98d1-46a2c0ea3d3b | note | Standard / Specification - 16.34.4
23a9d150-d78f-5f40-b13a-c477cd7850bf | note | Verifying Document - Survey
229506b9-eca3-5d50-9845-1b396476a60f | note | Frequency - Each Swale
2b0712c0-8c16-5497-acf7-391495473164 | note | Verification Activity: Activity - I
3255ead1-db2e-57cc-a751-ece462a8cef5 | note | Verification Activity: By - SV
5513e339-746c-4707-8da8-63b68a018e80 | checkpoint | 2.17.2 - Swale batters
ff71df35-12dc-5a60-8fa0-58f0c157ea3b | note | Acceptance / Conformance Criteria - Swale batters shall be uniform slope and the line and level of the top of the batter shall uniform slope and not vary by more than ±50mm from the vertical set-out position and ±50mm for the horizontal set-out position.
f0a7d388-a5e0-578f-b009-d1dd568d34c7 | note | Standard / Specification - 16.34.4
95a89954-80c9-54de-8325-36ab8317dd91 | note | Verifying Document - Survey
950c6f2a-726d-5e3c-85f5-1fd1da50002e | note | Frequency - Each Swale
23f2c3e6-f5ea-5985-b250-a37143e52f3d | note | Verification Activity: Activity - I
fff74a16-e8c8-54b8-87a7-b4d0ff24da66 | note | Verification Activity: By - SV
0f3987b4-0210-4b82-9b3c-58617f991014 | checkpoint | 2.17.3 - Grated Trench Drain
502a5a13-a457-567d-9992-22fdae8b2b19 | note | Acceptance / Conformance Criteria - Grated Trench Drains shall be installed as per Manufacturers specifications
d62df253-0272-5bfd-9ffc-b5029c2461a7 | note | Standard / Specification - PS 16.34
382762ac-21f3-5ddd-975d-b14dc1d69a8d | note | Verifying Document - Site Records
11f2d96b-76f3-5a42-beca-8b2a2f2a266f | note | Frequency - As per manufacturers specifications
781fd2d6-aaa3-5370-92dd-984cee2d91fb | note | Verification Activity: Activity - R
33aa6d8b-4c9e-5fe1-86c2-0c5f3776bedd | note | Verification Activity: By - SE
4004f9c3-1027-48f4-b64b-0decca7dfec9 | section | 2.18 As Built Records
bfe697e1-ecc1-4be6-8dbf-4285c277d29e | checkpoint | 2.18.1 - Survey Requirements - Stormwater Systems – Above ground:
9005e554-bee3-5850-a85b-af9739cce380 | note | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings: Treatment swales, wetlands, basin’s location, profile and grade. Diversion Drain location, profile, and grade. Trench excavation and invert. Line, levels and grade of kerb and channels. Rodding eye locations.
44efda96-6b2e-5997-bf9a-b74b8558cc96 | note | Standard / Specification - PS 16.33
a153d555-427f-529d-91da-788956120d6b | note | Verifying Document - Survey
a6a1ff4e-f306-5ea7-b03f-c9617fcfd0c1 | note | Frequency - All above ground Stormwater Systems
01154725-3044-531c-abb5-abeb4a81ad74 | note | Verification Activity: Activity - I
cd5bc385-5095-5866-b3af-e9525bf5da98 | note | Verification Activity: By - SV