## Drainage Installation
|  |  |  | Process Control Plan |  | LQS-QA-6007 | Approved |  | Signature
|  |  |  | Contract Name: | Lower Queen Street - Bridge Redevelopment |  | FH Engineer
|  |  |  | Procedure: | Drainage Installation |  | FH Project Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | LQS-CS-7025 |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Permits | H | Obtain Permits | As required | Document Review | Control Checklist - Digging / Excavating (incl. marking out & potholing existing services), PTW #2 Trench Excavation Inspection, Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
2 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review | IFC Drawings | Check Drawing Register | Site Engineer
3 | Survey Setout | H | Setout inlet & outlet points with inverts as required by Contractor to construct to design | Prior to commencement | Survey | Survey is correct and consistent with plans | Photo | Site Engineer
4 | Fill Material Compliance | H | Bedding, Side support and Overlay materials tested in accordance with Specifications | Prior to Installation | Document review Lab Testing | Council Water Main Specification - NTLDM | Lab Test results | Site Engineer
5 | Pipes and Precast Units (1) | H | Confirm pipes diameter, class & jointing type, as well as manholes, are as shown on the drawings, and that the pipes/pre-cast units are correct and in good condition. | Each delivery to site | Certification | Pipe - Diameter & Class, Wingwalls, Manholes, Cesspits etc. | Delivery Dockets | Site Engineer
5 | Pipes and Precast Units (2) | H | Flanges, Valve boxes, Fire Hydrants, bolts, nuts, washers shall be as in accordance with the Specifications | Prior to Installation | Document review | Council Water Main Specification - NTLDM | Delivery Dockets | Site Engineer
6 | Trenching (1) | W | Inspect trench profile and ensure it is correct to lines and levels to design. Ensure trench width is sufficient to provide enough space on either side of the pipe for compaction | Prior to Installation | Visual/Inspection | 350mm for external dia >900. DN900 for SW1, Line and level is correct | LQS-CS-4025 | Site Engineer |  |  | 350mm for external dia >900. DN900 for SW1
6 | Trenching (2) | H | Base of trenching to be inspected by Design Engineer. If undercutting required or excess water encountered, backfill material and method to be agreed before proceeding | Scalar 1/20m length of trench | Visual Inspection | Review Inferred CBRs with Design Engineer to sign-off | LQS-CS-4003 Scala Record | Site Engineer | Engineers Rep
7 | Pipe Installation (1) | W | Bedding to be placed and compacted 150mm thick bedding for pipe dia between 450 to 1500 | Prior to backfilling | Lab Testing | AP20 Bedding Clegg hammer CIV = >25 in engineered fill, and within berm (if req'd) CIV = >20 Pea Metal Bedding Photo record of bedding. | LQS-CS-4025 | Site Engineer |  |  | 150mm thick bedding for pipe dia between 450 to 1500. CIV 25 for at any point per NTLDM 5.6.4?
7 | Pipe Installation (2) | W | The pipes shall be laid with the variation between the specified invert level and invert level laid shall not exceed 5mm | Prior to backfilling | Survey | Vertical tolerance +/- 5mm, unless approved by eng rep | LQS-CS-4025 | Site Engineer | Engineers Rep |  | Eng Rep to witness prior to laying pipe
7 | Pipe Installation (3) | W | Pipe invert checks shall be carried out at least once per day with a maximum of 20m between checks. | Prior to backfilling | Survey | Vertical tolerance +/- 5mm, unless approved by eng rep | LQS-CS-4025 | Site Engineer | Engineers Rep |  | Eng Rep to witness pipe depth
7 | Pipe Installation (4) | W | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Prior to backfilling | Visual/Inspection | No defects/ gaps / pipes are aligned correctly | Photos
7 | Pipe Installation (5) | W | Backfill compacted and tested in 200mm thick layers | 1/20m length of pipe | Measure/Testing | <Subbase Layer - Clegg CIV >25 for engineered fill. In berms, Photo record. Subbase Layer - 95% MDD under carriageway for engineered fill. In berms, Photo record Basecourse Layer - 98% MDD for engineered fill. In berms, Photo record | Lab test Results/Photo/Clegg Sheet | Site Engineer |  |  | Compacted in layer not exceeding 200mm
8 | Structure installation (Manhole, Catchpit, Wingwall) (1) | W | Base of structure to be tested. Scala's to be minimum of 3 blows per 100mm | 1 test per structure | Testing | Scala minimum 3 blows/100mm | LQS-LA-4003 | Site Engineer
8 | Structure installation (Manhole, Catchpit, Wingwall) (2) | W | Structures to be installed to the design survey location and level | During structure construction | Visual/Inspection | As-Built Survey | LQS-CS-4006, As-Builts | Site Engineer
8 | Structure installation (Manhole, Catchpit, Wingwall) (3) | W | Corbals to be poured around each connection to a manhole structure | During structure construction | Visual/Inspection | Pipe joint to structure shall be encased in 200mm (min.) thick 20MPa concrete | LQS-CS-4006
8 | Structure installation (Manhole, Catchpit, Wingwall) (4) | W | As-built survey of the structure and all invert levels | Once installed | Survey | As Built Survey | As builts
9 | CCTV | H | For pipes <900mm a CCTV inspection must be completed. Pipes >900mm must be visually inspected | At completion of the works | Visual Inspection/ CCTV inspection | No Defects | Inspection Report CCTV DVD | Site Engineer
10 | Testing of Manholes & Pipelines | H | If required, testing for water tightness in the structures and low pressure air testing of the pipelines is to be carried out - test sheets to be filling in where required | One per line/structure | Measurement | Drainage Structure Water Tightness Test Record & Low Pressure Air Test Record | LQS-CS-4073 & FHIMS-CS-4074 | Site Engineer
11 | Survey As Built | H | Ensure all drainage lines comply with design prior to carrying on with next construction process | At completion of drainage line | Measurement |  | Survey receipt | Site Engineer
12 | As-builts | H | Updated drawings to be submitted with As-built line and levels recorded | At the completion of the Lot of work | Drawings | Council Water Main Specification - NTLDM | Asbuilt Drawing | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Project Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  |  |  |  | Signature: |  |  | Date: