## Relocation of Power
|  |  |  | Process Control Plan |  | LQS-QA-6090 | Approved |  | Signature
|  |  |  | Contract Name: | Lower Queen St - Bridge Redevelopment |  | FH Engineer
|  |  |  | Procedure: | Service Installation |  | FH Project Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | LQS-CS-7090 |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Permits | H | Obtain Permits | As required | Document Review | Control Checklist - Digging / Excavating (incl. marking out & potholing existing services), PTW #1 - Confined Space, PTW #2 - Trench Excavation Inspection, Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
2 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review | IFC Drawings | Check Drawing Register | Site Engineer
3 | Survey Setout | H | Set out utiliy service alignment, and depths per construction drawings | Prior to commencement | Survey | Survey is correct and consistent with plans | Photo | Site Engineer
5 | Material Compliance (1) | H | PVC ducting shall be of approved material and/or supplied by service provider | Prior to instalment | Document/Visual | Ducts are acceptable to the service providers standards | Delivery Docket/ Service Provider acceptance | Site Engineer
5 | Material Compliance (2) | H | Ensure cables, transformers and ring main units are to (service Providers) specifications | Prior to installation | Document review | As per (Power Providers) specifications | Delivery Dockets | Site Engineer
5 | Material Compliance (3) | H | Bedding material/backfill shall meet the specifications of the service provider/Specifications | Prior to installation | Document review | As per (Power Providers) specifications, NTLDM | Delivery dockets, Lab Material testing | Site Engineer
6 | Trenching & Service Installation (1) | W | Inspect trench profile and ensure it is correct to lines and levels set out by survey | Daily | Visual | Depth and line is correct as per for construction drawings | FHIMS-CS-4010 | Site Engineer
6 | Trenching & Service Installation (2) | W | 100mm thick bedding to be placed and compacted and cable laid (by other) | Prior to backfilling | Visual | >100mm of clean sand bedding | FHIMS-CS-4010 | Site Engineer
6 | Trenching & Service Installation (3) | W | As built survey at intervals of no more than 20m and at each change in direction | Prior to backfilling | Survey | As-built points spacing to be less than 20m at all times | As-Builts | Site Engineer
6 | Trenching & Service Installation (4) | W | If required, Mag slab to be installed 300mm above the cable | Prior to backfilling | Visual | Mag slab to be laid on top of clean sand layer | FHIMS-CS-4010 | Site Engineer
6 | Trenching & Service Installation (5) | W | Clean Insitu backfill material to be placed and compacted in 300mm lifts to meet (Power Providers) specification. | Every 300mm lift | Visual | <Subbase Layer - Clegg CIV >25 for engineered fill. In berms, Photo record. Subbase Layer - 95% MDD under carriageway for engineered fill. In berms, Photo record Basecourse Layer - 98% MDD for engineered fill. In berms, Photo record | Lab Test results, Clegg Hammer Checksheet | Site Engineer
7 | Directional Drilling (1) | W | PE Pipe installed by drilling to survey setout, draw wire/draw rope installed and cable pulled through pipe | Daily | Visual | Line and depth consistent with for construction drawings | Survey receipt | Site Engineer
7 | Directional Drilling (2) | W | As built survey of the PE pipe installed including depth using depths marked by drilling contractors | After duct has been installed | Survey | As-built points spacing to be less than 20m at all times | As-Builts | Site Engineer
7 | Directional Drilling (3) | W | Backfill connection pits, Sand placed to bed cabling. Clean Insitu backfill material to be placed and compacted in 300mm lifts to meet power providers specification. | As required by specification | Visual | <Subbase Layer - Clegg CIV >25 for engineered fill. In berms, Photo record. Subbase Layer - 95% MDD under carriageway for engineered fill. In berms, Photo record Basecourse Layer - 98% MDD for engineered fill. In berms, Photo record | Lab Test results,Photo | Site Engineer
8 | Feature installation (1) | W | Feature such as poles, transformers, distribution pillars installed as per IFC drawings | Daily checks | Visual | Location of feature consistent with for construction drawings | Survey receipt | Site Engineer
8 | Feature installation (2) | W | Install overhead lines to the locations shown on the drawings | Daily checks | Visual | Consistent with for construction drawings | Certificate of acceptance | Site Engineer
9 | Connection | W | Complete all jointing and carry out testing | After instalment of Cable/Ducts | Visual | Commissioning tests all pass | Confirmation Note | Site Engineer
10 | Service handover | W | Service accepted by the service provider | Completion of works | Document | Service provider approval | Certificate of acceptance | Site Engineer
11 | Abandonment (1) | W | Once the existing power line is taken out of service it shall be capped and sealed in the locations on the IFC drawings | Completion of works | Visual | Consistent with for construction drawings | As-built drawings | Site Engineer
11 | Abandonment (2) | W | Remove all other redundant items such as redundant poles, pillar boxes, overhead lines etc. | Completion of works | Visual | Site clear of redundant items | As-built drawings | Site Engineer
12 | As-builts | H | Updated drawings to be submitted with As-built line and levels recorded | At the completion of the Lot of work | Drawings | Council Water Main Specification - NTLDM, service provider secification | Asbuilt Drawing | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Project Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  |  |  |  | Signature: |  |  | Date: