## Relocation of Water Services
|  |  |  | Process Control Plan |  | LQS-QA-6092 | Approved |  | Signature
|  |  |  | Contract Name: | Lower Queen Street - Bridge Redevelopment |  | FH Engineer
|  |  |  | Procedure: | Water Services |  | FH Project Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | LQS-CS-7092 |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s) | Comments
1 | Permits | H | Obtain Permits | As required | Document Review | Control Checklist - Digging / Excavating (incl. marking out & potholing existing services), PTW #2 Trench Excavation Inspection, Notify Worksafe NZ if required. Ensure all necessary Permit to Works & Controlled Checklists are in place | Permit attached or permit number noted | Site Engineer
2 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review | IFC Drawings | Check Drawing Register | Site Engineer
3 | Survey Setout | H | Set out watermain alignment, design features and depths per construction drawings | Prior to commencement | Survey | Survey is correct and consistent with plans | Photo | Site Engineer
5 | Material Compliance (1) | H | Bedding, Side support and Overlay materials tested in accordance with Specifications | Baseline test | Document review Lab Testing | Council Water Main Specification - NTLDM | Lab Test results | Site Engineer
5 | Material Compliance (2) | H | HDPE pipe is in accordance with specifications. If Butt welded, this has been completed in accordance with Specifications and correct number of test welds completed | Prior to Installation | Document review | Council Water Main Specification - NTLDM, Project specification | PE welder Record, Delivery Dockets, Test weld cert | Site Engineer
5 | Material Compliance (3) | H | PVC pipe is in accordance with specifications. Joins shall have spigot and socket joints with rubber rings | Prior to Installation | Document review | Council Water Main Specification - NTLDM, Project specification | Photo, Delivery Dockets | Site Engineer
5 | Material Compliance (4) | H | Flanges, Valve boxes, Fire Hydrants, bolts, nuts, washers shall be as in accordance with the Specifications | Prior to Installation | Document review | Council Water Main Specification - NTLDM | Delivery Dockets | Site Engineer
5 | Material Compliance (5) |  | Concrete - ensure its in accordance with the Specifications | Prior to Installation | Document review | Council Water Main Specification - NTLDM | Delivery Dockets | Site Engineer
6 | Trenching (1) | W | Inspect trench profile and ensure it is correct to lines and levels set out by survey | Daily | Visual | Depth and line is correct as per for construction drawings | LQS-CS-4101 | Site Engineer
6 | Trenching (2) | H | Base of trenching to be inspected by Design Engineer. If underctting required, backfill material and method to be agreed before proceeding | Scalar 1/20m length of trench | Visual Inspection | Review Inferred CBRs with Design Engineer to sign-off | LQS-CS-4003 Scala Record | Site Engineer | Engineers Rep
7 | Pipe Installation (1) | W | 100mm thick bedding to be placed and compacted | Prior to backfilling | Lab Testing | AP20 Bedding Clegg hammer CIV = >35 in engineered fill, and within berm (if req'd) CIV = >25 Pea Metal Bedding Photo record of bedding. NTLDM 7.8.7 | LQS-CS-4101 | Site Engineer | Engineers Rep |  | Eng Rep to witness prior to laying pipes - Clegg CIV 35 under vehicle loaded area or 25 under non-traffice loaded area per NTLDM 7.8.7?
7 | Pipe Installation (2) | W | The pipe and fittings will be laid to within tolerance/specification. | Prior to backfilling | Visual Inspection | Council Water Main Specification - NTLDM | As-Built | Site Engineer
7 | Pipe Installation (3) | W | Pipe bends installed in the locations as per the drawings | Prior to backfilling | Visual Inspection | Consistency with Construction Drawing | Photo/As-Built | Site Engineer
7 | Pipe Installation (4) | W | Thrust blocks installed as required and per drawings | Prior to backfilling | Visual Inspection | 25 Mpa concrete unless otherwise stated, per design drawings | Delivery dockets | Site Engineer | Engineers Rep |  | Eng Rep to inspect formwork and reinforcements of thrustblocks prior the pour
7 | Pipe Installation (5) | W | Denso to be applied to all steel fittings, bolts, nuts and washers | Prior to backfilling | Visual Inspection | Council Water Main Specification - NTLDM | Photo | Site Engineer
7 | Pipe Installation (6) | W | As built survey at 20m intervals and at each change in direction, and butt weld/EF | Prior to backfilling | Survey | Council Water Main Specification - NTLDM | As-Built | Site Engineer
7 | Pipe Installation (7) | W | Approved Detector tape for Watermain to be installed 300mm above the pipe | Prior to backfilling | Visual | Council Water Main Specification - NTLDM, SD702 | LQS-CS-4101 | Site Engineer
7 | Pipe Installation (8) | W | Backfill compacted and tested in 200mm thick layers | 1/20m length of pipe | Measure/Testing | <Subbase Layer - Clegg CIV >25 for engineered fill. In berms, Photo record. Subbase Layer - 95% MDD under carriageway for engineered fill. In berms, Photo record Basecourse Layer - 98% MDD for engineered fill. In berms, Photo record | Lab test Results/Photo/Clegg Sheet | Site Engineer |  |  | Compacted in layer not exceeding 200mm
8 | Hydrants and Valves (1) | H | Fire Hydrant Lids shall be painted golden yellow. A yellow triangle shall be painted on or near the centre line of the road and RRPM. A yellow circle encircling the hydrant shall be painted if its location can be obscured by parked vehicles. | All fire hydrants | Painting | Council Water Main Specification - NTLDM, SD709 | Photo | Site Engineer
8 | Hydrants and Valves (2) | H | Marker plates on posts shall be installed near all watermain valves, if required. Valves to be painted to sepcification | All valves | Post installation | Council Water Main Specification - NTLDM, SD709 | Photo | Site Engineer
9 | Inspection and Pretesting | H | Watermain, service connections and fittings shall be flushed before testing | Prior to Testing | Visual Inspection | Council Water Main Specification - NTLDM | LQS-CS-4101 | Site Engineer
10 | Pre-commissioning (1) | H | All mains, service connections and fittings shall be pressure tested | Prior to Pre-Commissioning | Rebound Testing | -1200kPa for treated water mains - 540kPa for DN375 raw water - 645kPa for DN450 raw water pipe - 1350 kPa Wasterwater pipe (1.5 x operating pressure rule of thumb) | Test results | Site Engineer | Engineers Rep |  | 1200kPa for treated water mains and 540kPa for DN375 raw water, 645kPa for DN450 raw water pipe wastewater pipes should be pressure tested up to 1350 kPa (13.5 bar). This is 1.5 x operating pressure of 900kPa.
10 | Pre-commissioning (2) | H | Pipe sterilisation testing for the whole length. Once completed Chorinated water to be discharged | Prior to Commissioning | Residual Chlorine Test | Council Water Main Specification - NTLDM | Test results | Site Engineer
10 | Pre-commissioning (3) | H | Bacteriological Test | Prior to Commissioning | Tests | Council Water Main Specification - NTLDM. 0 E.coli present in pipe | Test results | Site Engineer
11 | Shutdown | H | Apply for Shutdown of Mains with diagram, site preparation plan and duration. Notify Council of Shutdown Commencement, carry out required work, notify Council of completion of works. | Prior to programmed work | Liaise with Council | Completed shutdown plan approved by council | Written approval from the Council | Site Engineer
12 | Tie-in and commissioning (1) | H | Connection to existing water reticulation per specifiction | During shutdown | Document review | Council Water Main Specification - NTLDM | Photos | Site Engineer
12 | Tie-in and commissioning (2) | W | Post connection inspection | Completion of works | Visual | Inspection | Site confimation | Site Engineer
13 | Abandonment | W | Remove all fittings from disused watermains if required. Capping of ends of abandoned pipes | After Tie-in | Document review | Council Water Main Specification - NTLDM | Photos | Site Engineer
14 | As-builts | H | Updated drawings to be submitted with As-built line and levels recorded | At the completion of the Lot of work | Drawings | Council Water Main Specification - NTLDM | Asbuilt Drawing | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Project Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By Design Engineer: |  |  |  |  | Signature: |  |  | Date: