## Master
INSPECTION & TEST PLAN
|  | Contract Name: |  |  |  | KEY |  | Date | Approved | Date
Perform (P)
ITP01 |  | 7059 -KAITAIA WASTEWATER OVERFLOW REDUCTION STAGE 1 |  |  |  | Review (R)
Witness (W)
Hold (H)
TASK | SPECIFICATION REFERENCE | ACTIVITY/TASK | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL | FNDC | COMMENTS
ESTABLISHMENT
Pre-Start/Site Establishment | Kaitaia Wastewater Overflow Reduction Pipeline Specification, page 7 | Visual inspection of site establishment. | FNDC | Prior to commencing works on site. | Acceptance by Engineer's Representative. | H | H
Site Clearance - Inspection of Defined Limits and Vegetation Removal | Kaitaia Wastewater Overflow Reduction Pipeline Specification, page 9 | Visual inspection of defined limits and vegetation removal. | FNDC |  | Acceptance by Engineer's Representative. | H | H
Survey Setout | Kaitaia Wastewater Overflow Reduction Pipeline Specification, page 15 | Set out the work to conform with the drawings. | UCCL | Prior to commencing each stage of work. | Acceptance by Engineer's Representative. | H | H
Service Location | Project Specification, page 16, clause 6.4 | Locate and protect existing services. Arrange with external network utility operators as required. | UCCL | Prior to commencing each stage of work. | Record of services location. Photos.
Aggregate | FNDC Engineering Standards 2023, Page 121, Clause 3.3 | Aggregate testing to comply with FNDC Engineering Standards. | FNDC | Test certificates to be provided to Engineer for approval prior to using aggregate on site. | Acceptance by Engineer's Representative. Material test certificates. | H | H
MANHOLE/PIPELINE INSTALLATION (TRENCHED)
Manhole Excavation and Bedding | FNDC Engineering Standards 2023, Sheet 39 | Visual check of excavation. Subgrade meets specification. Hardfill layer constructed as per project drawings. | UCCL | Prior to installing each manhole. | Subgrade meets minimum CBR of 5 (1.5 blows/50mm). Miniumum 150mm layer of GAP65, minimum CIV of 25. | H | H
Materials Quality | FNDC Approved Material List | Visual check for approved materials, quality and condition. | UCCL | On arrival to site, prior to using materials. | Delivery dockets, photos. | W | R
Manhole Installation | FNDC Engineering Standards 2023, Sheet 39 | Manhole installed in correct position and to correct level as per Project Drawings and FNDC EES. | UCCL | On completion of installation of each manhole. | Completed manhole installation checklist, photos. | P | R
Pipeline Excavation and Bedding | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 9. FNDC Engineering Standards 2023, Sheets 31-37 | Visual check of excavation. Lower bedding layer constructed as per project drawings. | FNDC | Prior to laying pipe. | Acceptance by Engineer's Representative. Photos. | H | H
Pipeline Installation | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 9. | Pipeline installed to correct invert levels and grade. | UCCL | On completion of each pipeline (manhole-to-mahole) prior to backfilling. | Acceptance by Engineer's Representative. As-builts drawings. Completed pipeline installation checklist, photos. | H | H
Testing of Manholes and Pipelines | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 9. | Engineer's Representative to witness testing of manholes and pipelines. | FNDC | During testing of manholes and pipelines. | Acceptance by Engineer's Representative. Testing checklists. | H | H
Sewer Connections (Household) | FNDC Engineering Standards 2023, Sheet 37 | Visual check of connection. | UCCL | On completion of each connection. | As-built drawings. Photos. | P | R
Sewer Connection (to Existing Wastewater System) | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 9. | Inspection prior to connection into exisitng wastewater system. | FNDC | On completion of installation, prior to connecting to existing wastewater system. | Acceptance by Engineer's Representative. | H | H
STORAGE TANK
Aggregate | As per Tank Design. | Aggregate certificates to comply with tank design. | UCCL | Prior to using as hardfill/backfill. | Approval by tank designer. Acceptance by Engineer's Representative. Material certificates. | H | H
Excavation to Top of Sheetpiles |  | Visual check of excavation, levels, position. | UCCL | On completion of excavation. | Photos. | P | W
Sheetpile Installation |  | Sheetpiles installed as per temporary works design. As-built taken of sheet-piles to use for periodic checks throughout construction. | UCCL | On completion of sheet piling, prior to excavtion. | Photos. | P | W
Excavation and Subgrade inside Sheetpiles | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 3. | Visual check of excavation, levels, position. Subgrade meets specification. Engineer to confirm grounding conditions and wastewater control. | FNDC | On completion of excavation, prior to placing hardfill. | Acceptance by Engeineer's Representative. | H | H
Hardfill Layer | As per Tank Design. | Visual check of hardfill layer. Hardfill layer meets specification. | UCCL |  | Confirmation from tank design Engineer. Photos. | P | W
Deadman Beams | As per Tank Design. | Deadman beams placed as per specification. | UCCL | On completion of installation of deadman beams, prior to backfilling. | As-built drawings. Photos. | P | W
Tank Installation | As per Tank Design. | Tank installed as per specification. | UCCL | On completion of installation of tank, prior to backfilling. | As-built drawings. Photos. | P | W
Tank Backfill | As per Tank Design. | Tank backfill as per specification. | UCCL | On completion of backfill. | Record of 'Vertical Diamter Measurements'. Photos. | P | W
WET WELL INSTALLATION
Pumps and Mechanical Equipment | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 4. | Engineer to approve specification prior to contractor placing supplier order. | FNDC | Prior to ordering pumps and mechanical equipment. | Acceptance by Engineer's Representative. Specifications for pumps and mechanical equipment. | R | R
Excavation and Subgrade inside Sheetpiles | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 3. | Visual check of excavation, levels, position. Subgrade meets specification. Engineer to confirm grounding conditions and wastewater control. | FNDC | On completion of excavation, prior to placing hardfill. | Acceptance by Engeineer's Representative. | H | H
Pumps and Mechanical Equipment | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 4. | Engineer to review certification and inspect installation. | FNDC | On completion of installation of pumps and mechanical equipment. | Acceptance by Engineer's Representative. | H | H
Hydrostatic Testing | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 10. | Testing done by manufacturer/supplier. Certificate to be provided with tank. | FNDC | On acceptance of tank on site. | Acceptance by Engineer's Representative. Supplier documentation. | H | H
Testing of Pumps | Kaitaia Wastewater Overflow Reduction Stage 1 Technical Specification Part B, page 10. | Witness draw-down testing of pumps. | FNDC | During commissioning of pumps. | Acceptance by Engineer's Representative. Commissioning checklist. | H | H
Electrical and SCADA | Kaitaia Wastewater Overflow Reduction Stage 1 Electrical Specification, page 20. | Review switchboard test certification and inspect the installation. | FNDC | On completion of installation of the wet well. | Acceptance by Engineer's Representative. | H | H
PAVEMENT
Aggregate | FNDC Engineering Standards 2023, Page 121, Clause 3.3 | Aggregate testing to comply with FNDC Engineering Standards. | FNDC | Test certificates to be provided to Engineer for approval prior to using aggregate on site. | Acceptance by Engineer's Representative. Material test certificates. | H | H
Compaction - Reinstate Pavement Layers | Kaitaia Wastewater Overflow Reduction Stage One Specification | Compaction of trenched pavement as per FNDC Engineering Standards Sheet 31. | FNDC | On completion of compacted pavement layers. | Acceptance by Enginner's Representative. Compaction records. Photos. | H | H
Road Re-Surfacing | Kaitaia Wastewater Overflow Reduction Stage One Specification | Pre-seal inspection. | FNDC | Prior to final road resurfacing. | Acceptance by Engineer's Representative. Supplier documentation. Photos. | H | H
Kerb and Channel/Footpaths | Kaitaia Wastewater Overflow Reduction Stage One Specification | Pre-pour inspection, inspect foundations. | FNDC | Prior to placing concrete. | Acceptance by Engineer's Represetative. Photos. | H | H