## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Below Ground Pipework Checklist - Water |  |  |  |  | Yes | QA 8 - Below Ground Pipework Checklist - Water | 14d2766c-deb6-4905-9771-49cafaa2a0b4
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits depths and trench runs.
label | 40f29d7d-0120-5e89-a77f-50955023c5c9 |  | note | As per DRG#
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | 7a601a81-a178-5389-ab08-464b5a7033ac |  | note | Spec#: AS3500
label | 53e01994-00e1-5ad6-9870-7a39edecc4dd |  | note | MDPE SDR11 PE100 PN16
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
label | 10ba4b7f-0b16-50a8-aefa-b1428be83029 |  | note | Spec#: AS3500
label | 3a1062af-a6bc-5032-a50a-47bdb3995511 |  | note | Packing sand encased pipe
checkpoint-status |  |  | checkpoint | Jointing of pipes
label | 5d978e97-0d8c-51eb-a124-0af76135aaaa |  | note | Electrofusion and/or Butt Welds
label | 04ac4e16-5f21-51c5-b0e4-c1385f068f80 |  | note | GPLQA16 form
checkpoint-status |  |  | checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
label | f16668c0-ba51-514c-8fda-63afd035b38e |  | note | GPL QA6 form completed
label | 8c445b5e-b26b-53f6-9052-d025369c627e |  | note | Water system tested to 1400 kpa regularly prior to finished surfaces are completed.
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec.
label | 6b6e5966-aa91-5be6-8423-40f93b30924c |  | note | Compacted crushed rock backfill 80% to 100% compaction
label | 7a093a69-fcab-5e43-9f9c-d8e5718044d1 |  | note | Detectable marker tape
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | 6214f64b-0928-579a-86f7-b78e056e74a7 |  | note | Ongoing
label | 746f7a87-8783-519b-b398-d56de5a7cba0 |  | note | To be provided
checklist-flat |  |  | checklist | Boiling Water Service Maintenance Log |  |  |  |  | Yes | QA 23 - Boiling Water Service Maintenance Log | 9e67c077-b65e-4ab4-8ddf-d620e75ee042
checkpoint-status |  |  | checkpoint | Boiling Water Unit Service Details
text | b3f30653-6178-506e-9db0-c86ab4fc3fdf |  | textbox | Purchased from:
text | ff0705b5-a1b1-510a-aa7a-e461a5a774d1 |  | textbox | Make:
text | a78e77ea-e373-5e4a-88a8-8b1fb7066083 |  | textbox | Model No.:
text | a1d24a33-e216-591c-895c-0b159085ad87 |  | textbox | Location:
text | e2697e52-d71d-5775-9301-bf7b11547968 |  | textbox | Room Designation:
text | 28d78b65-0d62-57b6-85c2-041a9d570d33 |  | textbox | Installed by:
text | 880f6bd0-870b-561a-90f2-36aa95480e0c |  | textbox | Installation Date:
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturers instructions
checkpoint-status |  |  | checkpoint | Does the installation appear in good working order.
checkpoint-status |  |  | checkpoint | Confirm all warning lights working correctly
checkpoint-status |  |  | checkpoint | Confirm filter is clean
checkpoint-status |  |  | checkpoint | Confirm Unit is Fully Operational
checkpoint-status |  |  | checkpoint | Commissioned By:
text | 679e3648-4bab-5088-ba86-3d3b6327e1e1 |  | textbox | Name:
text | f59ebde1-31f2-5a17-8679-ed7817fee637 |  | textbox | Date:
checklist-flat |  |  | checklist | Non-Conformance and Rectification Report |  |  |  |  | Yes | QA 9 - Non-Conformance and Rectification Report | 73cdb639-5dec-441b-acfc-7fdd572f4f7f
checkpoint-status |  |  | checkpoint | Non-Conformance and Rectification Report Details:
text | 497480bc-16f9-57d1-a38d-b53f285ead12 |  | textbox | Drawing No./Rev:
text | 6c7020c8-cb4b-5056-aedc-1eda68789ef9 |  | textbox | Zone or Grid:
text | c1b1944f-9e73-5dfc-85e7-ed80a4769931 |  | textbox | Issued To:
text | ec26a073-1fc2-5a02-a43e-1a4975f7246c |  | textbox | Item Not Conforming
text | 0344f07b-d886-595d-ac05-a2e52a3647ab |  | textbox | Reason For Non-Conformance
text | 6a8fe17b-aeec-5947-a7ad-703f786a7e75 |  | textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
text | 162acb0a-6221-5ed8-b32e-8bf9074941a4 |  | textbox | Action Required:
text | 49bb3ead-9d10-58ba-b134-b5dc0c361c05 |  | textbox | Date:
text | 41c65d3b-845e-51e2-b40e-83856850ea32 |  | textbox | Rectification:
text | b80c061a-a1e2-5ec9-a894-87917f2ade88 |  | textbox | Date:
label | 2942d0e2-7101-5037-8548-4a3587576906 |  | note | Note: Non-conformance register to be updated
checklist-flat |  |  | checklist | Stormwater Drainage Inspection Report |  |  |  |  | Yes | QA 8B - Stormwater Drainage Inspection Report | 19a2db7d-15cf-4da1-bb8d-5510d4ff941f
checkpoint-status |  |  | checkpoint | Stormwater Drainage Inspection Report Details:
text | 96534a09-78d5-566b-8e1c-bd616900d8aa |  | textbox | Spec No.:
text | 691a3f85-b396-508d-8efa-b875ee0fa6ed |  | textbox | Drawing no.:
text | b3a97a71-3ade-5cbd-af56-6bba0d0dcf33 |  | textbox | Zone:
checkpoint-status |  |  | checkpoint | Pipe Lines
text | f0081876-5cf6-5338-ac67-5f20f2359cb8 |  | textbox | Date started:
text | b7047d37-73f5-51b3-aa56-cff3da21a05f |  | textbox | Drainage Line Number:
button | 42206922-8550-505e-b6f1-25ebca54b913 |  | button | Pipe Damaged? | No,Yes
text | 6b87f441-6a74-5296-9ee3-6527a92c5422 |  | textbox | Size and Class
text | 7b89114d-5a43-5a0d-92f2-feba9d0ed240 |  | textbox | Jointing Required
label | a05abd2a-2e04-5664-992c-368b2c9edd4f |  | note | Bedding and Haunching
text | e4724d19-7eca-55e5-960b-780346b59511 |  | textbox | GPL - Initial/Date
text | d2f79eb3-0cbc-53fa-a115-32baa246211e |  | textbox | Builder - Initial/Date
label | 5724832d-4831-5e66-9f88-0f2666e7e6d8 |  | note | Backfill
text | daf9dd11-559d-5e43-92f1-8038f4cda23f |  | textbox | GPL - Initial/Date
text | f0283aee-c6b8-5ffd-b05f-ea1205d24304 |  | textbox | Builder - Initial/Date
text | a30725fa-ff75-50f3-9a99-747b51571cd5 |  | textbox | Comments
label | 21d4c3ec-faa4-5407-ab6e-ea5db3092822 |  | note | Final Sign Off (Initial & Date)
text | c554b75e-1cd7-50a1-b934-401436b07030 |  | textbox | GPL
text | 8f71769b-df8d-5a7c-be1e-094c9078a8ce |  | textbox | Builder - Initial/Date
text | 45fbabb3-bf51-568e-b94b-64c544f33f52 |  | textbox | HCC/CARDNO
checkpoint-status |  |  | checkpoint | Drainage Pits
text | 41bfac3e-e736-53f8-a3c0-b67390f7097a |  | textbox | Date Installed:
text | 8872d2a8-c6de-5d27-80ea-3ec21cdcbd16 |  | textbox | Pit Number:
text | f4d320f3-03aa-53f9-b2c0-098e79891a93 |  | textbox | Pit Base:
text | ee317b6c-3f45-54e0-8947-b251c820fb40 |  | textbox | Step Irons - GPL Initial/Date
text | 6b391512-d547-5e5b-a486-7eef0619bdd0 |  | textbox | Bedding - GPL Initial/Date
label | ca144f5a-75d9-56d5-a210-f5900948dc2d |  | note | Benching, Grouting and Patching
text | 2364d5e9-152f-52be-bf4b-cc1844ae4d93 |  | textbox | GPL - Initial/Date
text | d5fe73bf-85ab-5a4a-bf20-927ca8527627 |  | textbox | Builder - Initial/Date
label | ccbd4ec5-df79-5890-bf63-afa05fdb7700 |  | note | Placement of cover
text | 2b12ae14-47fd-5bc2-9c2d-7ab41bb11841 |  | textbox | GPL - Initial/Date
text | 60cec653-e084-5222-9f07-83b41782e285 |  | textbox | Builder - Initial/Date
text | bcd954dd-99df-5aab-801e-a58d959e3274 |  | textbox | Comments
label | 0003d9fb-8379-5766-ad9d-05f3f690c457 |  | note | Final Sign Off (Initial & Date)
text | 169ef68d-afd4-5080-8b58-fffabddf8e73 |  | textbox | GPL
text | 20d519a0-a401-5505-a07f-f42d745dd0d9 |  | textbox | Builder - Initial/Date
text | f85e9d55-97b8-5d67-8142-8c01c4722b13 |  | textbox | HCC/CARDNO
checkpoint-status |  |  | checkpoint | Compaction Test Report No.
text | b3985592-ee51-5330-9b1c-d05267d1e755 |  | textbox | Compaction Test Report No.:
checklist-flat |  |  | checklist | Fire Penetration: |  |  |  |  | Yes | Add Fire Penetration Checklist | 0ee42fe2-897b-4384-b45d-434068f7f524
checkpoint-status |  |  | checkpoint | Treatment Type
select | dda08e40-7dd9-531a-a2a2-34cae406e2c6 |  | dropdown | Treatment Type: | A1,A2,B,C,D,E,F,G,H1,H2,H3,J,K,M,N1,N2,O,P,Q,R,S,T,V
checkpoint-status |  |  | checkpoint | Photo of penetration and sticker must be taken
text | 6bebe046-7503-5351-8608-2524b69b0fd5 |  | textbox | Installed by:
text | 1f933fe7-d624-5fb9-9385-a1b250206f58 |  | textbox | Comments / Reasons why cannot complete:
checklist-flat |  |  | checklist | QA 6 - Pressure Test # |  |  |  |  | Yes | GPL QA 6 - Quality Control Pressure Test Report (CNRM) | 38940d67-03d0-486b-b988-aec75d50758a
checkpoint-status |  |  | checkpoint | Quality Control Pressure Test Report:
text | 051833c0-d828-55cb-bd3a-295bf2ec450e |  | textbox | Drawing No.:
text | 3f1c71e8-017a-5454-87e6-aa06385c9645 |  | textbox | Rev.:
button | 4c88cdf4-804e-5c38-a2d6-d148b42ed196 |  | button | Test: | Air, Water
text | 516ab3e2-4ca8-5170-8733-c1577f68d1b8 |  | textbox | Section
text | 6bd6856b-ce54-5c2b-9250-7fabf9f5e32f |  | textbox | From
text | 3dd04f38-7167-5246-b25e-bfd51dd3fed6 |  | textbox | To
label | c23827ae-a5b3-5051-9f75-39d36d7c28f8 |  | note | Specified System Working (500 kPa)
checkpoint-status |  |  | checkpoint | Specified System Test:
text | d0c4b2a8-e8b7-54b2-b0fe-400e0ac031d3 |  | textbox | Pressure (1500 kPa)
text | 64d6538e-fda9-5a8a-a4c1-b32243784777 |  | textbox | Duration (2 HRS)
checkpoint-status |  |  | checkpoint | 1st Reading
text | bb1127aa-8287-5c46-8edf-6d369c183336 |  | textbox | Time
text | 23be1de7-f15b-522b-b6c4-59d464c5a16e |  | textbox | KPA
text | e8af7a90-b785-5081-be19-c3a00a25b8c4 |  | textbox | Ambient Temp
checkpoint-status |  |  | checkpoint | 2nd Reading
text | 5a945a48-e043-5008-81e0-15cb2722afdb |  | textbox | Time
text | aaf76542-229d-523a-bc78-169bd423bfc1 |  | textbox | KPA
text | baef6a07-6769-5823-99fe-177b3e84bb34 |  | textbox | Ambient Temp
checkpoint-status |  |  | checkpoint | Test Result - Passed?
text | c1e783e5-b505-50ee-82cd-976c6baafa21 |  | textbox | Repeat
label | 627239ce-4e1f-5bd0-8952-6ff14cd6ad69 |  | note | Company: Geschke Group
label | 93aff65f-8183-5dc5-bc5a-3d614b81245e |  | note | Phone: 03 9798 1619
label | f5119d99-9ac2-587d-bcb2-c82eb5c3d065 |  | note | Address: 45 Pacific Drive, Keysborough
label | b4561904-4946-52b5-bd29-5cf0cee0ae58 |  | note | Project: Centre for National Resilience Project - Melbourne
label | bf762d1c-7c93-5397-bac3-3b155ca0b8f2 |  | note | Principal: Multiplex Constructions
checkpoint-status |  |  | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | ff0a7291-1aca-5c08-9741-7f7859d905f0 |  | button | Geschke Group Signature Sign-Off added below | Yes, No
button | 5af96a66-3772-5957-ae10-3ecdcd385bc0 |  | button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist-flat |  |  | checklist | QA (ITC) 8.1E; ITP A1.8 - Installation of Electrical Conduits Checklist |  |  |  |  | Yes | QA (ITC) 8.1E; ITP A1.8 - Installation of Electrical Conduits Checklist | 7abe6ffd-7505-45fd-8ddb-40e63a5882d9
checkpoint-status |  |  | checkpoint | Electrical Conduits Installation Report Details:
text | 976a7e37-2885-50b4-9a71-c7453141da48 |  | textbox | Spec No.:
text | 799c4ff0-c913-5754-85db-1c631f2dd348 |  | textbox | Drawing & Revision no.:
text | 9f3b30c5-77f5-5a7e-a62e-33887f23c1ce |  | textbox | Shop Drawings no:
text | f70715d2-2d1a-5b23-9d63-ec36fc1e2a50 |  | textbox | Zone:
text | c4ffe7f3-f32f-5cbc-8283-c7269893acff |  | textbox | Starting IL established:
checkpoint-status |  |  | checkpoint | Conduits Lines
text | 6d93e3ef-1594-58b2-a40e-bd23aff4f7c2 |  | textbox | Date started:
text | 83e26c5e-719d-5c80-b998-6f922396102c |  | textbox | Conduit Line Number:
button | 4131f6d0-de16-58c9-8e96-0ff10b849c24 |  | button | Bedding and Haunching | Yes,No
checkpoint-status |  |  | checkpoint | Bedding material, placement and compaction meets specification.
label | cfe5b3d6-55c5-5398-a86e-c2bca4fa4355 |  | note | Spec#: Electrical Specification
text | 76ca3871-d336-58c4-9a6c-89b045e389c7 |  | textbox | Material used:
text | 7d415809-0252-5322-ba5d-2c8423ff8642 |  | textbox | Docket #:
checkpoint-status |  |  | checkpoint | Conduit Instllation Checklist
button | 6a3e2c80-0378-5646-9dd2-d91a1893c6c9 |  | button | STOWE Conduit Installation Checklist is filled in and attached | Yes,No
checkpoint-status |  |  | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | 497055be-5465-5571-9689-f53be3c80bfd |  | button | Stowe Group Signature Sign-Off added below | Yes,No
button | 7fa0ebf5-e950-5139-bcb3-a84b181ab163 |  | button | Geschke Group Signature Sign-Off added below | Yes,No
button | b615d4e1-2ab6-5c8a-b894-043e24c537d4 |  | button | BESIX Watpac Representative Sign-Off added below | Yes,No
button | 2f62d8ef-8fc7-51e2-a37c-ad03a8e94e29 |  | button | Seqirus Representative Sign- Off added below | Yes,No
checkpoint-status |  |  | checkpoint | Backfill
label | e17dfc5b-6ed4-5b86-88a7-f47c6b53dc9d |  | note | Spec#: Electrical Specification
text | eccf9a51-c5b0-5408-8c5a-840dad0ad91b |  | textbox | Material used:
text | d5e24b82-d9fb-51c2-9350-0537d2cfefd5 |  | textbox | Docket #:
checkpoint-status |  |  | checkpoint | Compaction Test Report
text | 2b809eda-5ff8-53bf-a379-351ad2c492ad |  | textbox | Compaction Test Report No.:
checkpoint-status |  |  | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | c512ffa2-9b15-57c5-bf6d-c2d46bf9eb51 |  | button | Stowe Group Signature Sign-Off added below | Yes,No
button | 8e973650-15a0-5000-8886-56a6a84eb3e4 |  | button | Geschke Group Signature Sign-Off added below | Yes,No
checklist-flat |  |  | checklist | Quality Control Pressure Test Report |  |  |  |  | Yes | QA 6 - Quality Control Pressure Test Report | cc0048d2-1472-4f3c-83f3-0a1e820947c9
checkpoint-status |  |  | checkpoint | Quality Control Pressure Test Report:
text | 763fb90a-77bd-530a-b6df-f09df5777087 |  | textbox | Drawing No.:
text | 377238ab-017c-5bf4-a86c-fd0a05fc475c |  | textbox | Rev.:
button | ef171ad8-9030-5a90-b621-10466e7e971f |  | button | Test: | Air,Water
text | 78b5cfbc-0b1e-5857-badf-8bef5677741b |  | textbox | Section
text | e593cb21-9700-5405-9c45-7a192a0b9b52 |  | textbox | From
text | 96816a98-8b0f-5e90-9d26-582360018db8 |  | textbox | To
label | 779c7016-ce0a-5f4a-8a04-2ac7cbf79cb9 |  | note | Specified System Working
text | c1866042-532f-537a-9637-cd9a1ab947d1 |  | textbox | Pressure (KPA)
text | 2a580541-ea39-55db-b94e-93e2d5bc073e |  | textbox | Duration (HRS)
label | 752bf769-b934-51aa-af8a-8e9706d24599 |  | note | Specified System Test
text | 421be4fe-6ef0-5846-8e48-808c8cc96a3d |  | textbox | Pressure (KPA)
text | c9b007dc-a936-53c4-ab20-fe1e1a046f3a |  | textbox | Duration (HRS)
checkpoint-status |  |  | checkpoint | 1st Reading
text | 329e9c81-74de-5c4f-a364-de758d416404 |  | textbox | Time
text | 692d5b19-1191-5d41-b5ba-b6712b4cb2b2 |  | textbox | KPA
text | 65a3f29e-e8e0-5d9e-b114-84eeb16dc30c |  | textbox | Ambient Temp
checkpoint-status |  |  | checkpoint | 2nd Reading
text | c4677bc9-425a-511a-93f2-24fe2225546d |  | textbox | Time
text | 81d6c326-30e4-5390-afd9-ab54e48cb0cb |  | textbox | KPA
text | b230e7fb-2924-5453-bbae-ed90b51cd7d4 |  | textbox | Ambient Temp
checkpoint-status |  |  | checkpoint | Test Result - Passed?
text | 8a353ae8-0c9a-5e49-936a-7b86c2c57803 |  | textbox | Repeat
checkpoint-status |  |  | checkpoint | Sign Off
text | dd6f186b-67e9-5218-bc00-7f9ecceb30ff |  | textbox | Geschke Pty Ltd. Representative
text | c7fd4486-479e-5db0-905f-1c6d91cc5207 |  | textbox | Others Present
text | 92abec15-c9d1-5554-9e19-262c60d28f74 |  | textbox | Date of Satisfactory Completion
checklist-flat |  |  | checklist | QA 8 - W/RW/F-00# |  |  |  |  | Yes | GPL QA 8 Below Ground Pipework Checklist - Water, Recycled Water and Fire (CNRM) | 75d505b0-61cb-469a-aa36-762d41b6e6ae
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out of trench depths and runs
text | 50c368e2-e267-595e-916c-6e77c973ffed |  | textbox | Drawing & Revision # (or Attach photo below)
text | ee172f10-30ea-5fd6-aefc-1d32c9cc0e46 |  | textbox | Survey setout completed by
button | e6275d93-0cbe-50b2-9f34-15f21fe44c66 |  | button | Drawings attached | Yes, No
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification
label | f1002e73-0ff8-5dd2-89c5-1ea70c2c4b99 |  | note | Spec#: AS3500
text | 8b62a0c7-b7ec-5427-b0f8-2fc82279d6ab |  | textbox | Materials used
button | 8943f3c8-4d92-5c2b-a829-9fe29eed384a |  | button | Approved by Principal | Yes, No
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification
label | 52c24082-91b7-5489-8ffc-c9d211af5440 |  | note | Spec#: AS3500
label | 3f558930-55e6-5fe0-a95a-d97a30badb7e |  | note | Packing sand encased pipe
checkpoint-status |  |  | checkpoint | Jointing of pipes
label | bed56ccc-3194-52c7-b693-0fcc79ce1a2f |  | note | If either of below are selected, please reference the ITP/Attach below - As applicable
boolean | 5dddb535-0148-5c4b-9da2-f0edb4ce429e |  | tickbox | Electrofusion GPL QA 16 form
boolean | 91b13bb7-8bfd-59ee-9e69-16e4ae3b1501 |  | tickbox | Butt Welds GPL QA 25 form
checkpoint-status |  |  | checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint-status |  |  | checkpoint | Testing of pipes are carried out as required
label | 5a2b08bc-3f5a-5cb3-ab1f-7ac0ddbdea9a |  | note | If below is selected, please reference the ITP/Attach below - As applicable
boolean | 6c2403fb-a2be-5f1f-8a53-2204428a9c8a |  | tickbox | Water system hydrostatic test
boolean | 849a8533-f3af-5436-b95c-ba0574e1f182 |  | tickbox | Fire system test completed by Independent tester
checkpoint-status |  |  | checkpoint | Additional service within trench
button | 55927916-04c9-57fc-9bb6-63901dd4d8bc |  | button | Are there other services to be installed in this trench? | Yes, No
button | 236cf1c2-5cdc-5df9-967c-2bdac58479d9 |  | button | If Yes have these services been installed prior to backfill of trench? | Yes, No
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
boolean | 0060e49b-66d3-5fce-92d2-fd4219b9df37 |  | tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
boolean | 5357a94b-b5d6-5032-bf6a-f547b524dd31 |  | tickbox | 5% Stabilised Sand
label | 7c195169-860b-52b6-859b-9deb3343bdb7 |  | note | Detectable marker tape
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | 08501715-e012-50ec-a64c-2c6a44049958 |  | note | Ongoing
label | d2ace5d9-1555-5a52-93b3-28ddd404947b |  | note | To be provided
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | fbda63b9-65ab-59e8-9f51-ac780beee1e9 |  | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
label | a7ba52d3-362f-55aa-a696-553a38adaf28 |  | note | Company: Geschke Group
label | 3effaf47-2728-5f84-ba24-8add9156f65a |  | note | Phone: 03 9798 1619
label | ec9f75eb-53c1-5118-b321-8a24d3e9e5b0 |  | note | Address: 45 Pacific Drive, Keysborough
label | ac50fdf2-d5ab-53aa-8790-cdffadaf56b6 |  | note | Project: Centre for National Resilience Project - Melbourne
label | c986ec2b-0907-53b2-a369-238937f254a0 |  | note | Principal: Multiplex Constructions
checkpoint-status |  |  | checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
button | 7ed2b8ff-0f3a-5ad0-bc78-414806752c3b |  | button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | 7f06b819-7cf8-5f66-9542-144730c66932 |  | button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist-flat |  |  | checklist | QA (ITC) 8.1F; ITP A1.7 - Installation of Electrical Pits Checklist |  |  |  |  | Yes | QA (ITC) 8.1F; ITP A1.7 - Installation of Electrical Pits Checklist | bca55a20-890f-4a71-b91c-cc0c6c495231
checkpoint-status |  |  | checkpoint | Electrical Pit Installation Report Details:
text | e6cd1a78-144a-5f77-b721-62867b2addf0 |  | textbox | Pit number:
text | b936b1cc-421a-5b9a-92a8-f0731ba4f801 |  | textbox | Spec No.: Electrical Specification
text | a15b0e98-ecb2-5790-a765-54ab569dff2d |  | textbox | Drawing & Revision no.:
text | 9bc0a7a5-450e-58d3-b1ab-d0770a8b4669 |  | textbox | Shop Drawings no:
text | 87a187c6-ef50-52bf-a34c-5b134bf4e37c |  | textbox | Zone:
text | 35d41ae9-ce25-50fe-a004-d37e4d4474b7 |  | textbox | RL of the bottom of the pit
checkpoint-status |  |  | checkpoint | Bedding material, placement and compaction meets specification.
label | 4133d08c-e1c5-5803-8d14-d4b25256c01b |  | note | Spec#: Electrical Specification
text | 28a35568-01e3-5f28-8c56-71163d8561ec |  | textbox | Material used:
text | e444e53c-e650-5ff5-b127-522ddb6dcd99 |  | textbox | Docket #:
checkpoint-status |  |  | checkpoint | Pit installation
button | e7b60cac-6f4d-5431-9034-4634c8ebc0d0 |  | button | Placement of cover | Yes, No
button | 0c6de21e-0b33-52f9-b48a-b85b5aba2369 |  | button | Concreting of cover | Yes,No
checkpoint-status |  |  | checkpoint | Pit Installation Checklist
button | f0be774a-e3bc-5440-a6a8-97d48cac6ed7 |  | button | STOWE Pit Installation Checklist is filled in and attached | Yes,No
checkpoint-status |  |  | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | ddc6b497-7ac2-5287-8eac-7d708736eb3d |  | button | Stowe Group Signature Sign-Off added below | Yes,No
button | 6dc8f0db-d240-5e73-a973-554048a9beaa |  | button | Geschke Group Signature Sign-Off added below | Yes,No
button | 285d65f3-5cfb-513c-91f4-5361c1249f1f |  | button | BESIX Watpac Representative Sign-Off added below | Yes,No
button | 1afc22f3-94ff-530b-9bc5-749d13e09e1a |  | button | Seqirus Representative Sign- Off added below | Yes,No
checkpoint-status |  |  | checkpoint | Backfill
label | 5173203e-8df0-57cb-94c8-047e17628019 |  | note | Spec#: Electrical Specification
text | bdb07636-ab1d-5b69-bc1b-e8002efc6cd1 |  | textbox | Material used:
text | 75ff00f1-6588-5b38-a8d4-29c2fa12855b |  | textbox | Docket #:
checkpoint-status |  |  | checkpoint | Compaction Test Report
text | 139a0cf0-87aa-57b1-963e-c5596094e0e1 |  | textbox | Compaction Test Report No.:
checkpoint-status |  |  | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | 58852269-4222-5e76-a094-de8521a6bbbd |  | button | Stowe Group Signature Sign-Off added below | Yes,No
button | f11162a2-c5d6-5fe1-a31f-2ab7c91dde54 |  | button | Geschke Group Signature Sign-Off added below | Yes,No
checklist-flat |  |  | checklist | ITP Trench Compaction - Various Services |  |  |  |  | Yes | ITP - Trench Compaction - Various Services | 27ecf30f-6991-469c-ae2a-3040be254ce1
checkpoint-status |  |  | checkpoint | 8.01 - To assist with the requirements of not only test results but ensure supervision to assess the competency of the construction methods a Level 1 GITA tester will be on hand to express an opinion on the compliance of the work practices. Geschke Plumbing are to compact in 150mm layers with Trench Pad Foot Roller.
label | e6761e40-b5cd-5459-abb7-e85eac4c816e |  | note | STAGE / FREQUENCY: During compaction
label | cda4f2ce-2c9a-5ce6-8ece-cc0dcad2c7eb |  | note | RECORDS: Written document by Level 1 GITA tester. Geschke mark-up of backfill type, test & observation location by grid
label | 243a0fc2-133e-5bde-a079-1c30240fb722 |  | note | SPECIFICATION / STANDARD: AS 3798-2007
label | 9b836e52-e76f-5cf7-a84e-2661a8fddd66 |  | note | ACCEPTANCE CRITERIA: Geschke are to compact in 150mm layers with Trench Pad Foot Roller
label | 0baae71d-5450-58f2-a818-1ccd64ac0a3d |  | note | INSPECTION / TEST PROC: Audit Activity
label | 697e8709-c65f-5077-a162-2c8cddde9ca0 |  | note | INSPECTOR / APPROVER: Geotechnical Testing Authority. Geschke
label | 686a6865-e973-5493-9f2f-f7a5a868d60e |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 8.02 - If Stab Sand is required for back fill this will be delivered 5% stab sand as per approved material. 5% stab sand on 100 slump poured straight from the shoot
label | f6da8555-7024-5c1e-b696-ed91e9c49f6e |  | note | STAGE / FREQUENCY: Prior to installation / Each pour.
label | c0f928e5-90b1-563a-aeca-c31eccc3f025 |  | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
label | a383007a-c24d-5d47-909e-c5bdcf59c82a |  | note | ACCEPTANCE CRITERIA: Stabilised sand mix meets 100 slump direct from concrete truck shoot
label | e9d14697-8e61-51a5-9ad9-1bb363150544 |  | note | INSPECTION / TEST PROC: Document and Review
label | 2798801e-6a22-518e-83cf-49b3d894e52e |  | note | INSPECTOR / APPROVER: Foreman. Geschke.
label | f52f94e5-341b-5693-816f-41452db4492a |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 8.03 - Testing to be completed in backfilled zones with 1 test through 2 layers every 40 linear meters. We will test our trenching through 2 layers at finished height less topsoil depth. This test will be completed approx. every 40 linear meters.
label | c93b814c-c3d0-5126-a242-75f496017fba |  | note | STAGE / FREQUENCY: Prior to completion / one test every 40 linear meters
label | 8dfb8ae1-72da-5ec7-af4b-e170640db1be |  | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
label | b2e92509-9b11-5bab-9cea-97a9a172ae1a |  | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
label | 820c9b24-e47b-5778-8bed-48bfd891b652 |  | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivalent density of existing ground found adjacent to the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
label | eb9b719a-3676-55e3-bf1e-b82622b04f91 |  | note | INSPECTION / TEST PROC: Test Activity
label | 2b2f294a-748e-564d-a14c-5a112aa12598 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 7142a14c-7874-5ab4-a617-0e7d85de7db1 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 8.04 - Testing to be completed adjacent to work zone as required by digging back top soil layer and testing in ground. One test in existing ground adjacent to work zone through 2 layers at finished height less topsoil depth.
label | f7225629-caff-57fc-818a-12a2f41830de |  | note | STAGE / FREQUENCY: Prior to completion / one test as required
label | b5d3f0a5-6cc5-5dac-8e0d-f76cc80b5c91 |  | note | RECORDS: Geschke mark-up of backfill type, test & observation location by grid
label | 600c8976-e8f2-5020-a6e8-fa1f272d7770 |  | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
label | f62b7ea5-7a79-53ad-b39b-dc9a05d43225 |  | note | INSPECTION / TEST PROC: Test Activity
label | cc5d8b35-caef-515a-be2c-d0b4c0d76ada |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | abd06697-f488-5b7a-8fd2-dc742bb23963 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 8.05 - Compaction Test Results. Test Results as per above test plan.
label | afc35d1a-2d4f-5039-967a-0596d52e1e53 |  | note | STAGE / FREQUENCY: Testing as per above
label | 48e069c3-e90b-5644-b3c2-25c75b49899f |  | note | RECORDS: Standard HILF Test Certificate
label | a78e164c-ccf3-5ecd-b1b4-bbb3591ebd42 |  | note | SPECIFICATION / STANDARD: AS 1289.5.7.1 ACOR Consultants Civil Specification Section 6.12 & Table 8.1
label | cb38ff9b-48bc-54d3-9689-bf58e6a1bd0e |  | note | ACCEPTANCE CRITERIA: Rapid HILF Compaction Testing shall meet or exceed 90% or an equivariant density of existing ground found in the trench alignment. This shall include one field nuclear density test through 2 layers or between 150 - 750mm below finished level every 40 linear meters.
label | 9b873895-8268-55ce-9bcb-127a71fe6424 |  | note | INSPECTION / TEST PROC: Document and Review
label | a2899f31-7ed5-52ca-bcd6-4181d7c4b1a7 |  | note | INSPECTOR / APPROVER: Foreman. Geschke.
label | 21a3e53c-7646-50ce-9896-28bb3f85d099 |  | note | HOLD OR WITNESS POINT: Witness Point
checklist-flat |  |  | checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  |  |  |  | Yes | QA 29 Periodic Flushing / Copper Protection Test Sheet | 6fd871f0-4923-404d-87a3-a46ff9e60226
checkpoint-status |  |  | checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
label | 80e7c297-50b7-5d0b-866f-1fb9ddb7de55 |  | note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
label | d81741ec-c794-5f58-95ad-a812b36878a9 |  | note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
checkpoint-status |  |  | checkpoint | Flushing Details:
text | dba80432-6184-5118-abb0-60a9def9c585 |  | textbox | Level / building being flushed:
button | 570dae14-a5d9-5816-a08d-1f3632f279c0 |  | button | Time and Type of flushing: | Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
text | 5c90528c-6f25-5216-9e89-177c70735552 |  | textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
text | 4fd14e7f-23eb-524d-b588-c15fa5163600 |  | textbox | Start time of flushing:
text | b33f0b58-edf1-51c2-98ad-d9a86e9fb41b |  | textbox | Zone/branch to be flushed:
text | 652e9774-91c3-55fe-83c2-53f9b5e0e8aa |  | textbox | Finish time of flushing:
text | 818ee21c-2c8f-5875-acf1-cac8da47d1c8 |  | textbox | Zone/branch to be flushed:
checkpoint-status |  |  | checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
checkpoint-status |  |  | checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
checkpoint-status |  |  | checkpoint | Have you set a reminder for the next flushing of this pipework?
checkpoint-status |  |  | checkpoint | Have the hot and cold been interconnected for flushing purposes?
checkpoint-status |  |  | checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
text | f2d29014-ec27-5e96-98ef-fa7b4678ca54 |  | textbox | Date for next flushing:
text | 3e794e02-826c-5832-b41b-34920b3e5122 |  | textbox | Test completed by:
text | 7ad215f2-899c-5874-b842-20631844d69d |  | textbox | Builder Representative:
checklist-flat |  |  | checklist | Below Ground Pipework Checklist - Sewer |  |  |  |  | Yes | QA 8 - Below Ground Pipework Checklist - Sewer | a3e354cf-3cd2-44a1-8f58-f46ce04c6c87
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits depths and trench runs.
label | c9361086-e05a-53b6-8dea-dc67b362ba0d |  | note | As per DRG#
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | bbb7ff83-9750-5977-a62a-c638a1d6ad34 |  | note | Spec#: AS3500
label | c93c2f8a-b7e6-5087-ba22-3138f0a6d89c |  | note | UPVC BEP Type ISO 14001
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
label | 058ebf27-f9ab-598d-94a6-cd2b0c236eae |  | note | Spec#: AS3500
label | efec87f9-cd11-5589-8894-6f7d0af1d1a6 |  | note | 75mm Q-Minus Bedding and Encasement to top of pipe
checkpoint-status |  |  | checkpoint | Laying and jointing of pipes R.Ls and falls
label | 31379af2-dcb6-5b37-996c-69b600d27b52 |  | note | PVC solvent welded
label | d0cd148a-b809-5cab-afba-5c8a51524399 |  | note | 1:60 fall
label | 18548ed8-1e5a-5a76-bd87-25571cb4aad8 |  | note | AS3500
label | a4ad503d-d291-5b62-b618-a4aa6436da95 |  | note | RLs as per hyd drgs
checkpoint-status |  |  | checkpoint | Connections to pits and existing services
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
button | 46b0621b-9913-5855-a981-0a4d96382e79 |  | button | Air or Water? | Water,Air
label | a1ba283a-d239-51fc-a72f-6251909912a1 |  | note | Inspected and recorded by Independent Certifier or PIC
checkpoint-status |  |  | checkpoint | Mirror tests are completed if required.
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec.
label | 7d47f2a2-f0b2-5045-b631-538e4abfbe19 |  | note | Compacted crushed rock backfill 80% to 100% compaction
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | a742f916-dced-5d3a-8374-2369f82cb9f5 |  | note | Ongoing
label | 4ae5b7bc-a705-5f39-9862-7bc4dc7d0a2e |  | note | To be provided
checklist-flat |  |  | checklist | Quality Control Flow Test and Compliance Report - Safety Showers |  |  |  |  | Yes | QA 6C - Quality Control Flow Test and Compliance Report - Safety Showers | 08b2f18c-30f5-453d-89af-e83d909754dc
checkpoint-status |  |  | checkpoint | Quality Control Flow Test and Compliance Report - Safety Showers:
text | 933ec587-8d4b-525b-b8ba-65fd5d3f0d56 |  | textbox | Drawing nos/rev:
text | 2828d2dd-890a-5be1-b79e-b1848c472f8d |  | textbox | Appliance Tested:
text | 8eed1e6d-8b03-564b-a390-a16213c31189 |  | textbox | Room No.:
checkpoint-status |  |  | checkpoint | Specified System Working
text | a680c45e-b06b-593c-9687-fb3ff0e56c82 |  | textbox | Pressure:
text | 33ecb49b-bbc3-5c75-870a-69312eb9b522 |  | textbox | Flow Rate:
checkpoint-status |  |  | checkpoint | International Standard ANSI Z358.1 2004
text | 9424484e-5db9-5394-b32a-09333408d567 |  | textbox | Pressure:
text | 73866130-82f4-5b20-963a-e09484bb9a5b |  | textbox | Flow Rate:
checkpoint-status |  |  | checkpoint | Pipe Installed
text | 065b28e6-493e-537c-84c1-c64fcfd5b54f |  | textbox | Pressure set on each floor: KPA
text | f7e1956c-f240-52b7-b2ff-a3e90f9cbcc9 |  | textbox | Cold - Size:
text | 92eecc02-0b73-51c7-b484-a82537f5ed42 |  | textbox | Capable Flow Rate:
text | 802507c2-eaec-5aec-b4c5-0ab33e1da97b |  | textbox | Hot - Size:
text | 147eede4-4a41-5201-808e-222d10b5d7f3 |  | textbox | Capable Flow Rate:
checkpoint-status |  |  | checkpoint | TMV Installed
text | 71821eaf-d6c4-5879-a8c2-db5e3802722f |  | textbox | Brand:
text | fc55a191-c6ff-51bf-a010-182b72b0ecbb |  | textbox | Model:
text | 695d59fd-9ddb-5d37-9552-cdea3aa47f78 |  | textbox | Flow Rate:
text | c0d06518-1467-5694-afa6-d324ff46f8f1 |  | textbox | Temp Set:
checkpoint-status |  |  | checkpoint | Pull Lever Confirm Flow
checkpoint-status |  |  | checkpoint | Riser Valves Open
checkpoint-status |  |  | checkpoint | Safety Shower Valve Open
checkpoint-status |  |  | checkpoint | Drain Outlet not Obstructed
checkpoint-status |  |  | checkpoint | Temperature Test
label | b0bfe15d-e0e3-580f-b75e-4cdcb8bdda59 |  | note | Disconnect shower head, connect hose and extend to drain, turn on shower, test temperature.
text | 245063c4-04f0-5cdd-9f17-b2401404f3f6 |  | textbox | Temperature:
checkpoint-status |  |  | checkpoint | Sign Off
text | e6dc91d5-16d7-5480-a92f-85bb8460727d |  | textbox | Name - Geschke Pty Ltd Representative
text | 849f50a0-1643-5d7f-9a9e-e48b720c1bbe |  | textbox | Others Present
text | 0d972dea-5d4a-55d3-86a5-1beca7a2c4e1 |  | textbox | Date of Completion of Satisfactory Test
checklist-sectioned |  |  | checklist | VHH - Water Protection - |  |  |  |  | Yes | VHH - Water Protection ITP (V.090421) | eec09da5-34f0-4b15-94e6-81cae3b38d67
checkpoint-group |  |  | section | Part 1 - VHH Periodic Flushing / Copper Protection Test Sheet
checkpoint-status |  |  | checkpoint | ITP details
label | a47c0c3f-ba3d-5343-89b3-c9d48dcb12bf |  | note | Copper systems are failing in the construction industry due to issues relating to design, water quality, the management of water during construction, long term maintenance of buildings with issues arising from building management team not following protocols outlined at hand over. Stagnant water being left in both hot and cold copper pipelines have been deemed to have been a contributing factor to recent copper failures. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water
label | 1d28916f-c0b9-5b56-a63b-6e8696d5f957 |  | note | Geschke Plumbing in consultation with John Holland & AECOM have put forward a proposal of periodic flushing of the systems during construction to mitigate the stagnant water issues that have arisen in the construction industry. The purpose of this ITP is to help create a strategy to ensure water is flowing through the piping system and flushed at nominated locations
label | 31d10cf0-faa0-5586-ba19-071507a56087 |  | note | Plans to flush to be submitted to John Holland prior to any flushing occurring on site
checkpoint-status |  |  | checkpoint | Flushing Details (Flushing to be Completed with Water ONLY)
text | 7b1d1710-7b4b-51ae-8730-a9daf62f4d69 |  | textbox | Level being flushed
label | e02bf841-2c07-52d5-a32d-c28a41c6e070 |  | note | Stage of Flushing During the Project
boolean | ef70b62a-e9ad-52ba-b3e4-3b6708c8a509 |  | tickbox | 1. Initial flush after installation of pipework and prior to Quality Control Pressure Test Report (Geschke QA 6)
boolean | 1ebbe732-5f30-5d2c-9c7f-c0f8237e83d3 |  | tickbox | 2. Final flush post disinfection
boolean | 721a0b3e-8674-53a7-9f46-e70584e99fd9 |  | tickbox | 3. Periodic flushing during construction (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
boolean | 359ae6ea-f072-5bfb-af85-9b37600846b7 |  | tickbox | 4. Periodic flushing from final flush until PC (to be completed every 4 weeks in line with AS 4809 clause 6.2.9)
checkpoint-status |  |  | checkpoint | Time & Type of Flushing (As per reference table below)
boolean | d17d12ef-8873-5504-880e-de81e25b2eb3 |  | tickbox | 5. Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush
boolean | 3e8df79c-f834-5272-806c-3deb90fe3fca |  | tickbox | 6. Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)
boolean | 5158ed6e-0535-59fc-b4da-300528c7d793 |  | tickbox | 7. Short branches of copper that feed rehau do not need individual flushing
checkpoint-status |  |  | checkpoint | Which fixtures are being used to flush the system (Point of Connection & Point of Discharge)
label | cdfb0da9-8da8-561a-a7dc-55408dd2b9ca |  | note | Fixture 1
text | 9577e8cb-39b9-5d62-ac8b-3159431438cd |  | textbox | Start time of flushing
text | 6aa572e2-e41b-586d-ae60-8ec47bfae425 |  | textbox | Zone/branch to be flushed
text | 62fd0ad3-4584-506f-86ab-f7b867275f34 |  | textbox | Finish time of flushing
text | 6a3d0718-efef-5bef-b6aa-ec5651746668 |  | textbox | Zone/branch to be flushed
label | 7ce9f1cc-9f3d-56c7-b821-f7e41cc577b0 |  | note | .. ..
label | 3c9b2bbc-45a8-54d8-af7b-acac7bb42edc |  | note | Fixture 2
text | 9e7b2ae9-9f82-58ce-aaaf-7806ee5ad521 |  | textbox | Start time of flushing
text | 1add0bfd-7ea2-5b86-a3e5-e8e278228a85 |  | textbox | Zone/branch to be flushed
text | e5500dd1-6ee2-5330-9b83-3d4f8afc4845 |  | textbox | Finish time of flushing
text | 0012f34c-0c2a-55ef-a9d0-11c11087093c |  | textbox | Zone/branch to be flushed
label | 03b690ad-827b-5df0-94d0-8fc1be67b69b |  | note | .. ..
label | 715e45d7-33bf-5df6-9cab-f9dc2c9e821b |  | note | Fixture 3
text | 3b961fc4-98bf-5e11-b7fe-f58d222b2a2a |  | textbox | Start time of flushing
text | 3b45cf52-af6b-5e87-9e42-5c49a9e7e3b0 |  | textbox | Zone/branch to be flushed
text | dddf2579-34a5-5e4c-9d74-af72729fbca3 |  | textbox | Finish time of flushing
text | 11c7eee3-6580-55e1-b1b3-4236385d16db |  | textbox | Zone/branch to be flushed
label | 74ffc707-4c12-521c-8be7-c8af7eba48e4 |  | note | .. ..
label | dfc67b06-a031-5b2f-84e2-4d4fb87877dd |  | note | Fixture 4
text | ce13de99-f351-59ba-ac36-d658c7fb4f11 |  | textbox | Start time of flushing
text | efb1dc6d-0c2d-5f69-9202-2140ad900924 |  | textbox | Zone/branch to be flushed
text | 8fbd05d3-b443-5b39-b3ab-2f631976c7ef |  | textbox | Finish time of flushing
text | 17eebb25-70a0-52c7-9e0a-1559d4e52a0d |  | textbox | Zone/branch to be flushed
label | 19df8e61-1f11-51c5-a20f-f8f81462420a |  | note | .. ..
label | 99d1a2d9-e8d1-5d7b-b854-3bc2382f80c5 |  | note | Fixture 5
text | 9896504b-030c-543f-bb02-03c1e3db9dca |  | textbox | Start time of flushing
text | a478cfc2-683f-5adc-9a15-1d01ce5ed022 |  | textbox | Zone/branch to be flushed
text | 2ec13bc7-8b11-5425-94ef-e4950caa0aa4 |  | textbox | Finish time of flushing
text | 1270cdde-a99d-5cbd-9375-bbf58147bc4d |  | textbox | Zone/branch to be flushed
label | cf660ccf-2e0f-5f72-8c10-80ec6d356f57 |  | note | .. ..
checkpoint-status |  |  | checkpoint | Sign-Off - Pass once entered
label | ca622f3b-d1bd-5f3b-9e43-f9491c175c1a |  | note | Add comments/photos below as applicable
button | ef2ad896-5038-5b96-87e8-c4b0a70a2851 |  | button | a. Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated | Yes, No
button | fc5129fd-e3bd-5648-a7b5-1ae4d657f161 |  | button | b. Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case | Yes, No
button | dbca4f9f-0741-5694-8b22-1e329d0b22f2 |  | button | c. Have you set a reminder for the next flushing of this pipework | Yes, No
text | a5a2cf9c-1411-5fdf-be6c-bbd8ee514949 |  | textbox | Test completed by
text | d0dff097-67d8-5ad4-84b1-85b1c10bc2aa |  | textbox | Date for next flushing (Flushing to be performed every 4 weeks at a minimum)
holdpoint |  |  | signoff | Click to add Builders Signature(s)
checkpoint-status |  |  | checkpoint | Reference Table
label | ba92ffbf-ef7b-5d98-9be2-354484227217 |  | note | 25mm Pipe / 0.49 (L/m) / Flush for 0.15 (Mins)
label | 92c1ca36-90ff-5c84-832c-b8c414f1577b |  | note | 32mm Pipe / 0.80 (L/m) / Flush for 0.25 (Mins)
label | 98e44198-4a8a-5f20-ba53-a128e83c81a2 |  | note | 40mm Pipe / 1.26 (L/m) / Flush for 0.39 (Mins)
label | 67087260-04fc-5a9d-9d8c-272b4ab28478 |  | note | 50mm Pipe / 1.96 (L/m) / Flush for 0.61 (Mins)
label | d0b82f22-83ac-54d4-9226-7c5121c04a17 |  | note | 65mm Pipe / 3.32 (L/m) / Flush for 1.04 (Mins)
label | ece32ea9-e6f8-52ed-9908-308dea4bb8b3 |  | note | 80mm Pipe / 5.02 (L/m) / Flush for 1.57 (Mins)
label | e9731a23-b9d5-5c1b-bb1e-e1a9849e0248 |  | note | 100mm Pipe / 7.85 (L/m) / Flush for 2.46 (Mins)
label | e84c2bd9-4927-5fdb-b42a-2afb1bd9c419 |  | note | 150mm Pipe / 17.66 (L/m) / Flush for 5.53 (Mins)
label | a8ca5914-ec89-598a-a33e-5d54a2f086b3 |  | note | NOTE: The table flushing time is based on 100 metres of pipework discharging through 16mm nozzle at 350KPa
checkpoint-group |  |  | section | Part 2 - Water Quality Testing Frequency
checkpoint-status |  |  | checkpoint | Water Quality Testing Details
label | 4cad266e-f3dd-5ca8-8225-c0dd77d2e5ff |  | note | Stage of water quality testing during the project
boolean | f1323cc2-208d-5270-813d-f7ec443609b2 |  | tickbox | 1. Periodic water quality testing during construction (to be completed every 3 months)
boolean | ea7af0d4-d5a5-5951-b6cc-f7101ea08957 |  | tickbox | 2. Water quality testing post final flush
checkpoint-status |  |  | checkpoint | Sign-Off - Pass once entered
label | 38ce1d14-ee5e-5937-8518-d466ffe1d6be |  | note | Add comments/photos below as applicable
button | 5fe20241-cab8-5014-a263-4cfe4a87f95a |  | button | a. Geschke and John Holland management informed of sample / testing | Yes, No
button | 92dc9e8c-cd9c-592d-857d-241abdecce38 |  | button | b. Has the schematic / location of the sample collection been highlighted, attached, and nominated | Yes, No
button | 41ef2235-966a-5a10-a83c-69104b8b0eed |  | button | c. Sample captured as per laboratory requirements | Yes, No
button | bd7b5737-42ed-586f-bd43-5194c8d054ab |  | button | d. Time and date of sample recorded | Yes, No
text | f434af43-132e-55d4-8ba0-ca19640d884e |  | textbox | Time of Sample
text | 09ad9cd2-6420-55fd-baeb-826a49a0d75f |  | textbox | Date of Sample
text | 01329bfa-7873-5948-9989-46c05c34dc24 |  | textbox | Location of Sample
label | 94850d26-fd8e-5068-8bf2-3e4cbba33fb2 |  | note | .. ..
text | eb981d73-4fb0-5906-8813-caf839fdd903 |  | textbox | Sample collected by
text | 429d63ca-ae20-5c19-b8cf-ed9ef8cd2a9d |  | textbox | Date for next Water Quality Sample (Water quality testing to be performed every 3 months at a minimum during construction)
holdpoint |  |  | signoff | Click to add Builders Signature(s)
checkpoint-group |  |  | section | Part 3 - Disinfection of Pipework & Tank
checkpoint-status |  |  | checkpoint | Disinfection Checks - Pass once below completed
label | e6e740dc-b3cb-5901-99b4-f631a4c39b95 |  | note | Add comments/photos below as applicable
button | 52c8136b-76cb-53e7-85ed-54e63c1f35b8 |  | button | a. Geschke and John Holland management informed of disinfection with plan provided | Yes, No
button | 02f71b91-dc2f-58b7-bf4f-4dc69cae6967 |  | button | b. Has disinfection occurred for 6 hours as per AS/NZS 3500.1 appendix I | Yes, No
button | 208783e5-25c1-503b-b137-ce9e1016b2ff |  | button | c. Time and date of disinfection | Yes, No
button | 26180882-c7d8-5581-9204-90d2c73ee6d3 |  | button | d. Flush all levels and branches until chlorination levels have reached safe chlorine levels as per Australian drinking water guidelines. | Yes, No
text | 7a9959a7-ea24-5920-93d8-a57bf7313d70 |  | textbox | Time of Disinfection
text | b459ff69-10b5-5d36-a11c-b4ed70288867 |  | textbox | Date of Disinfection
label | 2283b912-d3e8-580f-a3bc-2c977a40b50f |  | note | .. ..
text | a59575c6-9598-5a37-a010-b30b6707cca6 |  | textbox | Disinfection Completed by
holdpoint |  |  | signoff | Click to add Builders Signature(s)
checklist-flat |  |  | checklist | QA 18 - Gasket Installation |  |  |  |  | Yes | QA 18 - Gasket Installation | 9c1a3d55-84ac-46d2-be71-38641acd3b2d
checkpoint-status |  |  | checkpoint | Gasket Installtion:
text | 7be172d1-9829-5a2c-b7f8-00457cfb7cc9 |  | textbox | Location/Identification:
text | f876129f-5eb4-51c8-bb9e-756b83edf312 |  | textbox | Nominal Bolt Size:
text | 9907296c-8706-5b66-9807-55d455c2d7c7 |  | textbox | Gasket Contact Surface Finish on Flange:
text | ea836f76-c300-5007-be0a-6a052b6b7f4f |  | textbox | Lubricant used:
label | 8b341548-e87e-54cd-8475-7e96e7853e4f |  | note | 1. Galvanised nuts and bolts must use good quality lubricating oil on threads
label | c956b192-1fea-588d-bb53-83472d861f51 |  | note | 2. Below Ground Galvanised nuts and bolts must denzo and plastic wrap full flange and cover bolts
label | d5e0165e-cff4-5c8d-bfea-b4a82bd73d4b |  | note | 3. Stainless steel nuts and bolts must use anti seize / molybond on threads must return 24 hrs later to tighten in sequence and required torque
label | d192a8f9-d6f4-58b4-ab1b-8a843ec0f0a5 |  | note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
label | 23edc375-619c-5ac0-9792-9449541ee315 |  | note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
label | 00b820d6-cc4c-53b3-8f3c-6c72d3b45a68 |  | note | 6. Zinc bolts, nuts and washers rust when used externally use galvanised
checkpoint-status |  |  | checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
checkpoint-status |  |  | checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
checkpoint-status |  |  | checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
checkpoint-status |  |  | checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
checkpoint-status |  |  | checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier seek from GPL foreman
checkpoint-status |  |  | checkpoint | Check gap for uniformity.
checkpoint-status |  |  | checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a Round)
checkpoint-status |  |  | checkpoint | Final Torque
text | 8c38a178-2bad-569d-8c91-4bb0a1397452 |  | textbox | Final torque*: |  | (Nm)
label | 74fb850e-4f2b-5f8a-8595-cf364cd6d87e |  | note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
label | 85b780c7-a5d6-502f-aa26-1029459226ac |  | note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
text | 9899d5d1-ecd4-5263-ab82-abcf9d1a1481 |  | textbox | Round 1 Tighten to: |  | (Nm)
text | b02ee652-b36d-5629-a550-0cfbcf597499 |  | textbox | Round 2 Tighten to: |  | (Nm)
text | 2e643e63-79ef-53a3-a263-9351b8b02708 |  | textbox | Round 3 Tighten to: |  | (Nm)
label | 6b8d6f2f-5526-5691-95cd-134f8af00f7d |  | note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
label | 0bf7c0ca-43f7-56c8-ba42-85e8487fcc21 |  | note | Final Rotational Round 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
label | 6bf8c817-4eba-5a8c-9e3c-974f59942045 |  | note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
select | cd968700-19be-54d6-8335-26348bb19bf3 |  | dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
text | 0590663a-5191-5add-8e4a-e6747fedf410 |  | textbox | Other:
text | e1bb53b7-18a6-56df-beee-b9bc27ecd4d0 |  | textbox | Where was torque information provided from:
text | a4b9afd0-2ce7-5108-b8eb-79ec7c44d92b |  | textbox | Joint Assembler Name:
holdpoint |  |  | signoff | Joint Assembler Signature
checklist-flat |  |  | checklist | Backflow Prevention Device Test Report |  |  |  |  | Yes | QA 13 - Backflow Prevention Device Test Report | 432f3297-fcda-4242-ba80-bc8fd5fbe2b6
checkpoint-status |  |  | checkpoint | Backflow Prevention Device Test Report Details:
text | f9255d70-0937-58a2-9e26-46caa0247691 |  | textbox | Owner/Occupier:
text | 70a26f95-686e-54ba-a736-a9f1895a6433 |  | textbox | Address:
label | c8b76ad6-c193-5eec-96e4-3fd710672a4e |  | note | Licence: 50043
button | dfb666b0-8e5c-5574-bb3c-48331907fe6a |  | button | Type of Test: | Annual Test, Installation Test
text | c9fb0cf7-9afd-5c56-9d49-600fbb1e86ef |  | textbox | Location of Device:
text | fc5eadc0-38a3-511e-8841-71d70f702e2b |  | textbox | Authorized Tester Name:
text | 02f19ee7-163c-561a-84d5-4345587e332b |  | textbox | Test Kit Serial No.
text | 075bfadd-bfa0-5e33-85dc-7c2dd44076e7 |  | textbox | Tester Licence No.:
text | dd7c7852-b1d4-5ab9-b169-1ee0ffcbc19e |  | textbox | Test Kit Calibration Date:
text | 4ecb3a75-84e3-5f7f-a4a7-d2bd70585df9 |  | textbox | Date of Test:
checkpoint-status |  |  | checkpoint | Device Details and Test Results
button | 5ddbe2d6-271e-5027-b9d5-099ca63cb6c6 |  | button | Permission to Isolate Water Supply | No,Yes
label | 160ccbde-f0c8-58ee-b1d3-ad55989d3340 |  | note | Device:
text | 855d08f8-d432-5eb0-929c-b356bf775d1e |  | textbox | Make:
text | c8ad756e-bbfe-5715-919b-901bb02b7ac8 |  | textbox | Size:
text | a9d69181-b549-5621-8478-3a715741a82c |  | textbox | Model No.:
text | 471269b0-1dee-52f0-a444-1f4f43d64af0 |  | textbox | Serial No.:
button | a971a94f-404b-52d7-a273-aa4161edf047 |  | button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
boolean | 9037f461-9809-5ec4-8116-84aa98d24b75 |  | tickbox | Containment Protection
boolean | e9bc88bf-963b-5389-a964-efaa3b2ca700 |  | tickbox | Individual Protection
boolean | 78fc6d43-605b-54a3-b4b1-99decc96fcaa |  | tickbox | Zone Protection
button | 6665c4fe-9946-5c1d-adab-3b568f802a23 |  | button | Strainer Installed | No,Yes
button | 45c910da-f39a-523d-a7c8-558a73224c96 |  | button | Strainer Cleaned | No,Yes
button | f741fcfe-8c15-578b-99ef-68df28942c46 |  | button | Device Type | Double Check Valve, RPZD (Reduced Pressure Zone Device)
label | 0111e824-5c83-5f31-8c73-1620084e78aa |  | note | Valve
text | 094a2ded-9128-54be-97b4-8f2c3b6bbab7 |  | textbox | Check Valve 1
text | fdf1284d-480e-5c69-acd8-ff6d7125246e |  | textbox | Check Valve 2
text | 8f3c5f7f-5650-5e06-8182-9cef3f42dd95 |  | textbox | Relief Valve
label | 52b603e7-19ef-5ce8-ace5-ce66487324cf |  | note | Testing Results
text | 27024507-4ef3-5610-9c9e-f7d822604d83 |  | textbox | Close tight at:
boolean | 3ebfd5c5-2fc8-56ee-95e5-4eead611def6 |  | tickbox | Leaked
text | 1a0c4210-e48b-5e44-8f77-e73b08dc6a38 |  | textbox | Close tight at:
boolean | 689bfbd4-e23b-5590-ad1d-0478831e8b84 |  | tickbox | Leaked
text | 325c08e4-9bcc-5311-abea-c7ce538906b6 |  | textbox | Opened at:
boolean | c9f6afeb-e85d-5c98-835b-89de412b3964 |  | tickbox | Leaked
label | 8f194669-4917-5228-9f98-96f37fbe4c31 |  | note | Reason for the device failure
boolean | 7f745c03-0bf4-5ae1-854f-4c095ff642d0 |  | tickbox | Incorrect position
boolean | a1b13c37-8c8e-56b6-819e-6031bb498e6b |  | tickbox | Incorrect installation
boolean | 585269bf-23b5-5ee7-81f1-cda7e654b959 |  | tickbox | Foreign material in the device
boolean | d9238f68-a103-59f6-9ce4-f1b71b58fc70 |  | tickbox | Spring wear damage
boolean | 436a86a9-694c-5dd5-ac74-eea585827806 |  | tickbox | Seal or Rubber Damage
boolean | e6eacad3-5617-5fc5-af2b-0fd064fa85d9 |  | tickbox | Other
text | e5fce321-84f7-5c96-8309-5b8bf20f2832 |  | textbox | Other:
label | 0e926479-3647-5814-821d-3089010b8005 |  | note | Test after maintenance
text | 0dd93b5d-394d-57be-a6c8-3b6a0438ab58 |  | textbox | Close tight at:
boolean | f6ccbea9-2b0c-5d28-bee6-204ce7aecda3 |  | tickbox | Leaked
text | 1646dc5e-849f-5245-8a23-1767ed573ca2 |  | textbox | Close tight at:
boolean | 81637666-0ab9-50c1-be2c-72ebfc0b1a7d |  | tickbox | Leaked
text | 9930ebb5-f594-557f-9d60-6c56f163b7a1 |  | textbox | Opened at:
boolean | 55afce6c-4833-5d61-918e-ad0d96e04ba3 |  | tickbox | Leaked
button | 35e0e473-97e7-5f33-8df7-8e0c71cf6d82 |  | button | Water turned back on | Yes, No
text | e0461cb7-7e8d-543c-8389-ad163b552275 |  | textbox | Describe the maintenance:
text | efb30f24-0022-5357-8bd2-b63517bb4e36 |  | textbox | Parts used in repair:
button | cca42836-21b4-5d24-966d-81f28d2bd6f4 |  | button | Is the device installed correctly | Yes, No
checkpoint-status |  |  | checkpoint | Test Result
text | 847adc8a-db65-50f6-b46d-59897dee7e9a |  | textbox | Tester Name:
text | 644aaa83-bd25-5f8f-8d26-48e12f053c86 |  | textbox | Date:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Commissioning Test Report |  |  |  |  | Yes | QA 7 - Commissioning Test Report | 169223b9-5755-47d4-873e-9b16f6aea576
checkpoint-status |  |  | checkpoint | Commissioning Test Report:
text | d327703b-f3ba-539b-b251-1bdae31b11c9 |  | textbox | Zone/Grid:
text | 8ae0555c-198f-58d7-96f1-34792d52d64d |  | textbox | Drawing No.:
text | 036bd35e-308e-50b4-83a8-10b735e5014c |  | textbox | Rev.:
checkpoint-status |  |  | checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
label | 20eb13e0-a11b-584b-9ebd-a15417a134c9 |  | note | Test:
label | 3db11513-05c7-532b-bf55-bbe4827a2d9d |  | note | Performance Test CL 2.20
label | 0d887cae-55e9-588e-b235-627fdc5d12a2 |  | note | Fill fixture with water remove plug
label | 53e6629a-e167-5ba9-abb0-d6d8c9c0032f |  | note | Test for:
label | 648a4c5e-2393-5020-8f35-eddfe179e4a9 |  | note | Leaks
label | 013055b0-bd75-5aa6-92df-0cac740afe59 |  | note | Loss of water
label | d293626f-d41b-5f0d-a1e7-4d20db791d6a |  | note | Seal in Trap
label | 133d001f-2654-5fff-bbc6-13c0a0704435 |  | note | Induce siphonage in trap of adjacent fixture
label | 20c8db35-41ba-50cb-b99e-5f79d25f9629 |  | note | Complete draining of fixture
text | 31b8d3d0-2c0d-527d-a988-2732a1665c5f |  | textbox | OK:
text | 7316e753-a568-52c8-ad94-1fe21ca06772 |  | textbox | Not OK:
checkpoint-status |  |  | checkpoint | Item: Water Supply
label | 67c87bc5-d6b0-5c1d-9155-8433a522d136 |  | note | Test:
label | 2d614b85-72c4-5b5c-adfc-d0c3c663cca9 |  | note | Performance Test CL 2.20
label | b250e969-b551-5d80-be4b-dffa7693ca9a |  | note | Check for adequate water volume.
label | 73abf86f-25d8-595d-b0a6-75317c670dd1 |  | note | Flush out pipework
label | 452b504a-081d-59c2-ad5c-10618af31089 |  | note | Clean aerator
label | ae730b29-0279-579f-8f30-919295fd7d51 |  | note | Water hammer
text | 30e248a3-9146-5ac6-ab8b-e9ce68ed56dc |  | textbox | OK:
text | ecd810a2-8f89-5453-95ae-8d9c6982aae1 |  | textbox | Not OK:
checkpoint-status |  |  | checkpoint | Item: Flush Performance
label | c9949532-2826-5289-8b56-aab0ff1a7b0c |  | note | Test:
label | b843bc61-cc18-5cbf-9683-a9b62bfc4e59 |  | note | Performance Test
label | 0f892e15-28b1-5230-9deb-3ac3e1966196 |  | note | Check for:
label | 38ece3ca-011e-5795-9208-065bd616d4c6 |  | note | Water Volume
label | dc85abcd-fc9b-50da-a62b-2e6fe40476c8 |  | note | Duration of flush
label | 0aee1722-0560-553f-bb4c-bf1ee62c2a5e |  | note | Flush out pipework
label | 9ae2a9d6-01d8-5d88-8008-cdbb6dee0b7d |  | note | Water hammer
text | 3c4f2bd7-2a10-5147-bbe5-c1f81fb7673f |  | textbox | OK:
text | db3a6357-1846-5330-9f4f-e5142d47ff66 |  | textbox | Not OK:
checkpoint-status |  |  | checkpoint | Other
checklist-flat |  |  | checklist | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review |  |  |  |  | Yes | ITP - Sewer Rising Main Sample Excl. Backfill ACOR Review | 2ee6c9a9-070b-407f-8fe8-74f574f3ae72
checkpoint-status |  |  | checkpoint | 1. Approve specialist subcontractor
label | 20a92ea7-d3e4-5b36-b5ad-e6f51f729ff4 |  | note | STAGE / FREQUENCY: Prior to awarding subcontract
label | cee580cb-2a38-5177-9072-b1372cf465a5 |  | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
label | d135b6fd-e847-5da0-853a-7d0fa2b2061b |  | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
label | 9a32b4cd-75a2-5d0a-92ea-307e8e9caa5e |  | note | INSPECTION / TEST PROC: Document
label | e4b8f7b3-6f44-51ac-b8b5-0888ba1adf28 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 9c0711f2-ac2a-557a-be57-55a819b8409b |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 2. Approve Samples
label | c9f9ac04-8923-5f00-86ce-4baffea66ecc |  | note | STAGE / FREQUENCY: Prior to ordering materials
label | e3a463c5-6c51-5d7d-a8fb-9b63ee11c9c8 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | 26e8510b-7ab2-5a1a-b61b-c0a32e61e789 |  | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
label | 88f40b6f-04fb-5a47-b5cd-20a3bb0550f6 |  | note | INSPECTION / TEST PROC: Document and Review
label | 493893ca-16a4-5402-a77d-84ecf244af37 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 8fbb0330-143d-5b43-ba26-b340c6b16832 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 3. Approve technical details
label | d999d84a-c3d9-5063-a790-f0672236e75b |  | note | STAGE / FREQUENCY: Prior to ordering equipment
label | db34993e-4374-5461-94e5-ceb9b4b32d18 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | 8d93dc7e-10a6-529b-bc0f-9922fd673cde |  | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
label | 35b45e72-dffb-54fc-b1ba-880142997ca2 |  | note | INSPECTION / TEST PROC: Document and Review
label | 096b54ff-5079-5a6b-8a8c-ed7c6c295ab9 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 7acbd227-5d7e-53f2-9f67-711562dce1a7 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4. Approve shop drawings
label | b6c8b376-a095-5fe5-b768-c032a5a52891 |  | note | STAGE / FREQUENCY: Prior to commencement
label | b17f7492-a1f4-524a-9254-a3479c8c2e4d |  | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
label | a2bad438-ff6f-5157-a9ec-e5e6ffa0ede7 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
label | 7f2d1efb-3749-5b5b-8d2d-f3ecc04a050a |  | note | INSPECTION / TEST PROC: Document and Review
label | 40010cd4-0f32-5df0-9047-6492d4cbf21b |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | ea7d96ee-4595-5bab-99d0-100768433d7c |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.01. Check set out of excavations
label | 7cfb3db1-9cff-506b-96fe-a034b2915ed5 |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | 95ce4686-6429-5deb-99b9-35e1c19eebad |  | note | RECORDS: 'Before' Photographs
label | 3a12d079-b183-5138-8e30-0f57773ab216 |  | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
label | 0f77604f-379b-54e6-a689-a878a8ec0056 |  | note | Minimum falls
label | 9a1acfde-4a63-58a9-9c30-e8406dbc5ca0 |  | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
label | 5e51fc2f-e40e-556c-a45c-26937d6a5e9b |  | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
label | 387b0c92-e2f3-51ce-809d-c5d75a58ab62 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | ba0b40ba-c6ad-5546-91e8-caf7fa17d08e |  | note | INSPECTOR / APPROVER: Foreman. LLB
label | 1aee4ba8-c80a-5338-b5df-8fe7471aea45 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
label | 49e345e9-e6cc-5432-9bd0-7a52e1d11e89 |  | note | STAGE / FREQUENCY: Prior to commencement / each TMP
label | 3ff3f0f3-74ae-5d42-88f5-96d459b5c60d |  | note | RECORDS: Copy of Consent and Traffic Management Plan
label | 6b66bfd0-37ab-54f5-9de4-3fd850a5d3c8 |  | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
label | ab9e74cc-5b55-5d28-aedf-187fa4d214c2 |  | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
label | e812eddf-b911-5df9-ad09-eb65abbc077e |  | note | INSPECTION / TEST PROC: Document and Review
label | 4fbabfa9-9d2a-5f60-9ff4-d104563e3683 |  | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
label | b8fde221-0a20-5b23-af9d-7fd7c0d9a701 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 6. Check deliveries of materials
label | faa6417c-f5f1-5b23-8a6b-aaace772b412 |  | note | STAGE / FREQUENCY: Each delivery
label | 9d157d4c-3360-570c-ab0e-c2f57cda8767 |  | note | RECORDS: Delivery dockets name, signed and dated by Geschke
label | 936c1b77-2ea1-5eff-9d22-bc7eb138d6ce |  | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
label | 0e7b152a-7356-52a2-8aa9-2a4bd5254b40 |  | note | Grade or class matches design
label | 8eca59fe-9613-5624-a338-a76da82142ee |  | note | Size and thickness matches design
label | d43706dc-2b60-545a-8d1d-f4ee3d218379 |  | note | Supplied items are free of defect
label | e8427688-6eb7-5e30-a60d-e09d3aa0aa00 |  | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
label | 7e776f7e-b121-508d-9d77-deb2be71b870 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | f1af6ae0-d5e3-5612-9e74-de91cc16b192 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 6e631d15-3f32-51e6-9188-0eace1f362ff |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.01. Check below ground pipework - pipe welds. Standard Bead Profile Test Standard Destructive Tensile Test Standard Ovality Test
label | 0bc175b9-afa3-5caf-8073-faa0ce974bf7 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling 1 test per 50 pipeline welds approx.1000 l.m
label | 336abc30-c34b-546f-8c99-9f7b9c8a5963 |  | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Standard Ovality Certificate Standard Bead Profile T est Certificate Standard Destructive Tensile Test Certificate
label | cdc881fa-9f03-51b5-b954-ef4e0e89b9df |  | note | SPECIFICATION / STANDARD: ISO 13953 ASTM F2620- 20 ASTM F2928 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
label | 8754923c-edc0-5e7d-9f23-f9861d3be1a2 |  | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
label | 89dd680b-8521-5757-9e28-1bb9b81c5d74 |  | note | Bead size to be uniform, symmetrical and free of contamination and air.
label | a065e7ab-e5b6-53e9-8df7-5d7e5f5d9ef0 |  | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
label | b33bf364-5997-54a1-84f7-ec7c9fca1d44 |  | note | INSPECTION / TEST PROC: Document and Review
label | 4eacc903-dff7-591c-83f5-cf8920a572c3 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 986164c7-9b71-5042-ab51-13b7fa83bdf9 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.02. Check below ground pipework - pipes and fittings
label | 3da1e700-45e9-5333-935e-8267ca3cef1a |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
label | b9af6399-ebcf-5544-973b-0adf40e1460d |  | note | RECORDS: 'During' Photographs & As-built Survey
label | fa50fcfa-4c2e-5a08-b79c-071f799b9712 |  | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
label | bf41cef5-7d76-5a6a-89d6-5ad3b9404b4f |  | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
label | 09809e68-6fbe-595a-87ff-e848f3822f67 |  | note | Joints, fittings and connections match design
label | 6841b510-8010-5353-85f9-ca843e9564f3 |  | note | Alignment and position are as drawn
label | c2edafd1-995f-58f5-8f2a-9bd71497ceaf |  | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
label | 2a6e4987-4c14-5039-beeb-20097dc50b62 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | a67af6c1-5f7f-5790-92c7-59cd223e8b92 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
label | 70f9ae23-699e-5867-a648-64f92f407b63 |  | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling
label | 6c46e8bc-6985-5fa4-bc06-1117e207aed7 |  | note | RECORDS: Standard Pressure T est Certificate QA.6
label | 4eead7bf-c06e-5dcc-a910-9f82cbdea57e |  | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,500kPa pressure for two hours
label | 45f3dcb9-41cf-5bf1-b1f6-7e546ed9ccb6 |  | note | Pipeline is flushed free of all debris
label | 33717f4b-06c6-5c20-8f00-1fdb1c855510 |  | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
label | 80af58c7-1422-5597-afba-5c6c2a385a27 |  | note | INSPECTION / TEST PROC: Document and Review
label | b40ecfef-256f-5778-ab24-8d259a704bce |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 0769b885-409f-52eb-ac43-2cde4c1a2db1 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
label | 82ddc18f-0db4-5aa8-b70a-1ea0fb809a90 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
label | 0c06d046-0e57-50c9-b10d-3d958ad338ad |  | note | RECORDS: Photograph
label | fb55838d-0000-544b-a71b-13a330597a63 |  | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
label | baa2c5a8-94df-5619-b667-0ff6a822d4d2 |  | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
label | 0203941c-c1dd-5bb5-ba07-7fd9ad00b5bb |  | note | Thickness of surrounding aggregate shall meet or exceed specified depth
label | bdc55870-69cf-51ac-84e1-c93a90763509 |  | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
label | cdf4b768-2307-5b46-b0de-45d4037279e9 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | b367c5db-13cf-5a05-ad82-b4f363e4ca48 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 2f16ad37-8748-50f2-a280-2df384135d21 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 9. Check Completed Surface - Make Good
label | c2c89f72-8aff-5673-9cc3-ba640952b0bb |  | note | STAGE / FREQUENCY: Prior to practical completion
label | c783503a-7d21-5f8b-af46-974d025627ff |  | note | RECORDS: 'Upon completion' Photographs
label | 2bad8e2e-8a68-5b05-95f8-aca36d117e7b |  | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
label | 1cfc28b5-40c4-54a4-bb46-0e33323fe0f3 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | cd5bb78a-93ad-55b9-9234-5a157dbbb832 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 98178df9-b017-54f1-b98e-f15c5c2aaee2 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 10. Obtain as built documents
label | 59f51a79-9da5-581f-9c2f-2dedfa43e65e |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 8c374076-7f52-5f39-b1f5-a7dc8bb06575 |  | note | RECORDS: As built documents
label | 19c3ba79-e6b0-5c31-bb77-a399af09f475 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
label | 9493e692-48f9-5afe-a26f-471153fb2dbd |  | note | INSPECTION / TEST PROC: Document and Review
label | 24db9943-32f7-53d3-88c7-5d71e2142e8c |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | e479c03c-92ba-5398-9b83-0ef55e68c4c1 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 11. Obtain Regulatory Authorities certificates and approvals
label | d8f8f9f3-aec8-5631-a3ca-2a2fac86f3b2 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 2d1f9c24-6229-544e-beaf-cc94f8a1ea6b |  | note | RECORDS: Certificates; Written approvals
label | 0e491fa2-97b0-5481-a768-89b586a710f2 |  | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
label | 50c92892-d781-572f-a388-9adfdbe993f9 |  | note | INSPECTION / TEST PROC: Document and Review
label | 40d8fef9-d45c-5b73-9729-0c96d3000956 |  | note | INSPECTOR / APPROVER: Independent Authority. LLB
label | a63b4bf7-1474-5353-ae31-f1634af39cde |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 12. Obtain operating and maintenance manuals
label | 49cf32d9-595c-5bf5-b8fe-db6d12a1e077 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 69d36648-92de-5427-b7db-7cc36ec23d4d |  | note | RECORDS: Manuals
label | 3895e359-64f8-583e-9787-d12564bc0168 |  | note | INSPECTION / TEST PROC: Document and Review
label | cdade328-ae96-58cc-b8d9-22a9ccc044dc |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 85b7dd92-ec7e-538b-82c5-f3a84e5460d8 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 13. Obtain guarantees
label | 462a0a0c-97d9-5420-8fa1-d7f2cdc75298 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 684e011c-8b00-5f81-981b-b15c89d24517 |  | note | RECORDS: Final commissioning checklist
label | 2279ff33-2068-5abe-a24b-3e99e5861149 |  | note | INSPECTION / TEST PROC: Document and Review
label | a33b8147-eb8e-5e02-83e6-b0f9334f6d86 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | a2ebf367-f25f-54fa-b6c0-fb928917d2e0 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 14. Final commissioning & inspection
label | 4e8e831c-bdca-5822-879a-b2b6305e7e14 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 760d6596-89e5-51b9-a1bb-59ff6626f4cd |  | note | RECORDS: Final commissioning checklist
label | f0a0cad1-9620-53f4-aa45-4448050f5032 |  | note | INSPECTION / TEST PROC: Document and Review
label | 4203b060-62e4-52fa-b73d-20665b486dc3 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 031d02b7-3ada-582f-96f4-75a6c6291ff4 |  | note | HOLD OR WITNESS POINT: Witness Point
checklist-flat |  |  | checklist | Grease Trap Checklist |  |  |  |  | Yes | QA 8A - Grease Trap Checklist | d2b59436-2ce8-4e13-a1a7-fe3c09015849
checkpoint-status |  |  | checkpoint | Set out of pits.
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
checkpoint-status |  |  | checkpoint | Laying and jointing of pipes R.Ls and falls
checkpoint-status |  |  | checkpoint | Connections to pits.
checkpoint-status |  |  | checkpoint | Baffle is in place.
checkpoint-status |  |  | checkpoint | Penetrations are patched and made watertight.
checkpoint-status |  |  | checkpoint | Suction line is installed as per spec.
checkpoint-status |  |  | checkpoint | Outlet pipework is installed as per spec.
checkpoint-status |  |  | checkpoint | Vents are connected and terminated to comply with Authority and Specification.
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
checklist-flat |  |  | checklist | Pre Cast Slab Penetration Placement Checklist |  |  |  |  | Yes | QA 15 - Pre Cast Slab Penetration Placement Checklist | f4e30670-caa4-4c04-b6d7-fe97ea9e5118
checkpoint-status |  |  | checkpoint | Pre Cast Slab Penetration Placement Details:
text | 9b9fa587-4e52-5a3c-bf64-8fe3a0d41b4d |  | textbox | Drawing No. / Rev:
text | b8e010e0-dc0c-5df3-a127-57413e1145e6 |  | textbox | Slab No.
text | 37c620e4-e830-5c4e-b88a-367415b6e782 |  | textbox | Total: Sewer - waste penetrations
text | 06b28005-fff3-5a96-9121-15826feccbd2 |  | textbox | Total: Stormwater penetrations
text | 674df700-7ea8-53a5-8bd3-84f9dcc0a78d |  | textbox | Total: Water
text | 5db08c04-89ae-513a-881f-d66e8502d98b |  | textbox | Other:
checkpoint-status |  |  | checkpoint | Geschke Representative Sign Off
holdpoint |  |  | signoff | Request Sign Off
checkpoint-status |  |  | checkpoint | Construction Company Representative Sign Off
holdpoint |  |  | signoff | Request Sign Off
checklist-flat |  |  | checklist | ITP - Fire Sample Excl. Backfill ACOR Review |  |  |  |  | Yes | ITP - Fire Sample Excl. Backfill ACOR Review | feefedae-b0e0-404c-a672-656b5608501c
checkpoint-status |  |  | checkpoint | 1. Approve specialist subcontractor
label | 0d3c38a4-c71b-5749-bd7a-d2067c70fa6b |  | note | STAGE / FREQUENCY: Prior to awarding subcontract
label | 75c6828a-f808-58d7-82db-5697b120d741 |  | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
label | 20972fc4-f613-5c36-9fdb-b3b59709138c |  | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
label | a4fb11ec-1b4f-5858-9dcb-e6dd466fe793 |  | note | INSPECTION / TEST PROC: Document
label | 76315aac-a835-5cce-b888-18c1af84f9bc |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | c9d4499c-c8f2-513e-9a20-71e1a0029c07 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 2. Approve Samples
label | 5ab0487f-5938-5e09-9b34-d720cf6d1755 |  | note | STAGE / FREQUENCY: Prior to ordering materials
label | e1fc6389-0ab8-5094-8af7-67349927b449 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | db57c290-2a20-56b4-aaa9-755f95ac8543 |  | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
label | 4b66d20e-9e42-55bc-9c26-9d2428688d41 |  | note | INSPECTION / TEST PROC: Document and Review
label | 322fb1ac-3495-5a30-baaa-976941d34e5b |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 84ed3336-74ab-5ca7-bdb4-a0df8c14ed95 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 3. Approve technical details
label | 5090bd27-d972-5bdc-8459-8f7791ad1747 |  | note | STAGE / FREQUENCY: Prior to ordering equipment
label | c1d89ecf-ddec-575c-ab99-87602db0e5fd |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | fe526921-c7c2-572e-8998-3a8f7826deb9 |  | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
label | 24a06e65-0f13-592c-9854-5c3509888e52 |  | note | INSPECTION / TEST PROC: Document and Review
label | 7059248c-f190-5668-b990-3f778ed2d7a1 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 04ecf25a-0a35-57ce-9cf3-70802e480fad |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4. Approve shop drawings
label | 6673dca8-e50e-5990-a4e9-9f301517e35d |  | note | STAGE / FREQUENCY: Prior to commencement
label | c0fd2d03-3ac2-5872-80c4-b2dcacc5d7fd |  | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
label | a4f7401d-931a-501a-be52-2bf58b0e39ac |  | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
label | 20931c45-aace-563a-9e25-5c0cc1d7cf36 |  | note | INSPECTION / TEST PROC: Document and Review
label | 382c42b2-01da-5f2e-9238-15bc5d4c6553 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 4dc5d5ed-f7ae-59fd-a74f-f428649b195e |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.01. Check set out of excavations
label | e0acea45-616a-5d20-abf3-dba65f5b042d |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | a932003a-f1bf-513a-b076-8b23298cd31d |  | note | RECORDS: 'Before' Photographs
label | a79969d1-d2cd-57b2-91b9-63f50ca78916 |  | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
label | 56168f84-e867-536a-9e9e-5bbab2444c7b |  | note | Minimum falls
label | 17ce3ec0-095e-5c3b-9cf5-1a3632d43397 |  | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
label | 8699d099-999d-5719-a9cf-58f918d3e344 |  | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
label | 8ee7adfd-c94f-5661-b4bf-ab906a836200 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 281c4987-bc8e-5f15-ba4b-b2db2af87cb6 |  | note | INSPECTOR / APPROVER: Foreman. LLB
label | 0c5ce48a-dc88-5912-9bee-29d674923416 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
label | 71c8a347-006d-5365-921e-9e44cac8f33a |  | note | STAGE / FREQUENCY: Each delivery
label | fa12bde1-b518-5a46-89fb-babef13fed3c |  | note | RECORDS: Delivery dockets name, signed and dated by Geschke
label | 75a9ac72-65df-59f8-a87b-1dc38aa71ffc |  | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
label | 88d997a5-c74c-55b8-9020-e5a9719ec44a |  | note | Grade or class matches design
label | 277a7844-7c60-57bd-94c4-452897bfdacb |  | note | Size and thickness matches design
label | b5479f1a-3776-560d-a901-d9889f2b3009 |  | note | Supplied items are free of defect
label | ea7e015a-c83a-552f-9c0d-968fe651d66c |  | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
label | 06c249c1-3742-581d-8a31-b45fe282e379 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 77b7e683-16d3-5cb3-9302-2e8b72c7d516 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | e66c018c-79b9-5978-a06a-2076f7f2d16d |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 6. Check deliveries of materials
label | 2f388e97-f458-5990-ac7a-da231124e69c |  | note | STAGE / FREQUENCY: Each delivery
label | 8c81df1f-03c4-5c8c-a51f-ca446c042651 |  | note | RECORDS: Delivery dockets name, signed and dated by Geschke
label | 0234a70d-72a5-5b1c-ab04-379851f9b6c5 |  | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
label | 1dbc0549-5aa5-5312-9f5f-6e50d9973200 |  | note | Grade or class matches design
label | 35679dd2-c8f2-55f3-b15f-9c20d6e079b4 |  | note | Size and thickness matches design
label | b8c8695c-09ec-5b0a-9d4a-b45492a3260e |  | note | Supplied items are free of defect
label | 41fbd58e-c3ff-5994-90cd-c9c715e4f4cf |  | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
label | 084bc65c-4140-520d-a2ab-a7251fdeadf7 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | a13da82d-004c-5fce-b969-d4faf5713e02 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 81bacfe1-6058-5740-b33c-72d3dbd2774d |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
boolean | 60895360-5cfc-5d73-9de5-e88b964b0c2b |  | tickbox | Standard Bead Profile Test
boolean | 95d4ef6d-8a3b-5c71-ad65-a13b083249fb |  | tickbox | Standard Destructive Tensile Test
boolean | 4143487f-54d2-5389-8e31-8da8c04c360a |  | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
boolean | a5c4b1c7-e5f9-5f8c-8fec-21b87eda5943 |  | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
boolean | 9c36cef4-e0e3-59c5-b7dc-c54f2b84876e |  | tickbox | Gasketing Record
label | 0c353f24-9b49-5251-b8bb-8712d155134b |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
label | 0828e881-42ec-5630-860e-3762aa3431d3 |  | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
label | b1fa0dd3-9b24-5405-a6b4-7da09ed5cc83 |  | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
label | 905b9be1-1a56-57ba-b057-a0050ec4adb2 |  | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
label | ed02e191-a017-520c-8d81-fdb97bb87741 |  | note | Bead size to be uniform, symmetrical and free of contamination and air.
label | 933b0fa1-7688-5a51-90a0-35e19fe810e8 |  | note | Bolt tightening to be completed using the correct sequence
label | 7fbdcfea-dd60-53b4-8fc6-53e1cd61464c |  | note | Final torque on bolts shall not exceed manufacture specification.
label | c5675546-2d97-512f-a5de-cc8a6bc262eb |  | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
label | 072bce59-c557-56d4-b177-af0e6872d5fd |  | note | INSPECTION / TEST PROC: Document and Review
label | 164562ef-e4ee-5470-a15d-7cc3efe78814 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 9471ad2b-4d7b-5e53-b569-df92a175db39 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.02. Check below ground pipework - pipes and fittings
label | 5a939c8d-0d66-5415-b8e7-d6b4fe7ac149 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
label | 7f370901-a89e-58bd-b582-ed3d2a6439d0 |  | note | RECORDS: 'During' Photographs & As-built Survey
label | 42e5f3ca-069d-53d3-b262-742bc6754cc6 |  | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
label | 55b187a5-80e2-5a56-9936-f2b685de3206 |  | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
label | 12c202c4-6038-5ce0-9d83-a18c23f3be6c |  | note | Joints, fittings and connections match design
label | ca9466ae-3314-55d7-b4f5-5dd465d6798e |  | note | Alignment and position are as drawn
label | 63f29fab-a3c5-57d9-aa59-b8dc74013ec8 |  | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
label | ed337331-cad1-56dd-acd5-86f1c084d7c6 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 0a34d3c5-b440-5ab1-8f12-f35365de11d2 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 7.03. Check below ground pipework - Hydrostatic pressure testing. Standard Hydrostatic Pressure Test
label | 47d52fd1-27b3-5ab6-b0eb-2c39ca430feb |  | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling.
label | 55136b13-f324-50db-8b1e-1c022e499c61 |  | note | RECORDS: Standard Pressure Test Certificate QA.6
label | 5c3f464d-f212-5da3-9587-31953a60efa3 |  | note | SPECIFICATION / STANDARD: Clause 2.3 of WSA 03 1999 & Clause 18.3 of WSA 03 1999
label | 3d0555c6-9314-5704-a4d3-996c25cbe080 |  | note | ACCEPTANCE CRITERIA: Pipeline and joints are watertight up to 1,700kPa pressure for two hours
label | 04030b35-344f-542b-8954-6a10388cb659 |  | note | Pipeline is flushed free of all debris
label | d5bda7d9-9af6-535c-9571-51ede6e82d5f |  | note | Test Passes MRWA Water Supply Pressure Test for PE Pipe
label | e33d1928-937b-58a0-9b54-7b55108e936e |  | note | INSPECTION / TEST PROC: Document and Review
label | 6e7d6f3f-0543-5437-8864-79833c91af1d |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 627dd8a3-8f2f-507f-9c87-375e4bf99c00 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
label | d7819289-6285-525c-9c56-51ae41faef53 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
label | 2a073575-1b65-56ab-9360-68bf67bc7f5d |  | note | RECORDS: Photograph
label | bac1b115-ff41-529c-978e-25403beda668 |  | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
label | 222792b8-72b8-51ce-85e3-53bffbb14a4d |  | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
label | c08b5490-31be-596a-8548-d38174fa41e2 |  | note | Thickness of surrounding aggregate shall meet or exceed specified depth
label | 7d826ade-6c04-56c3-9881-1d8f47d39829 |  | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
label | cbe2f887-5f8a-5cb3-b77b-dcf9505e9312 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | 421812d5-ab50-5a21-9773-bdeb970d995d |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | eb35a14a-3205-517d-891a-06a236881dd6 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 9. Check Completed Surface - Make Good
label | d678afab-c36f-5430-afcf-ef2ade7da5d6 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 2a16d9cc-2a78-5e36-99de-9e2da10a631d |  | note | RECORDS: 'Upon completion' Photographs
label | faa3f6d2-55e6-5166-9e9d-fce58af6cfda |  | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
label | 178bad91-4874-50be-8589-bacc16ae0be4 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 25cd5b2f-31ed-51fc-8328-4efeaefb5f08 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 2d97ab42-0b6a-58d9-bdd9-00ae28360671 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 10. Obtain as built documents
label | 5fb79931-9b5e-5fc0-aca3-2decb8ed9a67 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 8f369965-ed84-51c4-8206-7a5d30af97dd |  | note | RECORDS: As built documents
label | b9fb074d-7c8d-5509-a1a8-64cad860e6c7 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
label | 0f1934b3-17b6-5db0-ba60-0f229a73e3d3 |  | note | INSPECTION / TEST PROC: Document and Review
label | 3c3fd0da-9236-56e0-9e91-68084838a9db |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 16c6f24f-a9b2-5a3d-b638-2254ea0a39ab |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 11. Obtain operating and maintenance manuals
label | 649fe952-9b2d-5420-b002-2836eadc61bb |  | note | STAGE / FREQUENCY: Prior to practical completion
label | e5bc5bf4-2775-5de9-8e12-1c7cf330c43f |  | note | RECORDS: Manuals
label | daca2fdd-9cf8-55bc-a4c9-856fa7f6faa6 |  | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
label | fdc35e53-7276-55ea-93d4-37c6317da508 |  | note | INSPECTION / TEST PROC: Document and Review
label | d8e5342d-64bb-555a-941c-db52e4a757be |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | b9f4ef64-6cb1-5f7e-8bdb-b8e81d4a39ad |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 12. Obtain guarantees
label | 68138bcf-120f-5833-833b-875c080e3e2c |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 5a2046d0-5b70-5fb1-a51b-f6fc3c6bfc37 |  | note | RECORDS: Final commissioning checklist
label | 5fbd5ec1-d140-5cac-99da-963966f3d4e0 |  | note | INSPECTION / TEST PROC: Document and Review
label | ca326e45-62d2-521a-bfd5-5257d705091b |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 21b6d0f6-ed36-5073-82fb-1ae271ef93d9 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 13.01. Check above ground Hydrants - Signal and Flow Test. Standard Flow Test
label | 291a3373-562c-5228-8bb2-45ef34769d41 |  | note | STAGE / FREQUENCY: Upon installation / one test per hydrant
label | 19758053-533b-5c48-894a-814309e29b68 |  | note | RECORDS: Standard Flow T est Certificate QA 6E
label | 4451bffc-0b1c-554c-98c1-2df94a103050 |  | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
label | a62a56eb-87d1-5dfa-985b-4e76da52dead |  | note | ACCEPTANCE CRITERIA: Hydrant flows up to 30l/s
label | 89d2dc4c-fa94-5dc3-a8cc-ba457ed103f2 |  | note | Hydrant tagged and signed
label | 2516b1f8-0500-5ca4-8833-e6e4f873f2ce |  | note | Bollards installed
label | 67d7203c-1a2c-51c3-9554-cd17d87d3e58 |  | note | Signal sent to Building Sub FIP
label | de7c92f6-833e-58d4-b4b3-d5d2bba74411 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | dd1e30c0-1016-5e76-b327-70a6c0c28146 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 63088761-164c-55fa-a1be-c94a8d77eb5e |  | note | HOLD OR WITNESS POINT: Hold Point
checkpoint-status |  |  | checkpoint | 13.02. Final commissioning & inspection & independent report
label | d1a4f79a-4798-5403-84ea-2e023bd9b78e |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 7f49657a-c896-5d54-9b80-af8dca574b85 |  | note | RECORDS: Final commissioning checklist Independent Report
label | 813a4a22-5337-56a1-b94c-fa50f04b2e77 |  | note | INSPECTION / TEST PROC: Document and Review
label | e74b5748-d979-57a4-b25d-68594e678588 |  | note | INSPECTOR / APPROVER: Independent Engineer. Geschke
label | 727c7099-d267-57a0-930f-12c1f1d9137f |  | note | HOLD OR WITNESS POINT: Witness Point
checklist-flat |  |  | checklist | Below Ground Pipework Checklist - Fire |  |  |  |  | Yes | QA 8 - Below Ground Pipework Checklist - Fire | bfdd829d-0a1c-4a61-802f-8763c8b11632
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits depths and trench runs.
label | 05cc5510-efff-5b7d-967b-74d6c9831a02 |  | note | As per DRG#
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | f8d895c4-538c-501d-94ea-9a93c913af7e |  | note | Spec#: AS3500
label | da8e774e-5ba3-5829-876a-ffa9c0fde3c0 |  | note | MDPE SDR11 PE100 PN16
checkpoint-status |  |  | checkpoint | Bedding placement and compaction and material meets specification.
label | 1d684ccd-9a4a-5814-b8cb-f34c4a847823 |  | note | Spec#: AS3500
label | 6b2b018c-9049-56a8-94da-c684839f2733 |  | note | Packing sand encased pipe
checkpoint-status |  |  | checkpoint | Jointing of pipes
label | e059a789-b443-5d83-988b-b18f28d995dd |  | note | Electrofusion and/or Butt Welds
label | c94dfc17-099f-5a1b-9db1-edc9e82f0a8b |  | note | GPLQA16 form
checkpoint-status |  |  | checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
label | 3291b180-c40a-54b0-96ed-a62b051bef13 |  | note | GPL QA6 form completed
label | 895a72af-eba2-5f7f-9ad9-e03b939d4598 |  | note | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec.
label | 22e48b2a-9b2b-5246-ab0e-09f290be5adb |  | note | Compacted crushed rock backfill 80% to 100% compaction
label | 9919140f-7dbe-519d-bc48-1107cdfc1ec5 |  | note | Detectable marker tape
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
label | fc897ea4-9347-5687-b049-5e4b9bbd7e46 |  | note | Ongoing
label | cd74ba9a-0e4e-5ae2-985d-71027ffc3f0a |  | note | To be provided
checklist-flat |  |  | checklist | TMV Commissioning Log Sheet |  |  |  |  | Yes | TMV Commissioning Log Sheet V.040221 | 570a66ca-cd17-4e88-8b8f-929963bb9f2c
checkpoint-status |  |  | checkpoint | TMV Commissioning Log Sheet:
text | 26208a38-cac2-5918-9058-d6adb270105d |  | textbox | Building Name:
text | 787ef829-aee9-54fc-a8fc-d4e33aabce85 |  | textbox | Contact Person:
text | 9824ebd0-4dfb-5815-815b-add1ffc95121 |  | textbox | Address:
text | cd626b90-22ca-5992-bd5f-ab6086b4c2b3 |  | textbox | Lic:
text | 82ed12b7-69b1-577b-bf22-722957661691 |  | textbox | Registration number:
text | 07f933ec-5bcf-542f-9e95-50b4b99e4def |  | textbox | Phone number:
text | 01186232-24be-5ea9-b7b4-5b0f1683cd16 |  | textbox | Make of valve:
text | de882b36-bfe4-5030-8645-4723ae74aacc |  | textbox | Model number:
text | 8bdd78ff-e6a0-5a00-8c68-b3ec31b3c9f0 |  | textbox | Valve location:
text | a8dad8ea-077e-5472-9d1c-e77b6e4de212 |  | textbox | Room name:
text | ebd818f4-1e15-53d2-a9c8-f391da455ace |  | textbox | Valve purchased from:
text | eb6724cd-5f16-5c95-8c50-4a975f90a34c |  | textbox | Installation date:
text | 75b6926b-f474-5f4e-a8e4-46e55d7e5b1c |  | textbox | Valve installed by:
text | b4b5c4ce-9f24-51ec-b78e-e8e6560aa58c |  | textbox | Number of outlets served - Baths:
text | 66597c56-2cf7-5863-bfe5-78ad7d624a84 |  | textbox | Number of outlets served - Basins:
text | b62cedc0-a3a0-58d8-a8e5-e1782bf98dc3 |  | textbox | Number of outlets served - Showers:
text | eeafb204-d20a-5630-84dd-39203fef67e7 |  | textbox | Total number of mixing valves on site:
button | 62c1e723-7b4d-55f6-a717-edcf40fa36c3 |  | button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
button | 91258da4-776c-536b-acc9-d1e75ae8315b |  | button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
text | 85217217-7ea6-569a-b659-e3b40f2e6f2e |  | textbox | Temperature of hot water supply?
text | bdb81617-ceb6-5279-b3cb-aa4d42f75ac6 |  | textbox | Temperature of cold water supply?
text | 30190140-47c3-5ce7-9389-198b882367aa |  | textbox | Temperature of warm water delivery at outlet fitting?
text | 5ef75339-02af-5d05-8161-0937873b45c9 |  | textbox | Dynamic pressure of hot water:
text | db48ded7-f764-5dba-a1ae-dd93bc84c96d |  | textbox | Dynamic pressure of cold water:
checkpoint-status |  |  | checkpoint | Check fail safe operation (hot water at least 20c above warm water)
checkpoint-status |  |  | checkpoint | Commissioned by
text | 65f86cba-77a0-5c26-afdf-7b53eef90330 |  | textbox | Commissioned by:
text | a3daefa7-afd4-5c1d-aae3-7ac0018157bc |  | textbox | Company name:
checklist-flat |  |  | checklist | Service Cross Connection Check List Report |  |  |  |  | Yes | QA 19 - Service Cross Connection Check List Report | d3b073fb-c151-495a-ac39-f02a1079f59e
checkpoint-status |  |  | checkpoint | Service Cross Connection Check List Report Details:
text | 384806cb-258e-5258-90d3-e1a938c4939b |  | textbox | Zone/Grid:
text | fbd6a78a-4611-54c3-bb01-878d324421e9 |  | textbox | Drawing No.:
text | f10de94c-e511-511d-b795-ae0056e636f8 |  | textbox | Rev:
checkpoint-status |  |  | checkpoint | Service to be tested
label | b476d468-5583-54f0-a53c-9117067e9335 |  | note | Isolation of potable supply in general.
checkpoint-status |  |  | checkpoint | Potable Water Supply
label | 0fac9376-7e12-5259-aa89-9e5856bb2448 |  | note | Confirmation of service isolation at all fixtures.
label | 27e9f0f1-91a4-5a80-bc20-3b8b7a232445 |  | note | Keep potable water turned off.
checkpoint-status |  |  | checkpoint | Non Potable Supply
label | 5bf38340-bd7e-5665-afc8-d3f0a7362a3b |  | note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
checkpoint-status |  |  | checkpoint | Turn potable back on
label | f0587b91-5d9a-5d4e-ab05-64d20e6df0d8 |  | note | Potable back on
checkpoint-status |  |  | checkpoint | Non potable supply
label | 4d783ca5-0eed-5b3c-be44-c51958ad7ef5 |  | note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
checkpoint-status |  |  | checkpoint | Potable Supply
label | 9d0666be-dbab-57ad-abaf-c142eaff17d6 |  | note | Check all fixtures that receive potable water are still getting potable water.
checkpoint-status |  |  | checkpoint | Pipe Identification
label | 034987f6-3f7f-597c-a330-66077eb2e9bf |  | note | Confirm recycled water piping is identified by colour and labelling.
checkpoint-status |  |  | checkpoint | Other
checklist-flat |  |  | checklist | ITP - Subsoil Sample |  |  |  |  | Yes | ITP - Subsoil Sample | 18fab84a-43ec-4810-b6bf-b0af8f6baf14
checkpoint-status |  |  | checkpoint | 1. Approve specialist subcontractor
label | 9d4eb838-dc73-55bf-b69f-c9def836fd57 |  | note | STAGE / FREQUENCY: Prior to awarding subcontract
label | da6e934e-11e9-50eb-aafc-cf7d43313983 |  | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
label | 3828bc0d-05a7-5c3d-8b7a-7e232b6d0c0a |  | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
label | df637440-df77-5b80-bda8-ca27cd6c0396 |  | note | INSPECTION / TEST PROC: Document
label | 907bdaa2-ae11-5fe7-9b4a-b8726c61cc84 |  | note | INSPECTOR / APPROVER:Subcontractors Authorised Representative. Geschke
label | 009442fb-4d6f-5780-9dd0-e1d259c035b1 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 2. Approve Samples
label | e0753a28-228e-5b33-9dba-1f2ef8737545 |  | note | STAGE / FREQUENCY: Prior to ordering materials
label | ed2c4902-525f-5084-83cb-3597d98e2b4a |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | c0924802-0d21-5273-893a-36a5e749e8ad |  | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
label | 8d3a4a13-88ad-57f7-bd57-5569ee6bb812 |  | note | INSPECTION / TEST PROC: Document and Review
label | bb6eba40-717f-5c47-a5a4-f9c280ce59a9 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | b89ccf68-12f6-572d-8e63-5c97722e8790 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 3. Approve technical details
label | fd160c9e-62e4-5bb6-b481-0cf089407b1f |  | note | STAGE / FREQUENCY: Prior to ordering equipment
label | 4844bcc0-5510-5ea7-954d-5709d6e77639 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | 8688973e-580c-521e-a2ef-ab63fd5d5227 |  | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
label | bcb9c29c-4d10-58fe-9307-f7fb3cb80757 |  | note | INSPECTION / TEST PROC: Document and Review
label | 650067d7-f4fd-51b4-b854-7a1c032537d0 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | e435cb21-9254-5f72-8f6b-dd34ca67dd9b |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4. Approve shop drawings
label | e745eb57-8603-559c-a4c8-0161dad852a7 |  | note | STAGE / FREQUENCY: Prior to commencement
label | 7610d3ca-cefb-5da4-b772-f9b08eaa1ef8 |  | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
label | 0d000ef2-9abb-5855-acad-717d29720935 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
label | 6c873f21-a11b-5fe2-8348-eb058d7a2b10 |  | note | INSPECTION / TEST PROC: Document and Review
label | 04480fbd-5b24-5218-9ae0-41a1add9a686 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 840e34bf-364b-55b0-853c-dbb09dc2b066 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.01. Check set out - Works by Delta
label | 2f5d3c92-b74b-5a37-8791-2b7410bd4ade |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | 4aef75fb-96f1-56e4-a30c-94d2366ef86d |  | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
label | 896486f4-d9e0-589c-bfbd-ff59e938c842 |  | note | Height control point is marked within 40m of works area.
label | 910ebd13-ef48-5195-b307-d22c12848672 |  | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
label | 80584e9f-b783-579a-bdbf-2d373956ff7d |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | c9f3304a-3c33-5973-8975-2616504cf418 |  | note | INSPECTOR / APPROVER: Foreman. Delta
label | 9ad7cf58-d4a5-5db8-940f-68975769d27e |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.02. Check excavations
label | 31fae4e3-e09c-5061-9060-86d4ed0daa19 |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | 18382bba-eb68-52bb-9f70-b9de3e873c02 |  | note | RECORDS: 'Before' Photographs
label | 5075a1a9-1580-5548-9343-0db42c4f4c21 |  | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
label | 016f9252-71f9-5743-8531-0c0edce96d79 |  | note | Minimum falls
label | f47f7e19-4586-5d39-a733-9f6a253768d1 |  | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
label | 01fbf527-7206-5681-a244-1b6f59c3a7a4 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | 65e836c8-b615-5f9b-83b1-d0f9b5e3c02f |  | note | INSPECTOR / APPROVER: Foreman. LLB
label | a5e514d7-adb8-5b8e-a394-df6e6e372568 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
label | 57bd8763-fd51-5070-8dbd-e9262baa04b7 |  | note | STAGE / FREQUENCY: Prior to commencement / Each TMP
label | aea906af-f26d-5f81-a1ee-1b30392f229b |  | note | RECORDS: Copy of Consent and Traffic Management Plan
label | a845e705-da73-5d36-9ed5-764c10af7bc9 |  | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
label | 08946a2c-eb10-5c8c-8cd0-14ff16e194b6 |  | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
label | b4a32c14-779b-55e0-80ae-e31020b76fe2 |  | note | INSPECTION / TEST PROC: Document and Review
label | aa2b6ade-d039-5ed6-a124-dc0b69f55bf2 |  | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
label | 591e8f8c-978e-5af7-bfff-6f6f28f8ca68 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 6. Check deliveries of materials
label | 9d8a4093-5711-5eb3-b30a-82ec2309416c |  | note | STAGE / FREQUENCY: Each delivery
label | ddafe402-bf29-5e52-b6e8-92002eeb9866 |  | note | RECORDS: Delivery dockets name, signed and dated by Geschke
label | 55a02ce1-c761-5c8d-997b-7809e49d42e3 |  | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
label | dfdcc1cd-2aab-5726-9c19-8cebf0825dea |  | note | Grade or class matches design
label | 71d23c89-7dbb-5c18-83ea-76f954556b73 |  | note | Size and thickness matches design
label | 9e1a1ba9-8427-5d9b-b242-3800df4375a3 |  | note | Supplied items are free of defect
label | 86dcfe28-9be5-5a81-8866-6cc13cd393e9 |  | note | Marking, packaging and preservation is fit for storage / construction.
label | 2e6802d8-89c9-5e57-b922-6504e966cc46 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 9dc8ff4e-5257-53de-b86c-2fa4ad32b710 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 4d05ae0b-3ec3-50be-9af1-cdcd43203737 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.01. Check below ground pipework - pipes and fittings
label | 6587e6f6-8857-58ce-a81e-e69a0d7f018e |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
label | 51ff1b33-3f20-5c1b-946d-dfe5b18568dd |  | note | RECORDS: 'During' Photographs & As-built Survey by Delta
label | f63e3666-152a-53fe-a6b3-93c60acab6a4 |  | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
label | 11d98606-c4df-5995-9604-5b5d4a5065c2 |  | note | ACCEPTANCE CRITERIA: Joints, fittings and connections match design
label | 19fc3ed7-2d4a-598e-b197-9e5525441206 |  | note | Alignment and position are as drawn
label | a9d3c499-2d16-5906-a2f6-2d40e1ab833e |  | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
label | f87725be-7882-5a46-839c-7d99fe66332b |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 63902c13-9d83-5cb0-8476-8552efa85cd8 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 7.02. Check below ground pipework - high ends and flushing points
label | a23ebf66-8470-51c4-ad24-e68cff41e6bf |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
label | a5f06519-a097-5c0a-9438-394f9a11ff00 |  | note | ACCEPTANCE CRITERIA: Capped at surface level with hinged lid, cast iron box in concrete surround 300 x 300 x 150mm
label | d7d6e1b7-55fc-5b3d-9010-dbf2121c3186 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | 85aa3c7c-a514-53f4-a494-cd0d9424b2c1 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | d859aba2-bb4e-5787-9ff8-f51eca18a00d |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 7.03. Check below ground pipework - haunching, surrounding and encasing
label | 116b7a4d-b37b-5890-9c19-2ef492f2425a |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
label | ad62d472-435e-5bb3-814b-d16aae29631e |  | note | RECORDS: Photograph
label | 46a79d42-7477-5de8-9968-d405dfe77cd8 |  | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.19.3
label | c0fbbf83-66c2-59b7-ba63-11f2dd49fd9a |  | note | ACCEPTANCE CRITERIA: Free draining granular material
label | 61b3c230-eedf-5c4c-ab90-9f05e93e2c39 |  | note | All faces of filter material in contact with topsoil or similar shall be covered in geotextile
label | ce343597-2b89-547e-adae-4bf2831ea165 |  | note | Material used is as specified and approved.
label | 918be02e-b6a6-5a1a-9839-eb369acd7333 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | d2767c7d-2d8d-5d33-bd5f-f4856228c8a9 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | d74f6797-3c56-5c4d-8779-04c503ef3494 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 8. Check Completed Surface - Make Good
label | dce6dc94-4517-57ea-b403-733cfca67c81 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | e3846798-21c4-50e2-940e-4efa5c61d919 |  | note | RECORDS: 'Upon completion' Photographs
label | 9e0ec8ef-887d-5a06-a253-0d1424e803ed |  | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework less depth of works by others
label | 1cc14c4a-453a-5a62-b1fc-462636b96b1d |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 33e2b17a-1c55-56c4-9246-90f468242246 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 99c569b5-7437-5d5d-b0e6-884ae95e3856 |  | note | HOLD OR WITNESS POINT:
label | 76009441-b406-5a2c-b191-3ae372055b22 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 9. Obtain 'as built' documents - Works by Delta
label | 93c52f42-ea40-521c-b108-a5f5e2cff2cb |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 8087767b-333f-5e05-9eb0-7043923ed488 |  | note | RECORDS: As built documents by Delta
label | 723ca511-6a90-5520-b884-1220284158e5 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
label | 07a79762-12e9-5e5c-9b4f-6af501b5b26e |  | note | INSPECTION / TEST PROC: Document and Review
label | 6b1a0a76-d16e-511f-9238-c077e472a5a7 |  | note | INSPECTOR / APPROVER: Engineer. Delta
label | 89918e03-93b9-50cf-9589-ffe0837930f3 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 10. Obtain operating and maintenance manuals
label | 63efa2eb-fea7-582c-9919-aa2f8ceebea5 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | de7d9af8-0442-5628-bcca-4f3d8d4daf8c |  | note | RECORDS: Manuals
label | a5d4f506-c0bf-511e-8f30-2ea093e4fea4 |  | note | INSPECTION / TEST PROC: Document and Review
label | 6cfa71b0-06d6-5bd2-ac4e-59806bcedd44 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 59e07c13-61cc-510b-81e0-f2db1f8b0938 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 11. Obtain Guarantees
label | 814f23f8-7599-53fa-995a-51f98f900fa4 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 345d632d-1f3d-565d-b1ce-16d22c671d99 |  | note | RECORDS: Written guarantees
label | 7728e5a2-8c4d-5c9c-8a38-f72b7aa1f7a4 |  | note | INSPECTION / TEST PROC: Document and Review
label | fa565cb3-984a-5bb4-8f59-55e1254fdfd8 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | d11330c1-db74-536f-8249-dcd3a19b564a |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 12. Final commissioning & inspection
label | 12376f84-d771-574e-aabc-7a1854862690 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | a1830aad-a648-517b-95fd-6d5a7638c5dd |  | note | RECORDS: Final commissioning checklist
label | a716b483-bd9d-5d53-a3a8-c2e10802245f |  | note | INSPECTION / TEST PROC: Document and Review
label | adbdd134-9141-5c13-b0ee-710c899fc6f7 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 40201bcc-ad44-5507-b1d8-b31c30f5ba1c |  | note | HOLD OR WITNESS POINT: Witness Point
checklist-flat |  |  | checklist | TMV Routine Service Log Sheet |  |  |  |  | Yes | TMV Routine Service Log Sheet V.040221 | d5aefa4a-9694-4f21-b1e0-a0ce939a1eaa
checkpoint-status |  |  | checkpoint | TMV Routine Service Log Sheet:
text | 3c46d042-a662-50ff-97e5-fa7e49457aa9 |  | textbox | Building name:
text | 4c91d7fa-44c1-5e5a-9579-d0ace27e6a4c |  | textbox | Contact Person:
text | cf04d76f-e714-5108-b29b-9f8e5358a006 |  | textbox | Address:
text | 2954099f-da86-5fe0-ac4b-ec657dc24197 |  | textbox | Phone number:
text | 38da5784-8c05-58cc-8c2e-504bd857f216 |  | textbox | Make of valve:
text | ed15bce9-8c6c-58c1-9a8f-2393b7b3a8e9 |  | textbox | Model number:
text | 6d06dbe5-021d-55c8-adea-5c4de075304d |  | textbox | Valve location:
text | 4e8c9288-3144-50f5-92b1-fe6ecce0da68 |  | textbox | Room name:
text | 6c4362c9-c50d-54c4-9ba5-d7db15b9820c |  | textbox | Date of service:
text | fb53c14a-bd8f-5d0a-88cd-b9ca8414b000 |  | textbox | Outlet water temperature:
button | de222692-69fa-50dc-821b-7c9a91ef6e54 |  | button | Outlets flushed for 15 seconds | Yes, No
button | 4d8f7a63-c119-53ab-94e4-41a9172f8728 |  | button | Shower heads disinfected | Yes, No
text | fb96229d-b921-58f9-aaeb-6504200b316d |  | textbox | Serviced By:
checkpoint-status |  |  | checkpoint | Recommended Service Periods
label | c302b43c-ebfd-5a23-b91e-249dce98dbb5 |  | note | Outlet water temperature = Fortnightly
label | 8fa78483-a776-56c5-bf5e-1d073c25a39a |  | note | Flushing of outlets = Weekly
label | 511f6143-865f-5710-b8e8-c3c2c6aa3ed2 |  | note | Disinfect shower heads = Monthly
checkpoint-status |  |  | checkpoint | Completed by:
text | 3eb1dcb5-47c5-53b7-8026-074388ae4da4 |  | textbox | Plumber Name:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Day Labour Docket |  |  |  |  | Yes | Day Labour Docket | 5dceae5e-796d-49fe-ac90-394a5867e770
checkpoint-status |  |  | checkpoint | Day Docket Details
text | 5c7662b9-6d67-5076-b081-34174d83b306 |  | textbox | Project Name
text | b7294f2b-5cf0-527e-907f-9d7ee8f6d1ea |  | textbox | Job Number
text | 87975a9c-dc3f-53d8-b468-d8bf91570174 |  | textbox | Site Instruction
text | fd3b561b-2193-5a5b-b7e3-1de40a68ce7b |  | textbox | Geschke Reference / Subject
text | 43851586-96a4-59f4-8761-4f20e0c93511 |  | textbox | Requested by name
text | bf76ba28-5cd9-5a95-8e48-c79ba2487249 |  | textbox | Requested by company
text | 2340b828-e42a-5a5c-9fb2-c2644dc2d5db |  | textbox | Brief description - scope, location, other contractor involvement
label | 79e98b40-db35-5c2a-8348-61e9ec1a4f7a |  | note | Attached - requester signature
label | 5993b08a-e5d6-5cb6-b10b-38646360139f |  | note | Attached - photos before
label | cf644e64-73f9-5910-a520-92d88986c35a |  | note | Attached - photos after
checklist-flat |  |  | checklist | QA 25 - BW00# |  |  |  |  | Yes | GPL QA 25 - Butt Welding Checklist (CNRM) | d1b9d2c2-648a-4312-90d5-f42dc2a8278d
checkpoint-status |  |  | checkpoint | Operator Details - Pass once entered
label | 44d7c879-1d1a-5b36-b0e9-6207dfc67732 |  | note | Supervisor sign off at completion of ITP after weld #16
text | b23ef399-68aa-5c16-9c8e-e8b3e4f29083 |  | textbox | Name
text | 40169759-b361-5c48-bf70-c44b29a25c42 |  | textbox | Certification Number
checkpoint-status |  |  | checkpoint | Welding Machine Details
text | edd088c2-967e-5e92-84a2-f8a4a225a6d6 |  | textbox | Manufacturer
text | f370b8e3-6a6d-5991-9f8e-c7f63001dd2f |  | textbox | Type/Model
text | b4f3092a-be96-5caf-9e29-184f50161a40 |  | textbox | Serial Number
text | 48fdf86f-5376-51ba-8147-93525b93b994 |  | textbox | Year Built
checkpoint-status |  |  | checkpoint | Pipe / Material Details - Pass once entered
text | 09b9736d-5f8c-54f3-aa47-c5097f710adb |  | textbox | Dn (OD)
text | be5a7d47-f2c2-58d7-8913-7956418bd66e |  | textbox | SDR
text | ffd297a6-e2db-5df8-b9f8-e0709b71ba58 |  | textbox | En
text | 80d6854c-ea34-53b0-a3f8-685ba4a15523 |  | textbox | Type
text | bee7aa58-5514-5354-a0be-d2bc9fdd8f6f |  | textbox | Parameter
text | edd086df-c691-532c-90e7-47dce1b3c2b2 |  | textbox | SLP
text | 9f2761aa-8a73-5515-b310-d91badbb3e05 |  | textbox | SHP
checkpoint-status |  |  | checkpoint | Weld #1
text | bc9699dc-d883-5094-9413-e1b5f91e0284 |  | textbox | Time
text | a5f789cc-0b93-5d51-894c-78351e87151a |  | textbox | Ambient C
text | d3862185-3d9f-5cbf-97d9-425b3e7f438f |  | textbox | Heater Plate °C
text | 3022b20b-c03d-50ca-9dbf-a87820c5e367 |  | textbox | Drag Pressure
text | 2a86c27c-dcec-52ac-9eff-888cd9c6366a |  | textbox | Bead Up: P1 (Kpa/Bar)
text | fc34da7b-21fd-5fe4-aee9-95fa4d715ef2 |  | textbox | Bead Up: t1 (Evidence)
text | 4c67a8e3-f27c-5b18-b3ba-37b244244251 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | d6087c2f-8cf8-5eb2-abf3-d07fb8860c77 |  | textbox | Heat Soak: t2 (Seconds)
text | d2835900-c38c-5372-8b19-c4b96226f082 |  | textbox | Change Over: t3 (Seconds)
text | ff91d7a6-0916-5784-bf6b-38a069cbdd37 |  | textbox | Pressure Up: t4* (Seconds)
label | d17e9c85-aaac-55e2-bc01-1e71654b31d6 |  | note | *t4 not applicable for SHP situations
text | a7fe786c-ca25-5480-9dc0-09eaa3719874 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | a9d53b7f-948e-5ade-8bc9-e1b9b92d59d6 |  | textbox | Weld and Cool: t5 (h:m)
text | 2901ef98-4121-5d15-bf6a-407dfc3bb05b |  | textbox | Rough Handling: t6 (h:m)
text | 17f654c9-1910-5662-a723-b954b77a6ec2 |  | textbox | Bead Size: Min
text | 6a5990c2-ad5f-5178-8465-09691228d4ca |  | textbox | Bead Size: Max
text | 16dcda18-5d2f-5137-bf2d-ffa117a92f7c |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #2
text | db5a88b3-f59f-5d19-95ad-39edcb36ba85 |  | textbox | Time
text | 9f6e314f-b9d1-5e02-875b-7711078bc7ac |  | textbox | Ambient °C
text | 10cc49b0-9696-5afc-92ab-f35bf2b2a8e3 |  | textbox | Heater Plate °C
text | 35a69463-0fa8-5beb-a482-29cf93f1fc79 |  | textbox | Drag Pressure
text | 3ce4dc43-3b58-5c5d-82ab-9806ef45d250 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | cf9edc1b-4477-5ae3-9db9-dfb264387374 |  | textbox | Bead Up: t1 (Evidence)
text | 7c53d10d-8088-5228-9d6b-5335f3cd6fab |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 2792973b-b159-5383-81d0-8550c3771314 |  | textbox | Heat Soak: t2 (Seconds)
text | e8a01855-a16b-59ed-8bd7-9a8f37f2aa6b |  | textbox | Change Over: t3 (Seconds)
text | 03ba0a96-99e8-5ee2-89b1-f52fc60f3eb2 |  | textbox | Pressure Up: t4* (Seconds)
label | 0485d298-0310-5829-ad4a-8a49ea9897fe |  | note | *t4 not applicable for SHP situations
text | 576d831c-63c6-56bf-9768-1fdbc270ddd5 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 8439de80-939f-5b71-8f53-673e9926aea9 |  | textbox | Weld and Cool: t5 (h:m)
text | 79b49a2f-2c17-523b-8f9d-ed6b93695393 |  | textbox | Rough Handling: t6 (h:m)
text | 96640787-0b60-5287-bb3b-0e38ee84dd93 |  | textbox | Bead Size: Min
text | da32795b-8891-5466-b216-6b0881a0e9dc |  | textbox | Bead Size: Max
text | 53e70b26-5b42-5157-8c92-7298e0cac710 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #3
text | 015428cb-d388-5c67-a3b5-c9ceec1b2e98 |  | textbox | Time
text | 0ee00dbe-bb17-59a8-bd7a-054af1783557 |  | textbox | Ambient °C
text | 42476481-8dbd-5b2d-bc2b-72ea07b8f348 |  | textbox | Heater Plate °C
text | e08fa52e-94fa-56a3-a942-5f5080832deb |  | textbox | Drag Pressure
text | e9a5fa43-2b91-5ab5-9c6a-39ae3b212057 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 8f1a028a-da38-51d5-868c-5d50649ffaca |  | textbox | Bead Up: t1 (Evidence)
text | f7b4ba53-9219-5aba-98fe-b9687818f78e |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 72923825-7c13-5eb0-b3a2-437be2f4137a |  | textbox | Heat Soak: t2 (Seconds)
text | 4229b6ee-115f-5f3e-8b64-1e742ec88bd4 |  | textbox | Change Over: t3 (Seconds)
text | 5881296c-000c-51c0-900a-9e7ae47d0758 |  | textbox | Pressure Up: t4* (Seconds)
label | c45bd83a-7060-5265-b7e3-e4f6bf16e2f5 |  | note | *t4 not applicable for SHP situations
text | c8b50c41-1781-55dd-ad33-4b99314781af |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 78b755d9-f656-5778-ae41-77c9164e42aa |  | textbox | Weld and Cool: t5 (h:m)
text | 25ed308e-fc54-5666-9cfb-a754447435c1 |  | textbox | Rough Handling: t6 (h:m)
text | ae72f6d7-e35b-5163-9f12-83260195b1f1 |  | textbox | Bead Size: Min
text | 6facc60e-5cf1-5145-abbf-8a4888784618 |  | textbox | Bead Size: Max
text | af73991a-c771-53fa-826d-f116da3f2ce1 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #4
text | a1c872aa-1822-5b3f-8c50-9aa7d3c89aef |  | textbox | Time
text | 0f6e4430-d60f-5d40-83fe-ad9396dc71f3 |  | textbox | Ambient °C
text | a950a88a-d855-55e1-aa6d-a48de5d73132 |  | textbox | Heater Plate °C
text | 3d2e3ab1-efa5-5f42-8b61-edcaad61ec1e |  | textbox | Drag Pressure
text | 41157317-a7f0-5046-b4a5-77cd1a2ace69 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | c7bedc0b-1173-5889-b044-96e00ebc4bfb |  | textbox | Bead Up: t1 (Evidence)
text | 2c2e97cc-826b-5073-93bb-7e4f93977063 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | bf54adc8-609b-5bec-94ba-3b5f5fdc57c4 |  | textbox | Heat Soak: t2 (Seconds)
text | d3b17e7e-8561-54a9-bee8-a1ed3e4b815a |  | textbox | Change Over: t3 (Seconds)
text | 0153c081-77b8-5fac-a33c-2691c92b6e32 |  | textbox | Pressure Up: t4* (Seconds)
label | 7de83c66-f8d5-515c-9f73-fe6a53ffa61a |  | note | *t4 not applicable for SHP situations
text | dd2a3ebe-285b-55ca-8f7e-e52336fce2cc |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 36b316a5-ffdc-502e-9e6b-f85b7bad2ab2 |  | textbox | Weld and Cool: t5 (h:m)
text | 661818dd-34b1-5b94-9ef5-2f58facd3ee2 |  | textbox | Rough Handling: t6 (h:m)
text | dfd95ce4-6379-5fe0-9745-d7fbf2793278 |  | textbox | Bead Size: Min
text | 9f8fff29-68aa-5eae-b513-1bea33fcb476 |  | textbox | Bead Size: Max
text | 880ccdb5-9bef-55da-b9b7-8a1ed8c9f8d1 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #5
text | f3f65331-8e1a-5213-8a5d-c18e5619c628 |  | textbox | Time
text | d40f374b-af87-5067-b050-34e226919ea7 |  | textbox | Ambient °C
text | a693cd62-55f3-5634-a695-ace08d9e2f17 |  | textbox | Heater Plate °C
text | b56db16f-81a9-5124-81f8-adc9fadfd405 |  | textbox | Drag Pressure
text | f7a7b288-12ba-5142-8a7e-89263401b31f |  | textbox | Bead Up: P1 (Kpa/Bar)
text | c894dcad-ead6-5fa7-84ec-9ba62914f18b |  | textbox | Bead Up: t1 (Evidence)
text | c149edc7-b516-5e8e-b11a-242b0cdd4694 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | fa48e0ba-1901-51f0-89a9-9f61c0f903f3 |  | textbox | Heat Soak: t2 (Seconds)
text | e476b0e9-8da6-5cae-865c-710fc50da6cf |  | textbox | Change Over: t3 (Seconds)
text | 085c7e77-4ead-5a1f-bfdb-bcf3211caf41 |  | textbox | Pressure Up: t4* (Seconds)
label | 306dd4b9-cee9-5e9b-8bb1-fdadb46b189b |  | note | *t4 not applicable for SHP situations
text | 785dfa4d-2420-50ee-9230-52bc2dd0d974 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 29172ad1-0286-582c-8744-ab069d4bdf03 |  | textbox | Weld and Cool: t5 (h:m)
text | 9012091b-1dc9-50da-b1c8-d05ed2dbc6ab |  | textbox | Rough Handling: t6 (h:m)
text | 9c6bcb1c-0014-514c-b928-d923f7dd2c6f |  | textbox | Bead Size: Min
text | 2a2c24c5-6623-5c4d-ba0c-26235e75a16d |  | textbox | Bead Size: Max
text | 2175de99-d1f3-528a-8c87-f43e420eb9e5 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #6
text | fa0e65f9-2bdb-5cf8-8f82-47617c27bb27 |  | textbox | Time
text | d9d1df85-213e-567a-b549-b8d8e35d6a33 |  | textbox | Ambient °C
text | ccc234fa-b311-5644-bb09-82a96eff62d3 |  | textbox | Heater Plate °C
text | 0ebc8625-552d-5e1e-93dd-83a09ec4ec4d |  | textbox | Drag Pressure
text | 353f27f6-5a69-54df-bd95-93e5f1691409 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 8aa4baf4-ea05-52f5-9d96-73da03648eb3 |  | textbox | Bead Up: t1 (Evidence)
text | 0a092e83-ab13-51af-a34d-f17ecd48fbea |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | c9c54f24-8b24-57f1-b64a-b08dd235359d |  | textbox | Heat Soak: t2 (Seconds)
text | 0c731826-8f00-5a5c-93e7-374ae5a249bd |  | textbox | Change Over: t3 (Seconds)
text | 8d6b54a5-705f-519a-b3d7-0ba2d2a0724f |  | textbox | Pressure Up: t4* (Seconds)
label | a4054f94-95db-56a0-adbb-2356dc6dc68b |  | note | *t4 not applicable for SHP situations
text | 953b9474-5383-51af-9b4c-e116781f332c |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 66f411e1-09cd-5a3f-82be-1e4326867536 |  | textbox | Weld and Cool: t5 (h:m)
text | 69148c02-bc23-5f16-9f8e-4bcdf0436a0f |  | textbox | Rough Handling: t6 (h:m)
text | a81eec86-89a3-5a54-98c6-645c62182771 |  | textbox | Bead Size: Min
text | 84472177-d48d-5686-b4d8-af32152f2ecd |  | textbox | Bead Size: Max
text | 13d0760d-d0b0-5de2-8dc1-00ce570e811a |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #7
text | 72534e0b-f47d-5ddd-a43f-51d911cf26d7 |  | textbox | Time
text | 5c57eda9-9557-5b5d-83ae-485262c17583 |  | textbox | Ambient °C
text | 647a07b9-768f-58c5-a7fd-377b33b52295 |  | textbox | Heater Plate °C
text | 22043f46-0d3c-5e4c-a0fc-2b46933d9bbf |  | textbox | Drag Pressure
text | 018fb432-7e4f-53a1-a13e-4ac6f79dd926 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | c5fdbd0b-aa4e-5bb0-a74b-fab198cd5ecc |  | textbox | Bead Up: t1 (Evidence)
text | 69abe86b-d4cd-5405-9507-41d83946fb3f |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 9099abc3-d722-5b86-ae61-99b47037920f |  | textbox | Heat Soak: t2 (Seconds)
text | 72de2874-b613-55f5-99c2-8090803573ba |  | textbox | Change Over: t3 (Seconds)
text | 935657d6-8d6c-5e7b-9d66-5d3c61d02c57 |  | textbox | Pressure Up: t4* (Seconds)
label | e64ce176-71ac-5979-867b-c38acbd1f710 |  | note | *t4 not applicable for SHP situations
text | 25c04a4c-547e-5b12-8ad8-4eda968ea28f |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | d06a4478-3217-54fa-89eb-0b28b9f93415 |  | textbox | Weld and Cool: t5 (h:m)
text | 82a7f4a5-18b4-51d9-b9a8-1cdf23cc44b5 |  | textbox | Rough Handling: t6 (h:m)
text | ff220b77-58a5-5389-aa45-77ac8517ccdd |  | textbox | Bead Size: Min
text | 1a0f7413-b0d3-5ebb-834f-59b9dee4b31a |  | textbox | Bead Size: Max
text | 5fed14d7-5ce5-592b-832d-91f5a64450c0 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #8
text | 274dad37-befa-5d0a-8623-105e6f8833f6 |  | textbox | Time
text | 2ab6ac9a-6c9a-566e-a603-b80dcbbc92fd |  | textbox | Ambient °C
text | b9e91781-d1bb-5395-b2cb-481c722b10c8 |  | textbox | Heater Plate °C
text | ee64d230-19ca-531e-b842-79804e63cbb1 |  | textbox | Drag Pressure
text | 28fcd57d-2e36-5455-afb4-a142b5e89438 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 2d9404b0-c70f-5d39-987b-9784b1febc0a |  | textbox | Bead Up: t1 (Evidence)
text | 8437d4cc-baac-5971-a765-37dc3309bfd1 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 1fd0dd9f-995e-50c2-b061-f1cfe01a5347 |  | textbox | Heat Soak: t2 (Seconds)
text | b2f95662-0ce2-5ed9-a8c0-f60a277ad967 |  | textbox | Change Over: t3 (Seconds)
text | 502a599a-2426-5765-be22-2db409661576 |  | textbox | Pressure Up: t4* (Seconds)
label | 47d63e45-d059-5689-9c76-5f8265a90b3f |  | note | *t4 not applicable for SHP situations
text | 47fabe00-6779-5270-b047-05156c3edf78 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | ced994f5-4c73-55f3-8306-3d20db5e9b7d |  | textbox | Weld and Cool: t5 (h:m)
text | c5912eba-cfc2-5437-9321-df95f41f18bd |  | textbox | Rough Handling: t6 (h:m)
text | 87457dd5-45ef-5adc-afec-9e0dfc6c762a |  | textbox | Bead Size: Min
text | 7d1e343c-de68-5016-82ee-a1f19c6222f3 |  | textbox | Bead Size: Max
text | e0b6a4f9-8d07-52a1-a97a-6c527f09a7aa |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #9
text | 16132c2a-e8fa-5cd8-a245-f0308f43eec7 |  | textbox | Time
text | a56ab8fb-d061-512f-bab6-f6ce2c3845f6 |  | textbox | Ambient °C
text | e37e13c4-a9f6-5b8a-b4f7-23e70daf30b3 |  | textbox | Heater Plate °C
text | 8d4c5a28-8f84-5d91-950c-a5fa0e53d9f2 |  | textbox | Drag Pressure
text | 3708746e-9901-5ac7-86a8-78ec5c221357 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | fb4427a3-dfc6-5449-9802-00fde745f070 |  | textbox | Bead Up: t1 (Evidence)
text | 433dea68-3549-5b90-b84f-f93ee0749d21 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | d3d2bff1-00f9-58ee-9c79-4d57739ad201 |  | textbox | Heat Soak: t2 (Seconds)
text | 155ec100-336b-5848-87e4-f74fc64a28c1 |  | textbox | Change Over: t3 (Seconds)
text | ef37aed3-7f4f-5134-9946-f462f4517e50 |  | textbox | Pressure Up: t4* (Seconds)
label | 27edcd4d-bafa-5558-8a8c-9176ab0a9a10 |  | note | *t4 not applicable for SHP situations
text | 0f3bd917-62cf-5b3b-8861-d62938cc4b41 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 265a157c-383e-575b-ae0a-9d53e929eee2 |  | textbox | Weld and Cool: t5 (h:m)
text | 10062f86-0fd8-57d0-a346-ce4050ad84b5 |  | textbox | Rough Handling: t6 (h:m)
text | b184f9b8-7607-5fe3-9df6-5ff48d9e3308 |  | textbox | Bead Size: Min
text | 88d034a7-8db2-5ec0-8c34-14362c77accc |  | textbox | Bead Size: Max
text | 571d0dc0-90ca-5223-81b5-b3f4df83b60f |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #10
text | 8bee8241-ab4b-5845-a4ab-bde02d4aa22f |  | textbox | Time
text | dc40e920-3714-5299-ab03-d35009c92fac |  | textbox | Ambient °C
text | ac15f54a-ff39-5552-b610-e30311e75cbb |  | textbox | Heater Plate °C
text | e54af82d-344d-5373-ad31-c758fbb660ca |  | textbox | Drag Pressure
text | 1216cff5-9d89-5642-8509-f08bf9ce8dc0 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 400c2711-d973-55d1-a866-c34eba6d17bf |  | textbox | Bead Up: t1 (Evidence)
text | cfc1d5b5-0d1e-53fd-9b40-b10ef47bd485 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 9fe67302-1749-5c29-8a39-9522b10809d9 |  | textbox | Heat Soak: t2 (Seconds)
text | 981ad4fd-0ec8-5ca8-bd8a-1800bbadfbdd |  | textbox | Change Over: t3 (Seconds)
text | f84604a5-003e-5a76-b6bf-612ebeccd287 |  | textbox | Pressure Up: t4* (Seconds)
label | 3bb3dd65-7aeb-53a7-8d52-a1cfd6dc8658 |  | note | *t4 not applicable for SHP situations
text | d89c2c20-3245-52a0-9b88-e59a79ebba6b |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 9f5a8fda-1e96-5bea-8f3b-4ea10e34b9b9 |  | textbox | Weld and Cool: t5 (h:m)
text | 00e859fc-097d-5eba-ba5f-49d2f0ac122d |  | textbox | Rough Handling: t6 (h:m)
text | beffe23b-dc28-5e2b-9364-be5ebc4967ba |  | textbox | Bead Size: Min
text | b905df13-4289-5845-a507-afbb497a8030 |  | textbox | Bead Size: Max
text | 3946f003-652f-5ce4-9f3e-c15d7143dc9d |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #11
text | 8ebde7b5-91f8-516c-81db-51cc2733b492 |  | textbox | Time
text | a8313b6e-e31c-5944-b641-c53a4078a825 |  | textbox | Ambient °C
text | 5bf6c438-fcda-5c62-95d4-f6fc270edc1b |  | textbox | Heater Plate °C
text | bb207a4f-51f7-52ef-8639-3ee952551455 |  | textbox | Drag Pressure
text | fdf43002-1e47-552f-875a-2f1ac3efb462 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 60bf122a-39db-5134-ab14-d2f31ef330d5 |  | textbox | Bead Up: t1 (Evidence)
text | 25cbcf31-affa-51ea-b325-0bc5525419cb |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | f584ee40-6190-5886-80ed-4166a957652b |  | textbox | Heat Soak: t2 (Seconds)
text | 5929bb70-5c74-5346-a5ea-f32a5b67d6bb |  | textbox | Change Over: t3 (Seconds)
text | 2f933de2-4334-5515-a5b8-f4705a3751f4 |  | textbox | Pressure Up: t4* (Seconds)
label | 56a23d36-3614-5913-9ed4-daf97e63238b |  | note | *t4 not applicable for SHP situations
text | cb43f9d4-78b0-5871-87f0-55ebc2f3630e |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | b37fca65-c217-527b-a8c3-87637cb253b8 |  | textbox | Weld and Cool: t5 (h:m)
text | f5b1176a-327a-5c8d-bcdf-1c82e4af79a2 |  | textbox | Rough Handling: t6 (h:m)
text | a8bbe734-0635-51d6-a987-d55ff1868d2d |  | textbox | Bead Size: Min
text | 75456cfb-219a-5f36-9b7d-9b9e2c21f6a2 |  | textbox | Bead Size: Max
text | 513fa48f-5876-535e-a8cd-66059049ac20 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #12
text | 5f9c345b-e9ee-52d7-9811-2de7302d56ef |  | textbox | Time
text | 010c4aab-e8ff-5a68-a3c1-a569d26bb5c3 |  | textbox | Ambient °C
text | c21c7b0c-56c1-5eb7-a372-f97bd6e9a541 |  | textbox | Heater Plate °C
text | b726c46e-3c6a-5d7e-9e80-bf498b35f233 |  | textbox | Drag Pressure
text | f349474d-10bb-5ddb-b868-cce6ca61a5ff |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 08589c14-3c73-5a4d-b420-11ec652801f9 |  | textbox | Bead Up: t1 (Evidence)
text | ae726fcf-631a-5b8b-b176-c78072517f2f |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | d334f903-c4df-5f19-b71a-9a0d7f9c7d1a |  | textbox | Heat Soak: t2 (Seconds)
text | 3bb2306e-452e-5072-aeb0-25cc4ff6cfba |  | textbox | Change Over: t3 (Seconds)
text | e986d37f-37f8-5116-b2d2-f4bece218624 |  | textbox | Pressure Up: t4* (Seconds)
label | 8bbd2649-fd80-5458-b46f-5748a5199426 |  | note | *t4 not applicable for SHP situations
text | bd2b75c5-2033-5087-ba77-68e32c800876 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 13d917ab-89cc-581c-8698-daf3de9d2a9e |  | textbox | Weld and Cool: t5 (h:m)
text | 8078879e-06cb-5bab-8a0a-0f6e955c8074 |  | textbox | Rough Handling: t6 (h:m)
text | 7052ddf3-0a9f-50b5-abef-85a8bf841f9d |  | textbox | Bead Size: Min
text | c1c01554-51a0-530c-8047-43a573263991 |  | textbox | Bead Size: Max
text | 2b0b1306-8d5f-5048-b129-fd4c311cd308 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #13
text | 15820892-f921-5d4a-8075-9b6c488da292 |  | textbox | Time
text | 622e32c0-ea88-5002-a4d2-d9c66c57849e |  | textbox | Ambient °C
text | e42b61c6-52b2-505b-a53e-577d5ef968c9 |  | textbox | Heater Plate °C
text | 1b15f9ed-67e3-550d-a0a6-21d5bbb0dd36 |  | textbox | Drag Pressure
text | ab1a1da7-98a2-53f3-8ebc-cf57434f5fb3 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 78196ca7-5756-5328-8f91-74d2b5f91243 |  | textbox | Bead Up: t1 (Evidence)
text | f23afc03-d167-5aed-b330-9afa46d663ef |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 1e82fa4c-fa0e-5d92-90e1-7f333331237a |  | textbox | Heat Soak: t2 (Seconds)
text | e8925f81-4b0a-543b-9375-23226f4d1b0c |  | textbox | Change Over: t3 (Seconds)
text | 742b7902-23bd-5875-a08e-28c5bbd27756 |  | textbox | Pressure Up: t4* (Seconds)
label | eceb0d9a-bc24-5429-be5c-940fdab26695 |  | note | *t4 not applicable for SHP situations
text | 89a34668-060b-574d-a965-3462d5fca248 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | df7236b2-0f1f-5672-976a-2ad9b3b952f2 |  | textbox | Weld and Cool: t5 (h:m)
text | 0d9eb930-0761-51b3-8c4d-b2ef3cbc0e7f |  | textbox | Rough Handling: t6 (h:m)
text | be7bf59e-c85b-579c-a7c0-f69ae72affac |  | textbox | Bead Size: Min
text | 0775c384-d271-5139-9092-b0633ea75c9e |  | textbox | Bead Size: Max
text | fed8a321-9eaa-585e-b120-63f5d2c8c4de |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #14
text | 27b5eedd-7caf-540d-ab11-d5455fb39f3d |  | textbox | Time
text | 29c592dd-5875-545c-a9d0-ba738074c3b7 |  | textbox | Ambient °C
text | b428a4f9-49de-53c8-b78a-cb0374f2e627 |  | textbox | Heater Plate °C
text | 80116684-c48e-5f2e-a39a-f44942e87224 |  | textbox | Drag Pressure
text | 8a876851-757e-5741-816a-8fe68e9ed2c9 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | e670de68-384b-5b88-8223-d2fab1af53ff |  | textbox | Bead Up: t1 (Evidence)
text | 0f967ffa-2854-5ed3-a22d-ea050171160d |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 271a0516-51d7-56d3-8c1b-92c404d71caa |  | textbox | Heat Soak: t2 (Seconds)
text | 9a1a7d93-a538-527e-a05f-5cb9e6c7c6c2 |  | textbox | Change Over: t3 (Seconds)
text | 57f63711-0020-57ba-bf50-4e3073557fc2 |  | textbox | Pressure Up: t4* (Seconds)
label | 7a34e075-f760-53c3-b5d0-0b1a46891395 |  | note | *t4 not applicable for SHP situations
text | ec038315-82ac-5ac7-b63d-d8ed22cdc960 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 40eedc13-f853-5dac-b5a8-9a0eb295aee3 |  | textbox | Weld and Cool: t5 (h:m)
text | 6ee05c5d-7a78-5986-b40f-7607a2628c2a |  | textbox | Rough Handling: t6 (h:m)
text | dfd7a32f-d205-513f-9fd8-6cd7a53e4533 |  | textbox | Bead Size: Min
text | be33065a-d29e-5cc5-bdf0-8fa3ebca5ed1 |  | textbox | Bead Size: Max
text | 8f91594b-31cd-554e-a4eb-386071a25460 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #15
text | 823901fb-cd82-51b0-8da9-14b172d9730e |  | textbox | Time
text | f230f40c-69cd-597a-a692-e66c6cbe2806 |  | textbox | Ambient °C
text | 651e35cb-9b70-55c6-a166-b4339b28c968 |  | textbox | Heater Plate °C
text | 7ac64a49-0d58-5a38-afbd-7f115d5193a3 |  | textbox | Drag Pressure
text | 0ae7b457-4c86-5bac-92a8-dddb7416f114 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | fac2e750-0c48-585a-9417-c432529d7cd6 |  | textbox | Bead Up: t1 (Evidence)
text | f57c0ab1-d558-59de-9a77-a974ea7f1c70 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | efef8bc4-2135-58eb-9b19-eb4c3796c734 |  | textbox | Heat Soak: t2 (Seconds)
text | ed8d8a25-171f-5d3d-a431-46e8789b7794 |  | textbox | Change Over: t3 (Seconds)
text | b3e2cf93-8b33-53d1-984d-ea9a9af1091d |  | textbox | Pressure Up: t4* (Seconds)
label | abc329ab-4a52-5603-8035-cab2d9442a60 |  | note | *t4 not applicable for SHP situations
text | c3b70a2e-94cf-515d-929f-18d3f1652fca |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 201aa927-0344-596a-8c7a-ab12f77bab40 |  | textbox | Weld and Cool: t5 (h:m)
text | 9c1ea621-62f5-5ac4-9119-9f288b36f03d |  | textbox | Rough Handling: t6 (h:m)
text | 5f156729-65ef-5bb7-b375-a48045a69847 |  | textbox | Bead Size: Min
text | 8b036248-97f2-5b82-ab47-a7d93cf68ed6 |  | textbox | Bead Size: Max
text | ef54206a-6e5e-5ac6-8966-6bd840ac5902 |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Weld #16
text | cb7e30bb-1ea3-5659-b39a-ddfb73c13094 |  | textbox | Time
text | 7c1c0478-bad1-526e-a4dd-c36fd39029d2 |  | textbox | Ambient °C
text | 54518f66-a1aa-5b11-afe4-786d65cc4d4c |  | textbox | Heater Plate °C
text | fd488c9e-4267-5f38-84f2-1b38b7aec339 |  | textbox | Drag Pressure
text | 3a5446f0-336c-57d0-bc30-12220733111d |  | textbox | Bead Up: P1 (Kpa/Bar)
text | b95427be-ceff-57e7-9368-ac2bf9e1709d |  | textbox | Bead Up: t1 (Evidence)
text | 3958ba65-a478-56b7-9da3-49589ba1588d |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | d3486e1a-ba04-58d7-808f-45d2fb242aa5 |  | textbox | Heat Soak: t2 (Seconds)
text | 0b012023-3d28-527d-b440-ccb69069211d |  | textbox | Change Over: t3 (Seconds)
text | 3536e1ea-0890-5820-aaf4-badb9d97e8bc |  | textbox | Pressure Up: t4* (Seconds)
label | a111c964-dbf0-5b3d-ba0b-c1af772800fa |  | note | *t4 not applicable for SHP situations
text | 359cb985-ecae-5163-a73b-bccacb97054d |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 631bab58-74c8-5c92-94e8-abf885e2c196 |  | textbox | Weld and Cool: t5 (h:m)
text | f9253546-3165-5d9a-8523-b2d08e1cb6da |  | textbox | Rough Handling: t6 (h:m)
text | d22fa83f-c592-562a-bcbe-2787a4a1dd3c |  | textbox | Bead Size: Min
text | 10761089-62d5-5b1a-8a4f-a7d484465c7a |  | textbox | Bead Size: Max
text | 8981e3d5-706a-5660-a632-4fece9d21cab |  | textbox | Comments
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | f95258a0-3fce-5428-999f-18fcdaa3c6d2 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | 292f79e9-689a-501f-87cf-eb8a74f8582f |  | note | Company: Geschke Group
label | 3ca598eb-b490-5a4e-a613-c17b9eff9dbe |  | note | Phone: 03 9798 1619
label | 593d1a7a-6074-5741-9a88-11200b7a2ed7 |  | note | Address: 45 Pacific Drive, Keysborough
label | d74baf01-2f63-5a5f-9654-8e6754bc0bee |  | note | Project: Centre for National Resilience Project - Melbourne
label | 78eae871-9eb8-5bcd-934d-dec293f08d1d |  | note | Principal: Multiplex Constructions
checkpoint-status |  |  | checkpoint | Foreman Sign-Offs completed - Click to Attach Signature(s) below
label | 5c8b5786-3cb0-50a9-b372-390ed17c7106 |  | note | Operator Sign-off added to each weld above as required
button | a5196735-7d03-5e01-9a5b-e7516e15cb36 |  | button | Geschke Group Signature Sign-Off added below | Yes, No
button | 225ec6c5-bdfe-5291-acc6-cc7b6e81591f |  | button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist-flat |  |  | checklist | Equipment Calibration Register |  |  |  |  | Yes | QA 11 - Equipment Calibration Register | fb457690-85d3-41d5-a6e5-971c3a34f3ba
checkpoint-status |  |  | checkpoint | 1
text | b4d2c565-6cee-5beb-9f2a-9a346000f629 |  | textbox | Equipment Type:
text | be6ab2aa-d446-582d-a849-bfe836eb24eb |  | textbox | Manufacturer:
text | 47593f44-3f6c-5547-84c2-26e0bbe47831 |  | textbox | Model and Type:
text | 5941931a-1aa8-58e8-be93-967243c88d47 |  | textbox | Serial No.:
text | c86e3e82-4a80-595b-9779-716c2b19f620 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 2
text | 0306dcf0-68f3-549c-9016-f7af3b1c6ec3 |  | textbox | Equipment Type:
text | 33c0b8b5-8807-5a36-8e57-78e3b2cffd0b |  | textbox | Manufacturer:
text | 9bc41edb-c3df-5933-9cb9-88e19a0a352f |  | textbox | Model and Type:
text | 95d17765-6174-52b6-af43-d2574c3cf7c2 |  | textbox | Serial No.:
text | 974f94f4-32e3-5b07-b53e-96a207c4e5a9 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 3
text | 76a02e6d-6074-56d0-87c9-bedee5e2fd92 |  | textbox | Equipment Type:
text | 191cf691-0333-562f-84d4-a19180c8c35e |  | textbox | Manufacturer:
text | f4614282-7975-5463-b1d2-174c3a96397e |  | textbox | Model and Type:
text | c30ae13d-364b-5dbc-b392-cb79271ea4f3 |  | textbox | Serial No.:
text | 52bb628b-cc74-5d15-9174-7a2093a79f63 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 4
text | 3707671d-ca0d-57a3-adeb-787ad49847d6 |  | textbox | Equipment Type:
text | 6b916005-e6be-5e93-abc6-40dfef2a82c7 |  | textbox | Manufacturer:
text | 2ae7293d-67a1-55c5-8559-1f1c7f0191b0 |  | textbox | Model and Type:
text | 2b5afd9c-bed7-563d-9fba-8740e3731118 |  | textbox | Serial No.:
text | b1afa72f-9aca-5386-9ef9-0af842e99e74 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 5
text | 069ace06-2f9e-5ec9-b970-a842724880ea |  | textbox | Equipment Type:
text | 29c5bf83-58d0-556f-92ca-4404d9c3b2bf |  | textbox | Manufacturer:
text | 3f11dbde-edf2-5bbd-8c1a-ca5495acda6f |  | textbox | Model and Type:
text | 502d77c5-8f9b-582c-8fe8-11abd0c65c6f |  | textbox | Serial No.:
text | bd6fb2a4-219a-5322-ba03-0382fa934a03 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 6
text | e8563fe9-3fbd-5210-841b-411bcfb2df35 |  | textbox | Equipment Type:
text | a2683913-abd9-5c90-9c8b-40899f0ea4c3 |  | textbox | Manufacturer:
text | 8b366f34-db94-5c4d-a37b-98b8864a9024 |  | textbox | Model and Type:
text | 556b2989-7730-5701-9d81-b0d8702a4a5b |  | textbox | Serial No.:
text | 3bdbd6e4-a10e-5320-a32f-41e2025dab39 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 7
text | d9b32f47-74f7-5c54-86e7-29b5eb68f311 |  | textbox | Equipment Type:
text | c25f1b07-ccd9-545d-bcf1-70f7de3772ae |  | textbox | Manufacturer:
text | 557ae0af-ae79-52fe-ac32-5ae783bfbd24 |  | textbox | Model and Type:
text | da86f339-f33c-5594-ad94-a07efba683a0 |  | textbox | Serial No.:
text | 34b3d541-2c85-5e93-8711-8208ef1ae94c |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 8
text | 45af7411-27d7-5290-a4f3-e3c060b1732d |  | textbox | Equipment Type:
text | 439911d9-6d5a-58b9-9d9a-e5fbb711d9e6 |  | textbox | Manufacturer:
text | fbc2bbb8-1c08-5ed5-b94a-64d9a782f33c |  | textbox | Model and Type:
text | ac8e6743-b058-5e6f-bfa5-336be58119a7 |  | textbox | Serial No.:
text | 50731a42-0a37-550f-aacf-70906c6fcaa9 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 9
text | 1663dd13-3559-5831-919c-49102d9fec96 |  | textbox | Equipment Type:
text | c8f55def-8873-5711-ad58-9ea5462b3445 |  | textbox | Manufacturer:
text | fac8902a-ff44-5501-b258-36913a18b048 |  | textbox | Model and Type:
text | 9e3de27c-9b55-5e59-bc48-2a233c014957 |  | textbox | Serial No.:
text | 38356761-d8a1-5f92-89db-89d0b9e489a8 |  | textbox | Next Service Due:
checkpoint-status |  |  | checkpoint | 10
text | f44f60a4-ad2e-59a7-83c3-f267d022f77d |  | textbox | Equipment Type:
text | f1ff474c-26e8-5ddf-909d-0cdb53b8d9dd |  | textbox | Manufacturer:
text | a001f1d9-90a7-5634-9641-fc9b22fc172d |  | textbox | Model and Type:
text | ca7d7f0c-915c-5e5b-9c73-6e0c60b161d6 |  | textbox | Serial No.:
text | caafb20b-52c7-5415-9dbe-4f70c7fc52a1 |  | textbox | Next Service Due:
checklist-flat |  |  | checklist | QA 16 - EF00# |  |  |  |  | Yes | GPL QA 16 - PE Electrofusion Welding - Field Operational Sheet (CNRM) | 4347b752-6105-4ce4-ae58-3c9fa7e05b73
checkpoint-status |  |  | checkpoint | Operator Details
text | 097ec0d3-af79-52b5-a2c0-ce18b2b6545c |  | textbox | Name
text | de6205d8-cc62-5001-ac3e-29ca4b3c8bef |  | textbox | ID No.
text | f92140c3-99fc-54cb-a8bc-30e972c8287e |  | textbox | Company
text | bbd8f567-a299-50c4-b574-42d9ca170337 |  | textbox | Address
checkpoint-status |  |  | checkpoint | Welding Machine Details
text | 177d147a-7091-5ffe-a940-cdfb71abd639 |  | textbox | Manufacturer
text | e121c23a-9303-5f86-bb6a-a1f034ee6693 |  | textbox | Type/Model
text | 8e41462d-dcd9-5212-aa03-e596653b2843 |  | textbox | Serial Number
text | f59779f6-bda6-5b9d-9356-5b7af1522a1d |  | textbox | Year Built
checkpoint-status |  |  | checkpoint | Actual Pipe Size
text | 8d0e5696-0801-5a52-9e4a-155d1c29fc6e |  | textbox | Type
text | 53b764cc-6339-5609-b20e-ab314dcdf4e9 |  | textbox | Brand
text | 6e1f364a-2fdc-572f-838d-7d99dcf4965d |  | textbox | En
text | 7adfaf7d-3eb6-5215-b3e2-789c9aa2cff2 |  | textbox | OD
text | b9c69a5f-5397-511d-a582-9ce3a10b4f2e |  | textbox | Ovality %
checkpoint-status |  |  | checkpoint | Fitting Data
text | 0f7431b4-8f84-51ce-97b6-df4097d2a549 |  | textbox | Brand
text | d503c2e6-8ad9-5bd3-96f0-716baf2a4696 |  | textbox | Type (Coupling, Tee, Reducer etc.)
checkpoint-status |  |  | checkpoint | Unit Setting
text | 47785593-5b30-5119-80f9-462a82573a7e |  | textbox | Manual
text | e1436d7b-3589-5545-8fd6-7c2476e51867 |  | textbox | Automatic
checkpoint-status |  |  | checkpoint | Preparation
text | c950d7f3-d89c-5719-bce4-d67a9b387a1c |  | textbox | Cleaned and Peeled
text | 2584d68e-bbb6-5897-917d-d756d3b70386 |  | textbox | Pipe/Fitting Clamped
checkpoint-status |  |  | checkpoint | Welding Times
text | 0d6d9215-7c1e-5786-b59b-10a44cf69842 |  | textbox | Joining Seconds
text | 0714e89f-63bd-5d5a-bfc9-ebff1405eb1b |  | textbox | Cooling Minutes
checkpoint-status |  |  | checkpoint | Conditions
text | 564224b1-45f2-5473-8886-2f071d244cc1 |  | textbox | Ambient Temp
text | 2cb26253-71a8-5b0d-81ea-7f2ed705c084 |  | textbox | Weather
text | 70bcd800-1461-5128-bfc6-07899cb8ee1c |  | textbox | Preventive Measures
checkpoint-status |  |  | checkpoint | Power
text | 33f0f21b-b023-52cd-b112-2c1ec45f8b6a |  | textbox | Mains
text | 0358a0b3-4bc9-5d5e-aa37-6f2da020b627 |  | textbox | Gen Set
checkpoint-status |  |  | checkpoint | Operator Sign Off
checklist-flat |  |  | checklist | Butt Welding |  |  |  |  | Yes | QA 25 - Butt Welding Checklist | 291a1f72-d59e-43af-900a-545928e7f455
checkpoint-status |  |  | checkpoint | Operator Details:
text | 46a54668-3daf-53a8-a151-e3d03f8911d6 |  | textbox | Name:
text | 2b5d83a8-6916-5a15-864b-db62bbedc271 |  | textbox | Company:
text | 1abfa6f6-57ff-5614-beb0-a6f453afd4c6 |  | textbox | Phone:
text | 26da7c29-9908-5879-bd26-06afd54259f0 |  | textbox | Address:
checkpoint-status |  |  | checkpoint | Welding Machine Details:
text | 66ac11be-3c54-5c04-912d-d506cb74a987 |  | textbox | Manufacturer:
text | 9585ac34-0396-5687-a910-6afd1430ff0e |  | textbox | Type/Model:
text | 3717006a-52a1-5b9e-904b-55cf39bac98e |  | textbox | Serial Number:
text | d04d0eee-d87f-5773-9654-72e022766536 |  | textbox | Year Built:
checkpoint-status |  |  | checkpoint | Pipe / Material Details:
text | 56aa49ac-cf77-536c-b917-c3273ed34133 |  | textbox | Dn (OD)
text | 3473aa61-a0bd-5ae2-9abe-619e51c1b165 |  | textbox | SDR
text | fdf5fe47-d6a7-55fd-b61b-4b7d9f3f9015 |  | textbox | En
text | 8fb7d4e4-466c-5ec5-a881-10d733926107 |  | textbox | Type
text | a36004fa-1394-5ba6-a3f0-d4855d41565b |  | textbox | Parameter
text | 27378260-60c9-5c5b-b8a4-a6addaa79470 |  | textbox | SLP
text | 9ab68ca3-d26d-5bde-9e60-93d9896bca6f |  | textbox | SHP
checkpoint-status |  |  | checkpoint | 1
text | 0db8d60d-7522-5294-8183-cdfea08ef810 |  | textbox | Time
text | f5a8f40e-b467-5125-a090-edf393b5d733 |  | textbox | Ambient °C
text | 1440467f-5fde-5121-9ea8-a6e5a2800a42 |  | textbox | Heater Plate °C
text | 00dd074b-a686-53b6-8cec-6096504ae3e9 |  | textbox | Drag Pressure
text | 2400e408-8c18-5c31-8fd7-e44f93c2ef81 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | a9fd3c12-5904-59ac-9b3d-fc9f2c4df8c6 |  | textbox | Bead Up: t1 (Evidence)
text | 4c773931-c621-5bb5-b506-872ee39facdd |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 099e0b88-7dc5-5ccd-8022-ce71aa78bccb |  | textbox | Heat Soak: t2 (Seconds)
text | 4365a50d-2804-556c-83a8-f4d469b5e628 |  | textbox | Change Over: t3 (Seconds)
text | f77ed4e8-f999-54f6-a7e0-cbe0c172e5a8 |  | textbox | Pressure Up: t4* (Seconds)
label | c4894126-b54c-5136-9637-7fd9b4b213c5 |  | note | *t4 not applicable for SHP situations
text | 4a131c2e-c3d9-5b81-a50f-6a4af866e043 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 46cddc23-a2e1-5dea-b4e9-ca6bb1e5d16d |  | textbox | Weld and Cool: t5 (h:m)
text | e6defa1e-93e0-59df-9fa3-e2a42ab8ed28 |  | textbox | Rough Handling: t6 (h:m)
text | c30bd40f-f2cb-59a8-9753-f37f19ab31e5 |  | textbox | Bead Size: Min
text | d78eb3b5-1cb3-57a1-a6ef-5964108cdcfa |  | textbox | Bead Size: Max
text | 7e4c5935-5272-5a3e-85b5-3bf99c45bc10 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 2
text | 7858abc5-428a-54ed-8fef-c37697469294 |  | textbox | Time
text | 1cfa4730-2456-52a4-9929-12d7417a31cb |  | textbox | Ambient °C
text | 3c9c2a26-c894-52df-8a0a-f068a48df402 |  | textbox | Heater Plate °C
text | 84339dc2-878f-5dfe-92de-21e71a1e4759 |  | textbox | Drag Pressure
text | 7c2e3e5f-bfa4-5f80-b156-db516e6803f3 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 56b89cfa-138d-53dd-b4d7-cf0582bd5081 |  | textbox | Bead Up: t1 (Evidence)
text | 4cd79080-ad88-5291-a420-864d9ecf123f |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 5e06c1f4-5fb1-5372-9436-1256a3452506 |  | textbox | Heat Soak: t2 (Seconds)
text | 5bb56bcf-9bf0-5f44-bac0-543c14cb09e0 |  | textbox | Change Over: t3 (Seconds)
text | d365fd07-deac-5fa5-b778-cf586149acef |  | textbox | Pressure Up: t4* (Seconds)
label | 6625be94-0187-52f7-9f4d-6b0881825de1 |  | note | *t4 not applicable for SHP situations
text | ef636e50-3085-5671-9d2c-995d1539c53e |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 9771b85a-af6c-5693-960b-d1662063818f |  | textbox | Weld and Cool: t5 (h:m)
text | 97a80bdc-cf6c-5e66-b367-ccbad6ab6b3f |  | textbox | Rough Handling: t6 (h:m)
text | a0ca4822-cfa0-5a85-9305-d2323108f15a |  | textbox | Bead Size: Min
text | f2f58170-c484-57e4-a1bd-b6606185c49e |  | textbox | Bead Size: Max
text | 8c762868-6b9b-500c-bd41-454e79b789c3 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 3
text | 37c593c4-fe01-5350-bb10-d64a0893c68f |  | textbox | Time
text | ef19d41f-da99-57bb-8f40-3c067a66de5a |  | textbox | Ambient °C
text | 6276b928-ddcc-5bff-b3a5-13d24fac9aa9 |  | textbox | Heater Plate °C
text | 20841de0-1811-54fb-af1f-fba13a0ac8d4 |  | textbox | Drag Pressure
text | c1be99a8-d192-5c6b-b7cf-40c7fb0688c3 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 7b6c08a6-2e8e-5d9e-9546-94190f68b8aa |  | textbox | Bead Up: t1 (Evidence)
text | d17558db-4cc7-5545-bf8b-1aa2e2f54ddc |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | f56b19b7-7670-59a6-a0f0-47ecadd9008d |  | textbox | Heat Soak: t2 (Seconds)
text | 55574ce8-c096-5dfb-9bc6-055804e07282 |  | textbox | Change Over: t3 (Seconds)
text | f91cc93c-7588-5634-ad13-b2e294327807 |  | textbox | Pressure Up: t4* (Seconds)
label | d6c29471-709d-573e-9533-f3c4664ef232 |  | note | *t4 not applicable for SHP situations
text | e25a490d-2e19-5b38-bae2-bbac03dad96f |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 99635b19-e826-5e89-9411-e27801a4a38e |  | textbox | Weld and Cool: t5 (h:m)
text | 4d8f28ab-e025-5d13-b1ca-e82586be5a2e |  | textbox | Rough Handling: t6 (h:m)
text | d7b56e20-1e16-5422-a8f2-cc915f232800 |  | textbox | Bead Size: Min
text | 4dd96d85-f6cd-5391-8bfc-ab03c721e08a |  | textbox | Bead Size: Max
text | ce572f4b-3a9a-52f8-9204-0796e056b4c0 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 4
text | 51daddf4-f5ae-5f4e-9634-ee241615fd92 |  | textbox | Time
text | c4a74ddc-4dce-5ace-a620-e104b196d494 |  | textbox | Ambient °C
text | 6c9b499b-cff3-5937-b360-ce6decc063ee |  | textbox | Heater Plate °C
text | 49ba7e6f-08cf-57d9-ade3-168db33509ea |  | textbox | Drag Pressure
text | 4f4f6de0-69db-5755-ae12-cea2cbd7df0d |  | textbox | Bead Up: P1 (Kpa/Bar)
text | a7532573-46f7-5e0f-8463-da4ff38946c9 |  | textbox | Bead Up: t1 (Evidence)
text | 0123f480-9e99-5c8f-9531-bc8fbe1d24b0 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 3dd77afe-a845-5e29-b997-ab2eaddd96b1 |  | textbox | Heat Soak: t2 (Seconds)
text | 2c300354-a2c4-558e-b6dc-de91a259d66f |  | textbox | Change Over: t3 (Seconds)
text | a1b5b247-199e-5cff-954b-e5d3f1fd4cb0 |  | textbox | Pressure Up: t4* (Seconds)
label | 70286c1b-6c09-5500-9d52-93e488c4a136 |  | note | *t4 not applicable for SHP situations
text | 3ac31eb6-dad3-5fe3-9c4c-1d08d2845f0f |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 8ba47d42-db0e-52c2-8127-a6589ae88a10 |  | textbox | Weld and Cool: t5 (h:m)
text | 9b364ae5-7fda-5f80-b19a-d734900c5d90 |  | textbox | Rough Handling: t6 (h:m)
text | 7404fa90-02c6-51b5-bb2e-7becf2a552b2 |  | textbox | Bead Size: Min
text | 00609065-4f58-5d9f-856e-211c2e3e7597 |  | textbox | Bead Size: Max
text | 540fb917-4ed2-58f1-801f-3483011fef4d |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 5
text | 13239f5f-1f8a-5019-b566-9e319c80acd9 |  | textbox | Time
text | 5b118ae6-4ba9-5bad-8975-91ae7311b7b9 |  | textbox | Ambient °C
text | 879505e6-6aa5-5bf0-8162-5ec7f85a085f |  | textbox | Heater Plate °C
text | 1041f8c1-e35e-58bd-b9e1-fa037cd4b21c |  | textbox | Drag Pressure
text | b4570a54-9b5e-50d1-a7ac-dbfff9480f0f |  | textbox | Bead Up: P1 (Kpa/Bar)
text | a79dcfae-0969-5a9d-89c5-ad4ad3082e0f |  | textbox | Bead Up: t1 (Evidence)
text | 6748028d-2b9b-5290-8c21-98e9f8dfac93 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 1a2bef15-4acc-53cf-bb48-95e2f565c83c |  | textbox | Heat Soak: t2 (Seconds)
text | d6ec3494-e711-5413-8f7f-2d91f7320dc9 |  | textbox | Change Over: t3 (Seconds)
text | 2e717ebc-4a9b-595c-8816-1af63b4a9e58 |  | textbox | Pressure Up: t4* (Seconds)
label | 57db01d7-e6c2-5e37-a3cd-74bf3c938b9e |  | note | *t4 not applicable for SHP situations
text | 99c43286-1200-5dd7-bc4b-b0ec941959a9 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | ba5d1f54-3d21-5656-85d5-60c8df82a31a |  | textbox | Weld and Cool: t5 (h:m)
text | a646bad0-5ab4-5664-a5c3-7e59553a3e80 |  | textbox | Rough Handling: t6 (h:m)
text | e7ac60f7-3ab0-5562-bd49-1ee193c5719b |  | textbox | Bead Size: Min
text | 86f7e9b4-141c-54c9-a855-4aaa2c7b027f |  | textbox | Bead Size: Max
text | 44306b91-0190-5627-8049-51e163f997dd |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 6
text | c9f3a0fe-2fab-5a91-89b1-9764a223b93f |  | textbox | Time
text | 41c4a495-7520-57b9-bce3-7878bae669ef |  | textbox | Ambient °C
text | c808acf5-2f07-502e-9688-2f24492af699 |  | textbox | Heater Plate °C
text | 30d8d23c-105a-52c2-a741-bd834b3f37dd |  | textbox | Drag Pressure
text | a8a93726-6d74-5c1d-8648-db8e18b1b003 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 530a314d-5ab2-5605-80a7-aa264c1b45ef |  | textbox | Bead Up: t1 (Evidence)
text | 941274f2-a3f7-5f34-99bc-5e04bab74876 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 82385811-9bab-5c69-b475-b583f7583ae0 |  | textbox | Heat Soak: t2 (Seconds)
text | dcb2556a-fa5a-51ba-b67a-19bcf4c3428b |  | textbox | Change Over: t3 (Seconds)
text | 3f1a67ea-768c-5f79-9fdc-662c76dbf4b4 |  | textbox | Pressure Up: t4* (Seconds)
label | dc700e13-9645-50bf-a154-c34f8c0b288e |  | note | *t4 not applicable for SHP situations
text | 096898ab-46e8-56b9-8bdc-e55533668d76 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | b8bcef6c-5667-5690-b507-c03dee966d50 |  | textbox | Weld and Cool: t5 (h:m)
text | dcc821c0-9918-5f5a-867f-0aab3b249829 |  | textbox | Rough Handling: t6 (h:m)
text | 73aacf78-7d9b-544a-b824-435aab9e1b64 |  | textbox | Bead Size: Min
text | 1c2dd7d6-2b2a-5e42-9c37-6910e41eb33f |  | textbox | Bead Size: Max
text | d09127a9-51a0-556a-845e-512a56f4f8e7 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 7
text | 0c10e1be-c838-5343-98b6-642a7e8903a0 |  | textbox | Time
text | e52142b7-2655-54c8-92ce-c5658f09a5e9 |  | textbox | Ambient °C
text | d2ecc2ee-cbbd-547b-bf15-7744dad17c30 |  | textbox | Heater Plate °C
text | 2a6d8a9c-192a-5295-ba4f-3ee1805b3462 |  | textbox | Drag Pressure
text | cee2da90-ab6d-5722-a379-f620e6e3e210 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 0ffa0f68-f28d-59d5-bd59-7c06d3a79aa5 |  | textbox | Bead Up: t1 (Evidence)
text | 2ad53234-469f-5ab3-97c2-f642a7f37820 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | ccbecc9a-2c4b-5d30-8e26-31c041316285 |  | textbox | Heat Soak: t2 (Seconds)
text | 58432c0d-3dba-520f-a019-38eb82315dbb |  | textbox | Change Over: t3 (Seconds)
text | 466e8485-db20-5f7e-8532-bba280995899 |  | textbox | Pressure Up: t4* (Seconds)
label | b7fab505-9b68-5b63-a8e1-1795df504af5 |  | note | *t4 not applicable for SHP situations
text | 9f0933c1-1a99-51bf-9aee-dc8a8f9c3429 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 9b9dc124-4452-58cb-8e11-4e0d6d3ddb08 |  | textbox | Weld and Cool: t5 (h:m)
text | cae2a92e-d62c-597b-960d-bbdd9d2448c1 |  | textbox | Rough Handling: t6 (h:m)
text | df6274ad-0d65-5d2f-8ad0-5d8e51dfac89 |  | textbox | Bead Size: Min
text | a761fec6-c829-5103-ae44-caca2694b87c |  | textbox | Bead Size: Max
text | 1b2a5930-c652-5fdb-8078-744c32476a49 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 8
text | 866722b3-aa94-5c05-b768-e3f3c2afd1a6 |  | textbox | Time
text | 931196fb-778e-5314-8f70-97a6037357d8 |  | textbox | Ambient °C
text | 121fa6b5-5566-5ba0-8f85-73da1c8dcae4 |  | textbox | Heater Plate °C
text | 161b7d12-a950-5c51-8f61-471846a81f37 |  | textbox | Drag Pressure
text | f4c8a800-30d2-5ff2-b156-555ff94bbc5e |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 9c00aa83-30d1-52d3-bc6f-fc66f10bf475 |  | textbox | Bead Up: t1 (Evidence)
text | 5b72a478-b2f7-5141-88ad-3a0cc23532ce |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 1a347705-2201-5a16-b549-96f01a7eaacf |  | textbox | Heat Soak: t2 (Seconds)
text | b304443e-23e1-59f2-8802-67ae6436e952 |  | textbox | Change Over: t3 (Seconds)
text | dc495ef6-2fc6-55ee-a814-61946a50cfc7 |  | textbox | Pressure Up: t4* (Seconds)
label | 349a7808-1e9f-5d18-8f70-156f8e9aa373 |  | note | *t4 not applicable for SHP situations
text | 18e95f0c-08c5-50fb-8da6-de7c4ee7881e |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | c3196fd5-dfe6-50b1-aeb3-ae8a06b4b70b |  | textbox | Weld and Cool: t5 (h:m)
text | 8aab0d41-c8af-5fe1-b35b-30b1be882210 |  | textbox | Rough Handling: t6 (h:m)
text | 9bdee718-d0d9-57fe-9915-e734d0dccc1a |  | textbox | Bead Size: Min
text | bf57a7e7-88b4-5d3d-9492-6ef3920cfadd |  | textbox | Bead Size: Max
text | fc5a6f22-71b0-517f-9103-d45edbd1e8df |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 9
text | 2c79cefc-aaf9-57b9-8781-5b26502d45a2 |  | textbox | Time
text | e46d12b4-751f-5f12-b435-5de42b6ea1f5 |  | textbox | Ambient °C
text | e1c59bcb-dd92-5fd0-ae3c-a276e79e5f90 |  | textbox | Heater Plate °C
text | 8d92a942-eaf6-5c37-97c3-17334f3afb28 |  | textbox | Drag Pressure
text | 79138fa8-783d-5ae3-bdf0-6db58ef9daf0 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 35d1c479-4710-5411-b51f-520e9ee2bd7f |  | textbox | Bead Up: t1 (Evidence)
text | 4c7bff51-fd41-580b-b366-2572f5019c6b |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 0231f7b6-2bbc-52fd-9293-2720bf89c590 |  | textbox | Heat Soak: t2 (Seconds)
text | a6d2663d-f402-54c3-b90b-5647ad1943bd |  | textbox | Change Over: t3 (Seconds)
text | 8dba2c13-16d5-50e0-99b1-7829ba447443 |  | textbox | Pressure Up: t4* (Seconds)
label | 99e5e633-b91b-59f1-95f6-c883fd560261 |  | note | *t4 not applicable for SHP situations
text | 14cd0078-2664-5624-88df-1a0a070f69d5 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 689a73a5-db8e-50cc-8e15-e973bdc64f46 |  | textbox | Weld and Cool: t5 (h:m)
text | 685abf86-ae3f-5485-bf90-dbae9f453d0f |  | textbox | Rough Handling: t6 (h:m)
text | 320c993e-72ba-58c6-8b02-52f41709d669 |  | textbox | Bead Size: Min
text | ed77ab77-b645-5da0-97f0-e1fa2011bc28 |  | textbox | Bead Size: Max
text | 60c75f13-475d-5a5e-bd2e-02d1de1be078 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 10
text | 13ebd8cd-7e46-5e58-ac80-3969e63659b6 |  | textbox | Time
text | 3db617d6-c55e-5b1b-9bc0-2060de7cc58e |  | textbox | Ambient °C
text | e76f7ff5-3752-555e-b9b5-2b68da0eeb92 |  | textbox | Heater Plate °C
text | 678b39f4-b138-592c-ad7a-ff86edcda462 |  | textbox | Drag Pressure
text | fe052fff-e524-510d-90ae-d0e0b378bf2b |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 95f3bc5d-4bab-5569-8b81-c518272cc777 |  | textbox | Bead Up: t1 (Evidence)
text | 0db83871-a500-5c23-80b7-d414bac79e91 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 62de5984-72e4-58cb-abc0-3ed4ee1ed36c |  | textbox | Heat Soak: t2 (Seconds)
text | 6510e35f-c6db-5791-97a1-c218145efeea |  | textbox | Change Over: t3 (Seconds)
text | 38c66fc8-c2f7-5be1-849c-9b2712b2a659 |  | textbox | Pressure Up: t4* (Seconds)
label | d0a4931a-daf3-52be-8357-3e56e9a44643 |  | note | *t4 not applicable for SHP situations
text | 4371880b-5991-54f0-97a7-ebac0dfd77c7 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 9a0b6d19-2df5-5c23-ad28-4ac5854fd1dc |  | textbox | Weld and Cool: t5 (h:m)
text | 5c343646-c8e7-5eea-a1e8-24990a277796 |  | textbox | Rough Handling: t6 (h:m)
text | ffcac9cd-f968-55b3-9b14-61a405f27661 |  | textbox | Bead Size: Min
text | 6ce557ce-f756-53bd-a2e5-6fda7e99d876 |  | textbox | Bead Size: Max
text | 91307927-b19d-5b0a-b370-aaada4f41cc6 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 11
text | 53b2f860-eea7-5a3e-a64e-901575ae0fd9 |  | textbox | Time
text | 543469d9-517d-54a9-ab4d-040df6becd9f |  | textbox | Ambient °C
text | 4019160a-8475-5dd7-86cf-25bd345c2583 |  | textbox | Heater Plate °C
text | 96f95b28-4bee-567a-958e-b24b477dffd6 |  | textbox | Drag Pressure
text | d548ba3a-c539-591f-9c6f-379b7e74daa7 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 46c89aea-23a3-5471-9764-5d39ee0b24a0 |  | textbox | Bead Up: t1 (Evidence)
text | a486b75f-2f39-5fdc-af45-e5f97f1427d7 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 84c6f7a8-855e-55c4-8aad-fb74a5c66dbd |  | textbox | Heat Soak: t2 (Seconds)
text | f0175d97-9f0e-5c5d-8c01-4204b9b66b0b |  | textbox | Change Over: t3 (Seconds)
text | cfefa22e-cde7-51e3-8be6-c4c624a55533 |  | textbox | Pressure Up: t4* (Seconds)
label | 64337296-f6c1-56d2-9d37-e5887baa0618 |  | note | *t4 not applicable for SHP situations
text | 25b7cc88-e7da-5c46-9a9c-f013d1b7dcb4 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 8280b597-2298-5ae2-81b5-e94025c75b82 |  | textbox | Weld and Cool: t5 (h:m)
text | a2e3befa-30db-5d9b-923e-a2e43e81c4a5 |  | textbox | Rough Handling: t6 (h:m)
text | 90d16c4d-4a09-554e-a5b1-a3e414b0865d |  | textbox | Bead Size: Min
text | 26115009-8dbf-566d-9438-ac58659694e7 |  | textbox | Bead Size: Max
text | 93bc5a1c-5698-587c-acad-5fdd8fcd9b29 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 12
text | ff13f2af-268d-5c52-8f57-66ce637063dc |  | textbox | Time
text | 9e9c46cc-0690-5a79-a35e-bf57c9a2025e |  | textbox | Ambient °C
text | 0b15c02f-8ef8-5ede-a025-777ff9c0ce25 |  | textbox | Heater Plate °C
text | 106acc3a-add6-5b20-a30c-23487e6d58ea |  | textbox | Drag Pressure
text | b70e0548-ae95-554f-b70e-b2c68afde17e |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 42779eba-89d8-5e6f-9204-d94c047daa35 |  | textbox | Bead Up: t1 (Evidence)
text | a40f693d-96ce-560c-8582-487d21756759 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | 8975e037-bcc2-51fc-ac6f-0a4318bf354a |  | textbox | Heat Soak: t2 (Seconds)
text | 3c75c233-e69d-5d5a-a6c9-43a26cbf3812 |  | textbox | Change Over: t3 (Seconds)
text | 5c3388be-bb16-5984-84a4-72e50ead1129 |  | textbox | Pressure Up: t4* (Seconds)
label | a787c89d-9594-568d-bca6-b607465311a4 |  | note | *t4 not applicable for SHP situations
text | 25fab38e-55a5-502b-b13c-57b6b808cbe1 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 2d95d398-025d-59c6-9768-000abbc056aa |  | textbox | Weld and Cool: t5 (h:m)
text | 2e6e8933-b8a0-5b82-939c-09796f5540d3 |  | textbox | Rough Handling: t6 (h:m)
text | ab34fddd-b094-5057-9a65-9b7d7a189285 |  | textbox | Bead Size: Min
text | 9cb40fac-ad4a-5be9-8ad4-a7842288cce2 |  | textbox | Bead Size: Max
text | 988e914e-850b-57fa-b02d-ee5b6c102b84 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 13
text | 748b51fe-3a53-5c2d-bcfd-3df1d00ca0d1 |  | textbox | Time
text | ac72861e-30c7-55cc-9466-968c3f6de48c |  | textbox | Ambient °C
text | db47b348-f555-57f4-b63e-7bfd6b784815 |  | textbox | Heater Plate °C
text | a92d4d48-a6c9-51c3-8e79-952642d69c06 |  | textbox | Drag Pressure
text | 28bc6b16-0ae2-5641-ba6c-004068d1041e |  | textbox | Bead Up: P1 (Kpa/Bar)
text | 2fed65ac-def0-5f82-b88c-b811da9965a1 |  | textbox | Bead Up: t1 (Evidence)
text | 82259554-c0c2-56b9-b36f-3b55cffad1b6 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | d381bdbe-33a0-54b6-9629-ef55fd71e903 |  | textbox | Heat Soak: t2 (Seconds)
text | ed458da1-4766-50c4-b3a5-5188b32c8aec |  | textbox | Change Over: t3 (Seconds)
text | ba3c330d-f2a7-5fb1-9e56-e65bd6782a91 |  | textbox | Pressure Up: t4* (Seconds)
label | 009742be-7b0d-50ac-98e8-5eb3923b5977 |  | note | *t4 not applicable for SHP situations
text | adfbec0d-e7f4-5f29-8019-de03bb33a055 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 3e7bf794-a143-56e7-8068-d7d7a0ca5720 |  | textbox | Weld and Cool: t5 (h:m)
text | 5da0e128-0c38-538a-8723-f23ad0ab15de |  | textbox | Rough Handling: t6 (h:m)
text | 298241c2-04d5-53a4-9682-f47274449c44 |  | textbox | Bead Size: Min
text | facd45ab-fee1-5b38-8f4c-125657c1d7c6 |  | textbox | Bead Size: Max
text | 6ada4d34-58fb-59e9-9956-968fcf92af91 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 14
text | a7612892-71fd-5c4e-910d-64ae742ac696 |  | textbox | Time
text | e76a5509-9558-5be7-8d62-c8b58e36f04e |  | textbox | Ambient °C
text | 04fd5155-5e47-5e7f-9612-e8e16cf52c40 |  | textbox | Heater Plate °C
text | 862c1535-e1da-5054-86a6-cff4772c11b9 |  | textbox | Drag Pressure
text | 8d9b7892-d0c9-54e1-8d53-df1aa92a7054 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | f9c0ce2f-1d3e-52c4-b282-579531e7d6b4 |  | textbox | Bead Up: t1 (Evidence)
text | cf18d780-76cf-5c75-be93-07a817646e14 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | dc237503-ebfb-5a09-abdf-fc5c1eb24f0d |  | textbox | Heat Soak: t2 (Seconds)
text | 71caa803-60a9-520d-bc3f-d697de1cd147 |  | textbox | Change Over: t3 (Seconds)
text | 93054656-87b0-5c6c-bc5e-92d7612ef99f |  | textbox | Pressure Up: t4* (Seconds)
label | 0f0dac9b-b2b8-5ced-a346-68bf1137b01c |  | note | *t4 not applicable for SHP situations
text | 67bf54cb-515e-560b-b0af-a0c385b93180 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 91a16908-7a75-56fa-8e74-548795f0a95f |  | textbox | Weld and Cool: t5 (h:m)
text | 0b074d4a-a6cd-5238-9064-d11a75c4bd12 |  | textbox | Rough Handling: t6 (h:m)
text | 2a10f2cf-e0be-5a79-84e5-33dbcd522e97 |  | textbox | Bead Size: Min
text | 8d2e450b-487d-5837-b735-f94a0621e840 |  | textbox | Bead Size: Max
text | b1d20e13-32e8-514a-a611-a247bcc3e657 |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 15
text | e4908b7e-ea08-566c-833f-65fc5ecfbdc3 |  | textbox | Time
text | 5a214473-d982-5938-a146-47bc64d4efd4 |  | textbox | Ambient °C
text | a49ff0e6-04ac-539a-9bf0-32e64a73816f |  | textbox | Heater Plate °C
text | f318954f-5b32-5b37-978d-b9555a361be1 |  | textbox | Drag Pressure
text | 7d42aa3f-83c3-5159-86b7-70aeb7e88d3d |  | textbox | Bead Up: P1 (Kpa/Bar)
text | eb18063d-dd2b-52d9-99ef-6e743cf85068 |  | textbox | Bead Up: t1 (Evidence)
text | ecce34d2-5aa5-5df7-9927-83ef5f51f867 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | e0494f53-b7af-5b2f-b862-da90602027d7 |  | textbox | Heat Soak: t2 (Seconds)
text | d828b996-b513-512f-8697-9fcdcd50f51a |  | textbox | Change Over: t3 (Seconds)
text | 0c57053d-043e-5704-9e5c-a5dcf43126b6 |  | textbox | Pressure Up: t4* (Seconds)
label | 41c80c9b-7961-5d92-ad7c-f25e0d5f71f6 |  | note | *t4 not applicable for SHP situations
text | 246d0ed9-97fa-576b-b262-cca124664915 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 49d17b6b-0d97-5422-b887-0e3a06a3e14d |  | textbox | Weld and Cool: t5 (h:m)
text | ef20136f-08df-5ac4-af0a-535f4f28192c |  | textbox | Rough Handling: t6 (h:m)
text | b6c69118-760d-5c00-bb10-5efafb78912b |  | textbox | Bead Size: Min
text | 9215262f-c875-5d5b-8b74-92dd0c2831f6 |  | textbox | Bead Size: Max
text | 9b817919-9485-5e3c-a7b9-25d8b93704eb |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checkpoint-status |  |  | checkpoint | 16
text | 83cd7473-1388-5a2a-8755-b5def54256b8 |  | textbox | Time
text | e8e4f420-3047-5608-8132-e29dc812ffa5 |  | textbox | Ambient °C
text | 21051102-a589-51f4-aad9-3b8ad92af892 |  | textbox | Heater Plate °C
text | a2973ab5-51f3-520f-a3c8-75ce65ff5551 |  | textbox | Drag Pressure
text | 3d051440-88a0-5abf-adef-2faf517a94e5 |  | textbox | Bead Up: P1 (Kpa/Bar)
text | b0095b18-9a25-56f5-b2bd-997dba748629 |  | textbox | Bead Up: t1 (Evidence)
text | 3b071995-d27c-5a53-8e1a-778218da0782 |  | textbox | Heat Soak: P2 (Kpa/Bar)
text | efc9070f-0a39-50cb-802f-9db1127431da |  | textbox | Heat Soak: t2 (Seconds)
text | fcc4d142-cece-50e8-91fc-205fd24f6a5f |  | textbox | Change Over: t3 (Seconds)
text | 7ecc3263-dcfc-53ab-a7e6-eddd9dbb7125 |  | textbox | Pressure Up: t4* (Seconds)
label | 551ac8b9-5f7c-5249-9810-1ac1c85355dd |  | note | *t4 not applicable for SHP situations
text | bbfbb28d-f2f3-53e2-bfdd-7c0f3b219350 |  | textbox | Weld and Cool: P3 (Kpa/Bar)
text | 25be3ce1-36a8-5ea1-8a27-d8fb5dbb946e |  | textbox | Weld and Cool: t5 (h:m)
text | 4836e23b-4258-54fd-9cd4-d2c17018b188 |  | textbox | Rough Handling: t6 (h:m)
text | de193e04-fb91-522a-b753-b73aaba7c062 |  | textbox | Bead Size: Min
text | 686dede9-217b-5301-a4c1-e1ecf0d79483 |  | textbox | Bead Size: Max
text | b276dde4-4711-5011-80a6-5bf9e134857d |  | textbox | Comments
holdpoint |  |  | signoff | Add Operator Signature
checklist-flat |  |  | checklist | Water Meter Accuracy Test |  |  |  |  | Yes | QA 17 - Water Meter Accuracy Test | 12ed8b6c-91c9-4b8f-9b04-328ab93f51cc
checkpoint-status |  |  | checkpoint | Water Meter Accuracy Test Details:
text | 3314fb28-6004-50b1-9780-eefb1b71510e |  | textbox | Date:
text | 430b7245-e716-513b-9047-9c4e4fc6ca44 |  | textbox | Project:
text | 208dde16-7f35-52ce-b4aa-bf9e249d1072 |  | textbox | Location of Water Meter:
text | 72a0013a-b8c3-5856-a4c3-a54ed8e566ff |  | textbox | ID Number of Water Meter:
text | 06f570b6-b549-598c-991a-21c07d01fa4b |  | textbox | Model & Manufacturer:
text | fdbfa2df-492b-534b-b8f1-f7cc5a3e7405 |  | textbox | Current Counter Reading:
text | e89edae7-6e74-57cf-b7c7-7e878428911c |  | textbox | Zone/Appliances to be Metered:
text | 3e193013-f935-59a7-852f-40ae23dec67e |  | textbox | Pulse Rate:
checkpoint-status |  |  | checkpoint | Measurement Apparatus
boolean | 1e41da32-9761-534a-960e-e0f9e7e6b264 |  | tickbox | Bucket
text | 360faded-a3ea-5cfa-a0fb-f1b75e6c2aa8 |  | textbox | Bucket Size
boolean | ea7ae63a-b9ad-5afa-9fe1-43aed4f6003e |  | tickbox | Water Meter
text | 0e4bdf03-1f7b-5f0b-aab1-898e3d630651 |  | textbox | Calibrated Date:
text | 649b76ce-264e-5376-aecb-d46f59de9eda |  | textbox | Other
checkpoint-status |  |  | checkpoint | Measurement Method
label | 3622e18a-b1b3-56de-bf4f-0028521a67c5 |  | note | Isolate all fixings
label | 03c1d46e-10a6-5a14-9b1c-a3947a0e30c9 |  | note | Place bucket at outlet of fixture and fill
label | ccb3121d-2dfa-5a79-a724-46ce9a34d3c4 |  | note | Fill in completed counter reading and minus "current reading" to measure accuracy
text | 32d2480b-6c21-5252-87db-7f5c7291ba03 |  | textbox | Completed Counter Reading:
label | d7938c77-17a2-5fd2-95b5-d442fcd94056 |  | note | Accuracy
text | a90c66bb-a98c-5fb1-9288-5e92871b9098 |  | textbox | OK
text | 39d33286-e360-576e-ba75-e0e81e5c5b15 |  | textbox | FAILED
label | aec8060c-cb17-5fa6-98d5-69f07b2c8640 |  | note | Replace Counter and Re-Test
text | c14044e9-0ffe-5ba8-910d-9271ac1424a1 |  | textbox | OK
text | b6b31f97-d145-51b1-9ab0-d60631df6e69 |  | textbox | FAILED
checkpoint-status |  |  | checkpoint | Pulse Check
label | c96818d2-e638-55e9-a052-1c9937861a16 |  | note | Method:
label | 6e3c2261-ce63-506b-9a84-1f03bdcf0a8d |  | note | Connect multimeter to the 2x wire connection points on pulse kit and set multimeter OHMS
label | c0ffe883-62e1-5c4c-bcae-49e31526dd70 |  | note | Turn a fixture on and wait for pulse reading on multimeter, then stop flow immediately
label | f4399fce-a9c1-5503-935a-aa5d1cbb5d4b |  | note | Measure bucket contents:
text | 502a4ba5-22e3-53f4-8c1d-97cebc66e345 |  | textbox | Pulse Registered:
label | 9f07c428-edf3-5779-8f6e-58de75fc7371 |  | note | No Pulse - Install new pulse kit and repeat process
label | 5b8950c5-0956-5cc9-a698-3fa49180f8ad |  | note | If Pulse registered OK
text | 6c34fdbd-6bdd-5043-82cf-369de26354df |  | textbox | Pulse Accuracy:
label | 2dc63887-83ae-51bf-84c1-da817edca9d2 |  | note | (Bucket contents match spec at top of page)
label | 46079bb5-7f41-53aa-930b-73bf874e3ebd |  | note | Failed - Install new pulse kit and repeat process
checkpoint-status |  |  | checkpoint | Sign Off
text | ad50d9d8-26e8-56f3-bdd2-19531046f2ec |  | textbox | Name - Geschke Representative
holdpoint |  |  | signoff | Signature - Geschke Representative
checklist-flat |  |  | checklist | Fire Hose Reel (FHR) Test Report |  |  |  |  | Yes | QA 20 - Fire Hose Reel (FHR) Test Report | 6a56f799-4da3-4202-8d4a-b0d63e617d05
checkpoint-status |  |  | checkpoint | Fire Hose Reel (FHR) Test Report:
text | 8d58cc5e-d3fc-5537-a781-b5571a20430c |  | textbox | Location of FHR:
text | 1ed8786e-2a65-5227-a0be-d91bf822c43e |  | textbox | ID Number of FHR (If applicable):
text | 9f7035bf-b64c-5d42-b295-a7ac668fd4db |  | textbox | Manufacturer:
text | 0f33f513-1bcf-5cfc-a274-acdca3b342ef |  | textbox | Model:
text | aa16ce4a-c82e-5227-8bbb-a2985e1297c1 |  | textbox | Size:
label | 1a8545b3-89ec-56ab-84d3-7b3191023639 |  | note | Aust. Standard Flow Rate: 0.33 LPS @ 210-230 KPA
button | 0c74b826-3bf4-556d-8b06-9b7497fab69c |  | button | Measurement Apparatus: | Bucket
text | 3a041336-bda3-5a41-a1c7-b87f9eee1496 |  | textbox | Bucket Size:
label | a414a564-d770-59eb-92ab-534b8553fbfa |  | note | Measurement Method:
label | dfdbc226-bd3b-5722-b029-8a8e02c33951 |  | note | 1. Connect pressure gauge and outlet to end of hose
label | 37c1a67b-ee94-5d73-86ee-7eb7e52b36b7 |  | note | 2. Note static pressure reading on gauge
label | c27e9cc1-0383-59f2-b68d-2637e16c5371 |  | note | 3. Place bucket at outlet of FHR and fill
checkpoint-status |  |  | checkpoint | Reading
label | 5576b839-cdde-581c-b9c7-874b85616b36 |  | note | 3.3L
text | 52b49b62-24c4-506e-bcaf-94d4e091021e |  | textbox | TIME (sec)
text | 566d8f60-7640-5204-a2fd-dad1340c35f5 |  | textbox | Flow Pressure:
label | 83243216-be39-528e-acbc-a0ff44e932fe |  | note | 6.6L
text | 64d238f7-5ac7-56b5-9813-338a67069a5e |  | textbox | TIME (sec)
text | 8d3e2d70-5300-5dd7-9f87-c49a717e8f62 |  | textbox | Flow Pressure:
label | cbee89ff-3b69-5b0f-9e2e-b6c1c039de16 |  | note | 9.9L
text | cc5dd111-4c12-50ac-9a41-c9fc10f0d8a5 |  | textbox | TIME (sec)
text | 18bf24da-ab70-51bb-9f2d-7f2272dced90 |  | textbox | Flow Pressure:
checkpoint-status |  |  | checkpoint | Completion
text | e8273121-15be-50a1-9f1e-fcc4a4623e61 |  | textbox | Geschke Pty Ltd. Representative:
text | bce6d576-8284-5765-ac7b-64e9f2f68f43 |  | textbox | Others Present:
text | d7b6d998-6693-5342-a037-c4ee2105006c |  | textbox | Date of Completion of Satisfactory Test:
checklist-flat |  |  | checklist | QA 8 - BGS00# |  |  |  |  | Yes | GPL QA 8 - Below Ground Pipework Checklist - Sewer (CNRM) | 1a6c24fe-f0be-4fa8-874f-e7a6ede3bf3d
checkpoint-status |  |  | checkpoint | Principal Contractor Permits Issued
checkpoint-status |  |  | checkpoint | Set out pits trench depths and runs.
text | 94c74e81-f94a-5ffa-82b3-4ac046c72f4a |  | textbox | Drawing & Revision # (or Attach photo below)
text | 254f0294-bc63-519a-8ff6-b7b0f9302bf3 |  | textbox | Survey setout completed by:
text | 0ce6ed72-a6c8-5b20-9d1b-8d2141922183 |  | textbox | Manhole Coordinates - enter Eastings & Northings
text | b9a077c0-3398-5522-b13f-e0be13de716f |  | textbox | Starting IL established - enter IL
button | 53242941-a47e-5a04-9bec-e7cca2b5ff79 |  | button | Survey confirmed drain started at correct IL | Yes, No
button | 2e7c2cba-7669-5787-824c-fe6fefc058de |  | button | Drawings attached | Yes, No
checkpoint-status |  |  | checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | 3803bd15-8842-5ec0-94a4-96397169f497 |  | note | Spec#: AS3500
text | ed1f1a09-88b1-58cb-9da1-650bb24d82af |  | textbox | Materials used:
button | 38321f98-f746-5abc-91be-0216a94bb7f7 |  | button | Approved by Principal | Yes, No
checkpoint-status |  |  | checkpoint | Bedding material, placement and compaction meets specification.
label | 35823503-264d-5c95-b51a-15a3c716bbcf |  | note | Spec#: AS3500
label | 0e21f475-bb39-5885-a22c-b7b6c18e44f9 |  | note | 7mm Q-Minus Bedding
checkpoint-status |  |  | checkpoint | Laying and jointing of pipes - RL and fall
button | bd01fe56-24f5-5377-b58f-dbcd80f4b103 |  | button | PVC pipe with Rubber push fit jointing | Yes, No
button | 23cc0248-cbac-5b53-9b42-adcc8af1e638 |  | button | Fall achieved (1:200 required) | Yes, No
checkpoint-status |  |  | checkpoint | Connections to pits and existing services as per spec and Australian Standards
checkpoint-status |  |  | checkpoint | Hydrostatic tests are carried out as required.
button | c4144c95-faf0-53ba-9ef7-475b694a1f5c |  | button | Air or Water? | Water, Air
label | 1859611a-103e-57b2-8edf-378cc57b25d2 |  | note | Inspected and recorded by Independent Certifier or PIC
checkpoint-status |  |  | checkpoint | Mirror tests completed
text | e8582c5c-3890-5625-9ad0-0951839d2af4 |  | textbox | Independent testing company:
button | f2776431-47aa-5e24-a01a-eaf3b9ad1af8 |  | button | Inspection report attached | Yes, No
checkpoint-status |  |  | checkpoint | Placement and compaction of backfill and material meets spec - attach applicable reports below
boolean | c5d4c043-2d66-564e-af33-92330a699557 |  | tickbox | Civil specification 13.4: Trench Backfill Service trenches shall be backfilled with General Fill (Type B Material) compacted to 98% SDDR within 500mm below the Subgrade Level and to 95% SDDR below this depth in pavement areas. The moisture content of the compacted material shall be within 0% and +3% of SOMC.
boolean | 42ead38c-253f-5fed-ad28-2c25ffbce6b2 |  | tickbox | 5% Stabilised Sand
text | dc3ac396-f569-533b-8121-bcc1f0051bb5 |  | textbox | Compaction testing completed by:
button | 3b79353f-d2f0-57e8-aab9-d5f41ce1ce08 |  | button | Compaction report attached | Yes, No
checkpoint-status |  |  | checkpoint | Temporary cover provided to open drain.
checkpoint-status |  |  | checkpoint | PVC/ Plastic caps to open ends
checkpoint-status |  |  | checkpoint | As built information updated onto drawings
button | a530020f-1b97-549d-a8d9-d4e4a354f477 |  | button | Drain installed as per nominated drawing | Yes, No
button | 21c7fe6e-6da6-5ffb-9b72-e89c7d17fca3 |  | button | Invert levels checked by independent surveyor | Yes, No
label | 8d454213-8c40-5a7d-ba51-861d1127d644 |  | note | As Built drawings to be updated as required
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | 9c48bf7d-734b-5b8f-840e-abb6c2fffc88 |  | note | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
label | a63175ad-7b45-55e8-b6bc-625f3689f22b |  | note | Company: Geschke Group
label | 9af93cf5-cda1-5ddb-ad56-10088992e4bc |  | note | Phone: 03 9798 1619
label | 2acd112f-f7f7-54cc-a424-0a01a5e60c8d |  | note | Address: 45 Pacific Drive, Keysborough
label | 6134e066-2e40-5961-b93c-caa3ee914894 |  | note | Project: Centre for National Resilience Project - Melbourne
label | 85776876-e27b-57ae-b67a-a2139a60ace1 |  | note | Principal: Multiplex Constructions
checkpoint-status |  |  | checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | 4627f9eb-3565-5c01-bc63-81473ba55986 |  | button | Geschke Group Signature Sign-Off added below | Yes, No
button | e59a161d-3655-5713-9c75-46aff7d4b825 |  | button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist-sectioned |  |  | checklist | Maintenance Inspection Report - |  |  |  |  | Yes | Maintenance Inspection Report (Dec 2021) | d8b0b475-a25e-47e6-9c60-59bda7a4fd1e
checkpoint-group |  |  | section | Details
checkpoint-status |  |  | checkpoint | Inspection Details - Pass once entered
text | 13c6b75a-0dae-4605-aebd-f22cf8b9ef34 | Hidden property width:50 | textbox | Site Name
text | e9dd538f-b767-48c5-9a68-71d372c010a6 | Hidden property width:50 | textbox | Date
text | a7efaae1-c737-4c27-b0db-1ca7d6edb060 |  | textbox | Site Address
text | 467bc035-0cb9-4f08-bcbe-468fafc94873 | Hidden property width:50 | textbox | Contact
text | 2ae19935-2064-466f-9412-f655a0b16960 | Hidden property width:50 | textbox | Contact Phone #
text | 609f01ea-7840-49f6-9f6e-516a4476d95e | Hidden property width:50 | textbox | Inspection Task Location
text | e651c5e2-9313-49e9-860e-b0140927eb67 | Hidden property width:50 | textbox | Item/Equipment to be Inspected
checkpoint-group |  |  | section | Inspection
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturer's instructions
checkpoint-status |  |  | checkpoint | Does the item function as it was designed to
checkpoint-status |  |  | checkpoint | Is there any reports from the customer of the item not working or any issues
checkpoint-status |  |  | checkpoint | Is the item free from damage or future damage
checkpoint-status |  |  | checkpoint | Has all parts i.e strainers, sumps and pits been cleaned
checkpoint-status |  |  | checkpoint | Is there further maintenance or parts required to complete inspection
checkpoint-status |  |  | checkpoint | Photo taken and uploaded to report
checkpoint-status |  |  | checkpoint | Item left in safe working order
checkpoint-status |  |  | checkpoint | Inspection Completed
text | 4d75975b-ada0-47b0-94b1-1864704bd95c |  | textbox | Additional Comments
holdpoint |  |  | signoff | Click to Add Inspector's Signature
checklist-flat |  |  | checklist | QA 24 - Hose Reel Register |  |  |  |  | Yes | QA 24 - Hose Reel Register | e203dc77-f3c4-476e-ba6f-ad29d90dc3f9
checkpoint-status |  |  | checkpoint | Hose Reel Register
text | 04c69248-4f50-5d0e-bab9-f0c2c3a543cb |  | textbox | Ref No:
text | e9a1de0e-57af-58b3-b95b-8ce72f49b3f2 |  | textbox | Building:
text | 24a73e08-b0f3-501e-8bec-420ec5722d97 |  | textbox | Zone:
text | b82a8918-c844-5ed7-895f-5dbe58433300 |  | textbox | Level:
text | 3da07763-abf9-5a11-9683-7b4c2c647592 |  | textbox | Adjacent to:
text | 605ce2d6-c6db-5f48-8420-bc4cfe710ae2 |  | textbox | Length:
text | 0a92798c-9f03-58b9-9264-efe250f07a53 |  | textbox | Date Tested:
text | 48d16d02-b36f-552b-a1af-c7c8f1b9b4a9 |  | textbox | Flow Rate:
button | 737b6415-ead1-58e1-be99-6ce6adfea0f7 |  | button | Obstructed Access | No,Yes
button | 1cc787a0-fbd1-5ee4-9bd3-1786008c4718 |  | button | Operating instruction visible and legible | No,Yes
button | 34efa827-de53-5270-a719-eb8ac7dac657 |  | button | No leaks throughout hose reel mechanism | No,Yes
button | 53417496-304d-52de-9d4d-52b0e3faff0b |  | button | Hose runs freely through guides | No,Yes
button | 4370dc55-52ed-5d36-9e8b-0e98609ab247 |  | button | No signs of corrosion | No,Yes
checkpoint-status |  |  | checkpoint | Result (Pass / Fail)
checklist-flat |  |  | checklist | QA 6D - Quality Control Gas Regulation Test Report |  |  |  |  | Yes | QA 6D - Quality Control Gas Regulation Test Report | 5004e7a0-76f1-40f0-96af-ed29722b6500
checkpoint-status |  |  | checkpoint | Quality Control Gas Regulation Test Report:
text | b2474475-47ea-597c-8878-544232a4436d |  | textbox | Drawing No.
text | ed2e8944-0c4a-52db-9894-3c339e0c4c53 |  | textbox | Rev:
checkpoint-status |  |  | checkpoint | Test - Flowing inlet pressure to project
text | b537697e-f43a-5a6f-994a-191577a42caf |  | textbox | Inlet Pipe and Size:
text | 006efab9-0f46-5811-b8d6-e42e873e4771 |  | textbox | Spring range:
text | 74dacd66-d2b5-550f-8945-576709d4ab8e |  | textbox | Orifice Size:
text | 2ec37cb5-2073-524c-b468-28384a70ba40 |  | textbox | Model:
checkpoint-status |  |  | checkpoint | Section
text | 8ea0efb3-15f5-57db-9f52-72ae9d5429e6 |  | textbox | Section:
text | fb0b5590-2bc7-5d62-b23e-dfe24567ee80 |  | textbox | Pressure (KPA)
checkpoint-status |  |  | checkpoint | Test upstream inlet pressure to regulation
text | 3b56a1ec-b6a5-569a-96a0-1bd2cc5523fa |  | textbox | Pressure (KPA)
checkpoint-status |  |  | checkpoint | Test downstream out pressure to regulation
text | b6671b47-9467-54b0-8646-eb78feb3f51f |  | textbox | Pressure (KPA)
text | 0972ae5d-db47-56d7-9012-d89f2015ce44 |  | textbox | Duration (hrs)
checkpoint-status |  |  | checkpoint | Adjust out pressure KPA as stated on GPL shop drawings
text | ea5f6265-653d-5a55-859f-5464cc7ff375 |  | textbox | Reading (KPA)
checkpoint-status |  |  | checkpoint | Confirm outlet KPA does not fluctuate more than 0.8KPA
text | 1430adac-1555-59a0-8559-5093ac692453 |  | textbox | Repeat:
checkpoint-status |  |  | checkpoint | Sign Off
text | 9939deb9-66c8-562a-a833-77d66f1060b1 |  | textbox | Geschke Pty Ltd. Representative:
text | 80d7b81a-d4d1-523c-b839-9ba824c6d170 |  | textbox | Others Present:
text | fbed0f45-5d5d-52e0-923c-ff33638b9491 |  | textbox | Date of Satisfactory Completion:
checklist-flat |  |  | checklist | TMV 12 Month Service Log (use a separate checklist for each valve) |  |  |  |  | Yes | TMV 12 Month Service Log V.040221 | 8a4e17bc-1334-4878-90a2-7d91f127552f
checkpoint-status |  |  | checkpoint | TMV 12 Month Service Log
text | 6f50691a-1052-508d-8942-49e4f9fee3e3 |  | textbox | Building name:
text | 4b152a5c-c292-5f2b-b65c-9bd875e1b6b0 |  | textbox | Contact person:
text | 9009d3d3-e172-5e90-98c6-2424962fd352 |  | textbox | Address:
text | fe012bfe-2595-5101-b131-a979e02183bb |  | textbox | Phone number:
text | 2474ad68-5cf5-5eb5-bfbd-2aa6b41ee866 |  | textbox | Make of valve:
text | b58ba77d-9724-59e0-b632-a2c01965168a |  | textbox | Model number:
text | cec86261-f94b-5a41-ac58-08fa2f04f68d |  | textbox | Valve location:
text | e0416798-48a1-5701-87e1-805195bb6fda |  | textbox | Room name:
text | 07f0cc2d-796d-535f-ad26-3220c5fe212e |  | textbox | Date of service:
text | 74dc33f9-1bd1-5c78-a8ca-969583863bd7 |  | textbox | Temperature: |  |  | °C
button | 34c78806-8271-5c24-911f-9d7ebdc7ae05 |  | button | Element: | Ok, Faulty
button | 7b702738-5414-58fe-a150-2d29a9bfc558 |  | button | O' rings: | Ok, U, S
button | 42b01cf6-fa34-54d8-8d06-354262c6949c |  | button | Strainers: | Ok, Dirty
button | 5b9b3278-8c97-5b0f-849a-0a296e4355c0 |  | button | Non-return Valves | Ok, Faulty
button | 3364de9b-9acd-5733-b0fa-6204cd3ed21b |  | button | Fail-safe test | Ok, Faulty
text | 71c93ee4-c284-55ce-99e2-9bd18f206e34 |  | textbox | Serviced by:
label | 4fd502bb-1d32-589f-b31f-cc82df6a231d |  | note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
checkpoint-status |  |  | checkpoint | Completion
text | bb196e3b-d980-5044-b91f-ae492fc70d5c |  | textbox | Plumber Name:
holdpoint |  |  | signoff | Add Signature
checklist-flat |  |  | checklist | Hot Water Service Maintenance Log |  |  |  |  | Yes | QA 31 - Hot Water Service Maintenance Log | b04fad3b-87a4-4ae7-ac3a-b3661c328f83
checkpoint-status |  |  | checkpoint | Hot Water Service Unit Details
text | 5ba17582-ab6f-5989-ae29-87f5fadb283f |  | textbox | Purchased from:
text | 493fe2fb-5879-5cb8-b822-680d9a6988a1 |  | textbox | Make:
text | 6a5a4743-6599-5456-8980-a14aa118f8cd |  | textbox | Model No.:
text | a3035425-7210-5171-9336-4911cfb04e8c |  | textbox | Location:
text | af109ad8-4faf-5771-b51a-69fe136b80c8 |  | textbox | Room Designation:
text | 149190a9-e305-597c-8018-331afd1b1ac3 |  | textbox | Installed by:
text | ea06dcaf-d924-5479-b384-78ff1b210cbb |  | textbox | Installation Date:
text | ffa0020b-5d50-522e-89ba-d401f8650320 |  | textbox | Number of units in series:
text | a49b22a6-39bf-5cc1-9011-51a78aaf5f3b |  | textbox | Prescribed temperature set on unit or combined package:
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturers instructions
checkpoint-status |  |  | checkpoint | Does installation comply with current requirements of the local water supply authority
checkpoint-status |  |  | checkpoint | Clean Pump Strainers
checkpoint-status |  |  | checkpoint | Clean Hot Water inlet Strainer
checkpoint-status |  |  | checkpoint | Clean Hot Water Return Strainer
checkpoint-status |  |  | checkpoint | Confirm all Valve Isolation reinstatement
checkpoint-status |  |  | checkpoint | Confirm Unit is Operational
checkpoint-status |  |  | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
checkpoint-status |  |  | checkpoint | Commissioned By:
text | 2b06b16e-168d-5fd3-9842-9300234ee973 |  | textbox | Name:
text | c18f1ab9-b5a8-5adc-956b-c7d1fe467c18 |  | textbox | Date:
checklist-flat |  |  | checklist | Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  |  |  |  | Yes | QA 5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line) | 082f88f6-6b6f-4402-8c6d-766075bbf335
checkpoint-status |  |  | checkpoint | Installation Test Sheet:
text | 3ab24f75-839e-5feb-8634-746ace1f5ec0 |  | textbox | Drawing No.:
text | a27b0c19-c337-506e-b01c-bd672377243d |  | textbox | Rev.:
checkpoint-status |  |  | checkpoint | PIPE CLIP HANGERS
text | 8c6d265d-72c8-5004-8826-735678e11270 |  | textbox | Details:
text | c9f33966-4235-5d2c-a642-55dfe9387742 |  | textbox | Tester:
text | a23e1ec7-52f8-5620-a7d7-b2bddcda1640 |  | textbox | Date:
text | 8b10b5a1-ede7-5467-be9c-8756e0fad657 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | MATERIAL AND SIZE
text | 85f2a050-6afa-5632-828b-afe3efe2bff8 |  | textbox | Details:
text | 6c47264b-1054-5e3b-a3c7-ae22638da042 |  | textbox | Tester:
text | 2306a096-48bf-5628-8f85-1ab5cb86ca41 |  | textbox | Date:
text | d31e1f32-415e-5ad2-8d6a-f453efef7a00 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | ALIGNMENT
text | f5e906a4-c6cd-5d02-9781-85aebcb826de |  | textbox | Details:
text | 730d0518-46a4-5cc3-b078-51778c4b8d8b |  | textbox | Tester:
text | 204d18fb-5407-5e02-9e0e-772c5a3c2e52 |  | textbox | Date:
text | b167628e-1b40-523f-a9b9-9bc950edd00e |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | LABELLING AND IDENTIFICATION
text | 5abc4733-91e2-5ea4-b265-e7c6756baa16 |  | textbox | Details:
text | 8974f3be-8334-55cc-af4a-2bb675612ded |  | textbox | Tester:
text | 84bad23e-8903-5866-897e-c0413010add4 |  | textbox | Date:
text | a0ca3daf-c85a-5c24-aea4-1ecc86442a29 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | JOINTING
text | 913fc093-f4bc-54b9-a317-bfecc43b50f6 |  | textbox | Details:
text | 519b6096-c428-5344-a043-a484cd7e9880 |  | textbox | Tester:
text | 905fa5ed-ce72-566f-9b3f-fac78692c228 |  | textbox | Date:
text | 04a550b5-9486-5356-b2fb-30fa1a7ccefc |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | PENETRATION SEALING
text | 9be6327d-0481-5941-bb4a-5bf15dca51b7 |  | textbox | Details:
text | c85eca5d-c701-55e4-a5af-08a875a2a68e |  | textbox | Tester:
text | 743a8e40-3b63-5297-867f-405fbe2667c6 |  | textbox | Date:
text | 7e580f26-9c6e-504a-87da-e436fdd65de2 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | FIRE STOP COLLARS
text | 0200e894-a180-549e-9b0c-989540dd4e67 |  | textbox | Details:
text | 9aa43dfe-a906-5bad-8885-4b764f7e21b7 |  | textbox | Tester:
text | 2a9328f3-06bf-5b16-8c56-3b079327bc60 |  | textbox | Date:
text | ab52bfac-c6dd-5de8-b64a-19a4de88067d |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | PRESSURE TESTING COMPLTED (QA6)
text | af5b740e-faef-5789-a3ae-8f61f4fdc16d |  | textbox | Details:
text | 055e2025-36cb-5358-b845-3077ed4db718 |  | textbox | Tester:
text | 657b7f34-25e2-5b91-8a7b-58724dae4629 |  | textbox | Date:
text | a766b5a7-0571-5221-8413-f0f52772285b |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AUTHORITY INSPECTION (if applicable)
text | 2515ced0-5814-5994-b676-f17015782dfb |  | textbox | Details:
text | 1821d907-771d-5c8a-86d7-56dceb371f87 |  | textbox | Tester:
text | a096b3af-3fc2-5ee8-9433-4cdcbaaf1aa4 |  | textbox | Date:
text | c0fd3aac-4831-56b5-9961-9b4fa4a1637a |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
text | 3f7c901e-6389-5596-a074-565185b26a1a |  | textbox | Details:
text | 41b3f8cd-36a1-5dc1-8c11-361431372622 |  | textbox | Tester:
text | 77f1edcf-168c-5878-978b-5ce8cfa53139 |  | textbox | Date:
text | d9dcab85-f7b9-5291-86ae-31dfa9e23d03 |  | textbox | Notes:
checklist-flat |  |  | checklist | Installation Test Sheet (Waste, Vent, Downpipes etc) |  |  |  |  | Yes | QA 4 - Installation Test Sheet (Waste, Vent, Downpipes etc.) | be1bc74f-83ed-4637-b1fe-a5a42f07c447
checkpoint-status |  |  | checkpoint | Installation Test Sheet:
text | 50010c6a-497e-5442-9047-6492ddcedc0b |  | textbox | Drawing No.:
text | b6c19f8e-eb8a-53c9-b4e8-67dcd34fce06 |  | textbox | Rev.:
checkpoint-status |  |  | checkpoint | PIPE CLIP HANGERS
text | 938ff211-8098-5850-9575-547557287724 |  | textbox | Details:
text | 61a94842-7c6e-541b-bad2-1b3201e79bfb |  | textbox | Tester:
text | b28b0af2-61aa-572a-ac1c-e3ca9ddd0b1a |  | textbox | Date:
text | bf76422e-333d-5726-99d8-65920e82aec8 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | MATERIAL AND SIZE
text | 99c29d93-4585-59e5-aaf6-0a0732abe73b |  | textbox | Details:
text | 0c553487-159c-5ffd-b6a3-067893b8312a |  | textbox | Tester:
text | 6d13be7e-a92e-5f79-a73b-929f25b82f73 |  | textbox | Date:
text | 9421d903-7af1-5d2c-a7f9-fbd2aabb05b0 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | ALIGNMENT
text | 77660e0b-d569-505a-a31a-b220d1e993a5 |  | textbox | Details:
text | 7d17e639-b3a4-5a7d-9976-ad0cb2ac69f8 |  | textbox | Tester:
text | ceb4259c-3937-598d-873e-fa47ea3ed01a |  | textbox | Date:
text | 70aa940b-9f9a-528e-9295-a408b66037d5 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | LABELLING AND IDENTIFICATION
text | b0528441-550f-515a-b6ee-03333d09591b |  | textbox | Details:
text | bda1a7d3-9a71-53af-a354-ceab8bfc2f14 |  | textbox | Tester:
text | 5e844718-ee95-5f26-bb04-7995b0a5b725 |  | textbox | Date:
text | d1ca136a-b3f7-5a7e-a325-b9abd3f25d26 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | JOINTING
text | 09df9ddf-ee35-57ba-9a0e-1d4ea48284f8 |  | textbox | Details:
text | 2080e1ce-7158-562c-b028-f2e362dd17c2 |  | textbox | Tester:
text | 1caad794-5e16-5e67-89ab-308b732a129d |  | textbox | Date:
text | 650f6886-eeb2-52dc-9c74-db0e726bfdbd |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | PENETRATION SEALING
text | 5fec8545-0bd5-5769-b785-5886e48e0a2d |  | textbox | Details:
text | d5687398-72b2-5175-9227-11829ada762c |  | textbox | Tester:
text | 08552a3d-e64e-5352-a0fd-87d9cce07ff2 |  | textbox | Date:
text | 796b720d-7223-58d3-bc3b-74f444f1c736 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | FIRE STOP COLLARS
text | b1de19e6-6232-586f-8acc-ab7e8e91002e |  | textbox | Details:
text | 13acb819-4a2d-5ae0-aa5d-f0463cf81883 |  | textbox | Tester:
text | 721432cd-fd09-53f0-a61f-eaffa6e93089 |  | textbox | Date:
text | 9cd6ac9f-62df-55b4-85a2-4ee5f0385d38 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | TESTING
text | 2a8de8f4-e50e-58a0-a6f9-4ff82aff92b5 |  | textbox | Details:
text | afff0e22-f456-5c83-85cb-657a96c4b0e2 |  | textbox | Tester:
text | 67f96e93-463c-5056-832b-34fee4b4b963 |  | textbox | Date:
text | c891d953-500a-55fe-af4d-2cc4ca4434a1 |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AUTHORITY INSPECTION (if applicable)
text | 84adf893-0c43-57df-ac7f-6579c80dfe92 |  | textbox | Details:
text | 898a8d40-cb8b-5a3b-9a3a-39f5585b4a52 |  | textbox | Tester:
text | 4b973924-17ce-5584-b35c-4cc2d19bb4ba |  | textbox | Date:
text | cdbedb38-df79-5a4d-b1fd-36b980b5e7aa |  | textbox | Notes:
checkpoint-status |  |  | checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
text | 3fc1722d-62e9-5876-ae82-146959941991 |  | textbox | Details:
text | f375dc1b-3bfa-5c81-8ee0-5872cec70607 |  | textbox | Tester:
text | 5d2a97de-b848-59d4-b966-2e1aafd650ac |  | textbox | Date:
text | d1f47705-35b0-54c6-8286-0a94093f6635 |  | textbox | Notes:
checklist-flat |  |  | checklist | QA 16 - PE Electrofusion Welding - Field Operational Sheet |  |  |  |  | Yes | QA 16 - PE Electrofusion Welding - Field Operational Sheet | fd39c4b9-b8db-4ea9-acbb-13cd50e1a57f
checkpoint-status |  |  | checkpoint | Operator Details
text | d09890f7-646a-5143-b4f3-8969ff90db97 |  | textbox | Name
text | 57467f91-fde3-52e0-b267-7ab820283d74 |  | textbox | ID No.
text | ceea6ef6-6308-537d-9437-f8e63b6f21ac |  | textbox | Company
text | 8daea862-b26a-564a-a7a8-38196260bc8f |  | textbox | Address
checkpoint-status |  |  | checkpoint | Welding Machine Details
text | 6d41d224-e2e5-546b-8b09-be07b8add981 |  | textbox | Manufacturer
text | c6e1c48b-a115-580a-8f7c-18a9fbd4a3b4 |  | textbox | Type/Model
text | a6161095-5a26-5337-9adb-93ec7a6c00bf |  | textbox | Serial Number
text | f7e39ce5-586e-5ced-9b42-366b61773496 |  | textbox | Year Built
checkpoint-status |  |  | checkpoint | Actual Pipe Size
text | f984d670-cda8-5f18-bf60-2e0f2a47d258 |  | textbox | Type
text | 494cb07f-d5a8-5039-a6fd-ded454b33aaf |  | textbox | Brand
text | c426b190-d5fb-50b3-8329-bcc5dc0c6c93 |  | textbox | En
text | a28c3702-0c63-5953-ba84-af92909d5e43 |  | textbox | OD
text | 6aeaed54-c92c-599c-9731-2f4ac78f2885 |  | textbox | Ovality %
checkpoint-status |  |  | checkpoint | Fitting Data
text | 31760176-42f8-5b20-b8d5-f13e4fe89024 |  | textbox | Brand
text | 183249e9-b8ac-5e48-b375-03c842a1ffce |  | textbox | Type (Coupling, Tee, Reducer etc.)
checkpoint-status |  |  | checkpoint | Unit Setting
text | 333602de-d20b-5569-8fe7-680b88bca173 |  | textbox | Manual
text | 8a211235-6a36-557d-ba86-0d8a0adc44bd |  | textbox | Automatic
checkpoint-status |  |  | checkpoint | Preparation
text | 8d969b29-d822-5ebc-947a-f3de632ff619 |  | textbox | Cleaned and Peeled
text | 482fee68-93a2-5ef0-8a4c-9456b9d680a3 |  | textbox | Pipe/Fitting Clamped
checkpoint-status |  |  | checkpoint | Welding Times
text | 0577cc8d-f3e3-52e5-ac80-91e18b37b737 |  | textbox | Joining Seconds
text | 826b512c-5d90-56c1-a74b-8e4e5876e703 |  | textbox | Cooling Minutes
checkpoint-status |  |  | checkpoint | Conditions
text | 32a3c930-dbd3-59a5-a937-863e388c83d9 |  | textbox | Ambient Temp
text | 0bcf9c4f-5183-5a0a-a5b5-f3a6c2ace2ef |  | textbox | Weather
text | 81ba753f-caa6-55ba-ab86-854ee1f6d67d |  | textbox | Preventive Measures
checkpoint-status |  |  | checkpoint | Power
text | af7e98e3-5e08-5b7c-a821-fcde34042cd0 |  | textbox | Mains
text | 7dda302b-01bc-53f8-a5ab-dbc76f069c6f |  | textbox | Gen Set
checkpoint-status |  |  | checkpoint | Operator Sign Off
checklist-flat |  |  | checklist | ITP - Storm Water Sample Excl. Backfill |  |  |  |  | Yes | ITP - Storm Water Sample Excl. Backfill | e15859be-f17d-4669-9726-b15c07834d4a
checkpoint-status |  |  | checkpoint | 1. Approve specialist subcontractor
label | 579a17e0-8ad3-5903-977f-546ae524560d |  | note | STAGE / FREQUENCY: Prior to awarding subcontract
label | 9897091c-6795-50d8-87b1-2909975ffdc7 |  | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
label | 2ce7b111-a674-56f4-907e-c6ae92cbc849 |  | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
label | 6fff61e7-4ae4-5c40-9ad9-cd21588e2e0f |  | note | INSPECTION / TEST PROC: Document
label | 9de3f2e4-adae-5b97-8a60-e70d05a4a683 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | a507b848-4988-5b18-b6fa-6668123292e1 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 2. Approve Samples
label | 6f3b5f52-80b6-53cd-9358-eb1fc7d15abf |  | note | STAGE / FREQUENCY: Prior to ordering materials
label | fe1b05cf-5c65-5c03-95d6-d946773baee0 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | ff6a7005-beb1-54c7-82cf-ea3786c3c668 |  | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
label | c3b18f65-a7f8-5111-a9a0-20de8b063450 |  | note | INSPECTION / TEST PROC: Document and Review
label | 2a2ef85c-e1e9-52da-b975-b51a14bffa95 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | c2b44cd9-e9fe-538f-97f6-a067f7b37d92 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 3. Approve technical details
label | 2280be94-248b-5441-ab41-bbf7be009aef |  | note | STAGE / FREQUENCY: Prior to ordering equipment
label | 35098c03-addb-5302-9c2c-0254e57b5b08 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | 39df51df-8e79-5fb2-814e-935ae6d96349 |  | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
label | c5780456-3d10-5cbd-afb0-3b7f3549f677 |  | note | INSPECTION / TEST PROC: Document and Review
label | 028eee12-4313-5437-a6ad-be679ae31e68 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 2ad3401a-8dbd-5392-9c22-34a66234bf2e |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4. Approve shop drawings
label | a294d36f-be8f-5f48-a44f-9f2a93b4a018 |  | note | STAGE / FREQUENCY: Prior to commencement
label | bd4aa7d0-0326-51ea-8f7d-7a2e2d148066 |  | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
label | 5d7e6f5d-d4cf-5dd2-b866-8ba4f0db8ba9 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
label | 5bd361e8-03f0-5088-b192-619abb9610c8 |  | note | INSPECTION / TEST PROC: Document and Review
label | 68c57aef-aba9-5484-bd83-bf7bc85319a4 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | d8c8592b-0884-5611-a030-5771dca33acb |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.01 . Check set out. By Delta
label | 94f39236-b40b-5ccc-9900-8e0b3995cc32 |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | 804c7e99-089b-5e84-8967-1baad13b6240 |  | note | ACCEPTANCE CRITERIA: Set-out of pits is marked with pegs and alignment matches design layout
label | ba272a2c-f683-596c-b449-420068f3d884 |  | note | Height control point is marked within 40m of works area.
label | e23a708b-8214-54e4-8a05-f4c6451a1250 |  | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
label | 64fe05a8-ffa2-5f73-957e-eb70b70c860b |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 4d9bead1-5ef7-5476-b465-c1ba978873e5 |  | note | INSPECTOR / APPROVER: Foreman. Delta
label | d6a6c68a-3414-57c6-a325-8375c0e48de8 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.02. Check excavations
label | 07ddcc0f-e52d-55b3-b5cf-6cecc2c59717 |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | 0f01c69e-75bc-57a0-b64d-3e6280919381 |  | note | RECORDS: 'Before' Photographs
label | eec60234-8957-5ad6-9052-ac8450d387dc |  | note | ACCEPTANCE CRITERIA: Alignment commences at outlet and proceeds upstream
label | bd5f06c3-57b4-57f9-ad5e-02fc0a4034ac |  | note | Minimum falls
label | 2c73ff79-3f88-56b2-b4ff-c8afffdd900c |  | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
label | 398331e2-01e3-55ca-9fb9-4a86b0cb52b5 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | eb9e910d-4edc-58ba-8996-b22810cde5e8 |  | note | INSPECTOR / APPROVER: Foreman. LLB
label | 190978bb-671d-549d-a56e-20fa2a063a88 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.03. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
label | 237645e6-0e32-5387-802f-d9e5fec025f0 |  | note | STAGE / FREQUENCY: Prior to commencement / each TMP
label | fdd73e6c-d553-5764-9aed-a798d64ac203 |  | note | RECORDS: Copy of Consent and Traffic Management Plan
label | 0d6323e4-7b78-5df1-a0cd-39b1e06fd2e6 |  | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
label | fa365a6b-c9f0-5df1-9390-4fda655bef68 |  | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
label | 601962a5-3a4c-59f8-baea-bc370ce7221e |  | note | INSPECTION / TEST PROC: Document and Review
label | 2deac7b9-04b5-51ac-a8c8-9b30110cffca |  | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
label | 19206954-a178-5ec4-ab53-2a3c37da7841 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 6. Check deliveries of materials
label | 5e961d45-fac9-5707-b1f3-311de95f2ee3 |  | note | STAGE / FREQUENCY: Each delivery
label | e219b9da-0fa3-53b3-994f-5be701378798 |  | note | RECORDS: Delivery dockets name, signed and dated by Geschke
label | eca7fc03-8c1a-5821-ac66-118fe2c1a8ef |  | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
label | 904fdc14-ac50-560a-a2a2-9a7a31068ce9 |  | note | Grade or class matches design
label | c58af743-1b41-5c5f-8d50-aa227bf2aa23 |  | note | Size and thickness matches design
label | 114f8da3-2b70-52ce-93d0-780a6716f798 |  | note | Supplied items are free of defect
label | af88a8d6-64c1-5177-9311-d1a19951fc9f |  | note | Marking, packaging and preservation is fit for storage / construction
label | e0c743cf-f5e5-5a4e-862f-c9d9b3d0019c |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | fb9a82ee-a0c5-501c-943a-995eed848716 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | c32e73a5-8e82-5937-b270-b4b028f791d3 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.01. Check below ground pipework - rubber ring joints
label | 79b07097-14c8-5389-9b53-607eac7e0ddd |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / one test each grid
label | d05c7c22-a129-5f43-9ac8-168b3a595008 |  | note | ACCEPTANCE CRITERIA: Joints are secure and flexible
label | d7d1e873-d3d8-531b-beb0-0b1d5b215077 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | 84e84d69-fade-5c5a-918f-c9f24682c2da |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 704f4d55-950f-5c90-b662-20e06a1831c6 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.02. Check below ground pipework - pipes and fittings. By Delta
label | 932b8696-92c4-5ecc-a1c8-d776e65d83b2 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / once per grid
label | aef56460-c00a-5c86-afb0-3d9c0e7a3b5a |  | note | RECORDS: 'During' Photographs by Delta & As- built Survey by Delta
label | ebfa7cbc-afc8-5c91-9e51-84c92b6baa7f |  | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
label | 8cf1d354-86ab-5c82-8033-cc849454f060 |  | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
label | d2765691-e522-5b30-a5a0-913ecb67cde6 |  | note | Joints, fittings and connections match design
label | 761e4e44-0db0-539f-95e7-a8142390d4b9 |  | note | Alignment and position are as drawn
label | 9f49e8f1-0c71-58e6-8907-f0ce1c608a2f |  | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
label | 1789af76-9468-5348-9600-dab084fbd57d |  | note | INSPECTOR / APPROVER: Foreman. Delta
label | c73542c6-7ca0-5dc7-b094-3c73fee732e9 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | Hold Point
checkpoint-status |  |  | checkpoint | 7.03. Check below ground pipework - bedding, haunching, surrounding and encasing
label | 158db5d2-b2cf-54bf-a4cc-db275c70f786 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per grid
label | 944bdc59-a716-5110-b19e-fc24abf076e7 |  | note | RECORDS: Photograph
label | b35a6850-eddb-5583-a9f0-b02ca9c517ce |  | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
label | f0526b19-a523-5b3f-b83a-495ab433be39 |  | note | ACCEPTANCE CRITERIA: Constructed using approved material
label | fcd9d1e8-b749-5762-acb3-08933cd53387 |  | note | Thickness of surrounding aggregate shall meet or exceed specified depth
label | d67c16ec-d9cd-5486-91c3-8722146fa29b |  | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
label | bf0be4bf-e2ad-55f6-aea5-517360682175 |  | note | INSPECTION / TEST PROC: Visual Inspection
label | b69e20b8-18bd-55b8-98a1-5b2cec32f6b0 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | f08e8d54-7716-5757-bdc2-41b13f36e4db |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 9. Check Finished Surface - Make Good. By Delta
label | 799554c8-62a6-5b5b-bb16-5ae94578222d |  | note | STAGE / FREQUENCY: Prior to practical completion
label | d98025d7-d37f-5555-ba31-260aeace4e5f |  | note | RECORDS: 'Upon completion' Photographs by Delta
label | 3b974184-5cef-52ae-b87b-d7d59113e5e7 |  | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.18.5.12
label | 6021f566-3fdc-5701-83e2-94e1368064bc |  | note | ACCEPTANCE CRITERIA: If works are in existing roadways, paving or asphalt has been replaced.
label | 5271ad4a-9884-55a1-9203-cfc8fd03dca2 |  | note | Finished surface is free of obstruction/debris and matches finis
label | 7d400862-af0f-59fa-be17-02e77375a3b0 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 58699ed6-1055-511e-a853-d434722107d0 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Delta
label | d213bb88-b631-5214-a0ba-063f2dd93304 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 10. Obtain as built documents. By Delta
label | 769c69d6-5bb7-5fa0-88ad-1b5200130ef6 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 94d41758-8345-5935-8481-bc476bd68a78 |  | note | RECORDS: As built documents by Delta
label | fb735312-09a5-5b21-98ee-34f4e229e302 |  | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
label | 97d7908f-2bd5-585a-bf57-b81ca5d8d6b4 |  | note | INSPECTION / TEST PROC: Document and Review
label | 150efdf0-2579-59a2-9e9e-bd456ebe937c |  | note | INSPECTOR / APPROVER: Engineer. Delta
label | 4f79dabd-4ad4-5f5d-b0aa-723637338a94 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 11. Obtain operating and maintenance manuals
label | c5201abc-ffa0-500d-853d-7fefade54c16 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 91acd45f-805b-5144-82bd-2b8e71a0ca92 |  | note | RECORDS: Manuals
label | 241affb0-abc1-596a-b6a2-ba72a78fc0b5 |  | note | INSPECTION / TEST PROC: Document and Review
label | 44f29409-ee95-5303-a352-169f70fc14e1 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 7845c777-4f63-53f0-be2c-1b54d84a09cc |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 12. Obtain Guarantees
label | c1ddafe7-d690-52b9-a2d7-d637294a67bd |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 1cf4c80c-297a-52d8-aa29-327c7d2e72c2 |  | note | RECORDS: Written guarantees
label | 5097f1c3-1bf0-5cd9-a99c-eb96824e2960 |  | note | INSPECTION / TEST PROC: Document and Review
label | 368370ce-3f96-5716-8cc7-0323ea5dccdf |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 3f30fa19-84bc-5635-9d8b-404ab035a6e5 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 13. Final commissioning & inspection
label | bdb5e9ab-955f-5d85-b5ed-8d547149f4f5 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 5f7191ea-6c9a-51dd-bdf1-5e10c6d77b4c |  | note | RECORDS: Final commissioning checklist
label | 618e6a35-a03c-5139-903e-c14bd3f04db0 |  | note | INSPECTION / TEST PROC: Document and Review
label | faf5d475-0b90-51b1-8806-799d324cb2e1 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 941ffd4c-5c3b-5f8c-8f28-1b3d5e4d344f |  | note | HOLD OR WITNESS POINT: Witness Point
checklist-flat |  |  | checklist | Project Photos |  |  |  |  | Yes | Add Project Photos | d9446279-f7c0-4a90-9209-5a3263e25abd
checkpoint-status |  |  | checkpoint | Attach Photos and Comments
checklist-flat |  |  | checklist | Fixture/Hydraulic Installation |  |  |  |  | Yes | QA 30 - Fixture/Hydraulic Installation | ad63d434-3d5f-46c2-a89d-50583033006c
checkpoint-status |  |  | checkpoint | What is being installed?
checkpoint-status |  |  | checkpoint | Where is this fixture being installed?
checkpoint-status |  |  | checkpoint | Have all parts been connected/completed and tested? If no, please detail why?
checkpoint-status |  |  | checkpoint | Has photos of installation been taken and uploaded?
checklist-flat |  |  | checklist | Hot Water Service Maintenance Log |  |  |  |  | Yes | QA 22 - Hot Water Service Maintenance Log | 6302076c-ac1f-4fcc-a387-8cfbee12df5c
checkpoint-status |  |  | checkpoint | Hot Water Service Unit Details
text | 63d73ac6-aea3-5c36-8015-cb51cb592f4a |  | textbox | Purchased from:
text | c701aab0-23fa-54db-8eb4-36a9d8191aab |  | textbox | Make:
text | b8d6242f-6aaa-5426-adc4-bb6721d87868 |  | textbox | Model No.:
text | 9d816d75-87e3-529c-8f2f-94cb5d73f2ab |  | textbox | Location:
text | a4961ada-714a-51b1-afb7-4931cf068cc7 |  | textbox | Room Designation:
text | 322a2297-029b-5812-beb5-79e883c67499 |  | textbox | Installed by:
text | 829ba56b-89f7-5ca2-9552-932647263471 |  | textbox | Installation Date:
text | d30e5faf-4346-5783-b265-0d75243792de |  | textbox | Number of units in series:
text | f3cf3ba4-f0d0-5804-8929-8fce3cd39c06 |  | textbox | Prescribed temperature set on unit or combined package:
checkpoint-status |  |  | checkpoint | Does installation comply with manufacturers instructions
checkpoint-status |  |  | checkpoint | Does installation comply with current requirements of the local water supply authority
checkpoint-status |  |  | checkpoint | Clean Pump Strainers
checkpoint-status |  |  | checkpoint | Clean Hot Water inlet Strainer
checkpoint-status |  |  | checkpoint | Clean Hot Water Return Strainer
checkpoint-status |  |  | checkpoint | Confirm all Valve Isolation reinstatement
checkpoint-status |  |  | checkpoint | Confirm Unit is Operational
checkpoint-status |  |  | checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
checkpoint-status |  |  | checkpoint | Commissioned By:
text | 031d4ebf-deb6-5725-aa7f-0f8d56950e2c |  | textbox | Name:
text | 4569b960-cfdc-594d-9c6d-c0925dd0a8ee |  | textbox | Date:
checklist-flat |  |  | checklist | ITP - Gas Sample Excl. Backfill ACOR Review |  |  |  |  | Yes | ITP - Gas Sample Excl. Backfill ACOR Review | b094d09e-8044-47e1-bbac-68bae0a8e1f5
checkpoint-status |  |  | checkpoint | 1. Approve specialist subcontractor
label | 9ea333d3-e251-5d91-92b8-dad13708f963 |  | note | STAGE / FREQUENCY: Prior to awarding subcontract
label | db29dbe5-4805-510b-b2ec-d2a30b655f30 |  | note | RECORDS: Refer to Overall Project ITP for Written approval Geschke Quality Management Plans
label | 1c4b1048-ebae-5109-a1c5-fe60645fbf2f |  | note | ACCEPTANCE CRITERIA: Subcontract is executed and witnessed by authorised representative from associated parties to contract
label | e31dcff0-918e-5359-a33a-725e87ce2cf1 |  | note | INSPECTION / TEST PROC: Document
label | 54786f94-4968-5706-9dfc-90f6bc42bd42 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 1968fce4-cfdd-5243-8107-c353fe77934e |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 2. Approve Samples
label | a93ea1b4-701b-535b-9c01-43e7ab1a9918 |  | note | STAGE / FREQUENCY: Prior to ordering materials
label | 7ecc9f59-fce2-5244-bb31-d7fec10b85e5 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | 28720d0c-e982-5af4-9a71-f347010b9e5a |  | note | ACCEPTANCE CRITERIA: Samples is marked with Approved For Construction
label | e7c5dce6-a1f3-5422-85cf-274e6aa390ac |  | note | INSPECTION / TEST PROC: Document and Review
label | 2eb15892-2d82-5d46-8848-9b1d434386f6 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | d4e71e4b-9c57-5f88-b57b-def6006b50c2 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 3. Approve technical details
label | 310221d0-4deb-56e2-8118-33ac56ae503f |  | note | STAGE / FREQUENCY: Prior to ordering equipment
label | ac421837-e634-5a54-b0b3-e93a99f8ea90 |  | note | RECORDS: Refer to Overall Project ITP for Written approvals QA.1 Geschke Quality Submission Register
label | 7c99100d-b225-5c5d-aa42-8e9886c96d19 |  | note | ACCEPTANCE CRITERIA: Technical Data is marked with Approved For Construction
label | 372aee8d-8958-5010-ad4e-800ce2166e33 |  | note | INSPECTION / TEST PROC: Document and Review
label | 01233f45-471e-5ad5-ae0f-e615f419e673 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | cf143dd5-5046-581e-ba5a-48524941a517 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4. Approve shop drawings
label | a635d0eb-72f5-5b4d-86fa-cdceb5f37c1b |  | note | STAGE / FREQUENCY: Prior to commencement
label | 9bbcc727-acb0-532e-a758-723be6b0e041 |  | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
label | f9bd7c30-8a20-527e-aebe-c5e9f658262c |  | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
label | 49ae78bb-3cc9-5a75-a0fc-cfe5f90211fc |  | note | INSPECTION / TEST PROC: Document and Review
label | ef74c504-43a8-5ec2-aab4-b7cbd50ad9c9 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | da543418-5452-5297-a6b6-07d5dd811239 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4.01. Approve shop drawings
label | 82862675-b97b-5bac-9c51-9f072b1bad27 |  | note | STAGE / FREQUENCY: Prior to commencement
label | 47fdcf3d-957a-5d5c-a04f-00fac1813bab |  | note | RECORDS: Approved Geschke Shop Drawings & QA.2 Geschke Drawing Register
label | 23a863b3-aadd-5150-a889-91d84f7c034e |  | note | ACCEPTANCE CRITERIA: Drawings are marked with Approved For Construction
label | 03314676-f5d5-59f9-bf48-9443cdb774ed |  | note | INSPECTION / TEST PROC: Document and Review
label | 6bf4621a-27ee-507f-b0e3-b6176c0cedbc |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | d352d4ad-56fd-5d0b-9a74-d5f40a09c74b |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 4.02. Approve Method of Work Plan
label | 896940f3-2274-5a00-ab32-0907bc7323ef |  | note | STAGE / FREQUENCY: Prior to commencement
label | 6ba3f27a-acb9-5b3c-8caa-5e277fdba933 |  | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.26.10
label | 6cd650c0-8012-54b3-932c-d83ccb57a5d2 |  | note | ACCEPTANCE CRITERIA: Construction staging plan to execute the works
label | a249a61c-b1e7-59dd-b701-254616e06e0a |  | note | Pipeline construction schedule
label | 00060701-cebc-567d-9d7d-84ecd0a9721f |  | note | Nominate temporary supply
label | 10edf26a-9eb0-5054-b514-b07708334551 |  | note | Nominate safe work measures
label | 6ac82613-5a71-5f2c-b95f-728896c68bfe |  | note | Nominate notification procedures
label | af8a8354-8e2f-5224-bade-75e31b731e15 |  | note | INSPECTION / TEST PROC: Document and Review
label | 84672809-2759-5d8e-8067-eb989c0af23d |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | a32f3aac-8b57-5fff-a2b9-06f58cb03cb3 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.01. Check set out of excavations
label | 219bbfba-63b5-591a-8f7b-83aaa72e8252 |  | note | STAGE / FREQUENCY: Prior to commencement / Once per grid
label | eaea237c-88bd-5270-ae70-51ede65a6bac |  | note | RECORDS: 'Before' Photographs
label | 9486341e-caa5-55bd-8cd4-ed377f5b7daf |  | note | ACCEPTANCE CRITERIA: Set-out is marked with pegs and alignment matches design layout
label | d6c36211-fe4f-5241-be82-1df031b349f2 |  | note | All 'known' existing services have been potholed, marked using a riser 1m above ground and backfilled with sand.
label | 93a5dcd7-f1f2-5bc7-b27b-85ee7ff98333 |  | note | Excavation alignment is outside of minimum clearances from above ground assets, below ground assets and boundaries or plan for excavation works or temporary works meets requirements within exclusion zone.
label | 9e0e911b-c4f5-50fb-b39a-45606fa89624 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | c2592481-11b6-524d-a952-286bf598114e |  | note | INSPECTOR / APPROVER: Foreman. LLB
label | 8eeb8f06-7f99-5ae6-85d1-d6b44a149571 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 5.02. Approve Temporary Traffic Management Plan if trench crosses existing road, road reserve or footway
label | e980ec79-41de-51f5-885b-3c0506e619e3 |  | note | STAGE / FREQUENCY: Prior to commencement / each TMP
label | cb9c6239-e14b-5e80-9928-0d9af5848298 |  | note | RECORDS: Copy of Consent and Traffic Management Plan
label | 23d7f1ed-e28f-558e-afed-6e9213380ea7 |  | note | SPECIFICATION / STANDARD: ACOR Consultants Civil Specification Section 6.2.4
label | 38afe6bc-3962-5e7c-a3c5-ea0259cc2b8c |  | note | ACCEPTANCE CRITERIA: A copy of the consent for working in the Road Reserve and Temporary Traffic Management Plans approved by the relevant Statutory Officer
label | 0e52176a-f3fc-5c33-b581-298c8be10302 |  | note | INSPECTION / TEST PROC: Document and Review
label | e9902a8f-7069-5392-8dbf-b331dfbac91b |  | note | INSPECTOR / APPROVER: Contractors Authorised Representative. LLB
label | f2c7bf91-fb5c-5b9e-8193-fd69557e87a1 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 6. Check deliveries of materials
label | 8bbb91cd-4a14-5743-8faf-ed8f8a58835a |  | note | STAGE / FREQUENCY: Each delivery
label | d1f3695f-3609-5d75-a7a1-1ce5ae06f1d4 |  | note | RECORDS: Delivery dockets name, signed and dated by Geschke
label | 267755d8-b900-5b54-a052-2dfed8af84c8 |  | note | ACCEPTANCE CRITERIA: Type and material supplied matches design
label | 223c4aec-51a3-52c9-9b78-5c20b74cfac0 |  | note | Grade or class matches design
label | 5e8e5672-de19-5ba1-9061-2b25ca5e35a4 |  | note | Size and thickness matches design
label | c664ab5a-b198-573c-9c50-f3ac6e76b760 |  | note | Supplied items are free of defect
label | 7c28391a-4e10-5c8e-a7d4-c38cf666aa5d |  | note | Marking, packaging and preservation is fit for storage / construction. i.e pits covers marked with SS.
label | b9f89331-4ada-59a1-80be-7b2113613fe0 |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | 3d7a5e31-24c5-5a27-8853-97de9df7efea |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 62906e0f-35a0-5526-8419-ae9814b8a99a |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.01. Check below ground pipework - pipe joints - HDPE-HDPE welds, DICL- DICL/Other Material Flange, GMS-GMS Rolled Grove Gasket. If HDPE- HDPE welds:
boolean | c33c1a8c-376f-54fe-984d-4743a7f2ecd3 |  | tickbox | Standard Bead Profile Test
boolean | 4e67ccb9-ae07-54e4-9b33-dcff5ca1af94 |  | tickbox | Standard Destructive Tensile Test
boolean | aad1d026-c7b7-5433-b7a2-02a18babc43e |  | tickbox | Standard Ovality Test If DICL- DICL/Other Material Flange
boolean | 4f4ebc46-e6ef-5ef8-a451-8b23c2c85a2e |  | tickbox | Gasketing Record GMS-GMS Rolled Grove Gasket
boolean | 1608437e-e7f8-5c51-a95e-7429d5794daf |  | tickbox | Gasketing Record
label | 5efc0212-a44c-5337-8f5a-219b924b11b4 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling/ 1 test per 50 pipeline welds approx.1000 l.m
label | 8e566ca9-c3d9-51dc-81fe-a95f7c4dd724 |  | note | RECORDS: ElectroFusion Welding Record QA16 Butt Welding Record QA 25 Gasketing Record QA 18 Standard Bead Profile Test Certificate Standard Destructive Tensile Test Certificate Standard Ovality Certificate
label | 5300de34-dbcd-521a-a1f9-73489b1521ae |  | note | SPECIFICATION / STANDARD: ISO 13953 , ASTM F2620- 20 & ASTM F2928 AS4087 AS1110 & AS 1112 ACOR Consultants Civil Specification Section 6.15.1 AS 2566.1
label | ac3c75e4-b98d-54b4-80aa-f01a0b17f84f |  | note | ACCEPTANCE CRITERIA: Meet or exceed tensile pipe strength
label | 65727a2b-2689-5178-81fc-34048201e4e0 |  | note | Bead size to be uniform, symmetrical and free of contamination and air.
label | 27354e34-4e6f-51a1-87bc-dac11bddeb90 |  | note | Bolt tightening to be completed using the correct sequence
label | 8ff6b512-f3dd-5127-814c-0578925c569d |  | note | Final torque on bolts shall not exceed manufacture specification.
label | 77390acd-79c8-51f3-ba47-3308e49bc28a |  | note | Standard Pipe Ovality Test shall be meet and be no greater than 2% for cast iron pipes or 5% for all other pipes
label | bfe304c9-5d53-5b6e-96ca-d7c6c61a61e0 |  | note | INSPECTION / TEST PROC: Document and Review
label | 935bdf51-aa77-5e50-a8f5-f1d5b013d332 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 5a317e88-e2f1-5f2a-8dec-a06c61917d12 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.02. Check below ground pipework - pipes and fittings
label | 96b2dc90-a53a-572f-87bd-bed5a73eabd0 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
label | 1eaa3d6c-80bb-5688-9a66-69a0bac1f18c |  | note | RECORDS: 'During' Photographs & As-built Survey
label | 4b2ec00c-fbdf-5e6e-93ee-99d389111223 |  | note | SPECIFICATION / STANDARD: AS 2566, AS 3500, AS 4130 and AS 5065
label | 533ce572-fb81-503c-9add-12f6107bc54c |  | note | ACCEPTANCE CRITERIA: Service type clearly labelled with dimension & colour stripe
label | 4641189c-1536-5048-b2b5-5d7a6a4e2d17 |  | note | Joints, fittings and connections match design
label | a4f51eb2-de4d-5e00-9f83-e254b8527e76 |  | note | Alignment and position are as drawn
label | 82eb4e20-91ce-508c-8464-e73daecf8ed5 |  | note | INSPECTION / TEST PROC: Visual Inspection & Document and Review
label | 1d84c139-66bf-5579-9709-a687af53e932 |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 90ecdc67-a645-56b2-8fbc-ac3cea97876b |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 7.03. Check below ground pipework - Air pressure testing & swabbing. Standard Air Pressure T est
label | a3fd3d4d-0eb5-5274-baf4-1a74b60e50c9 |  | note | STAGE / FREQUENCY: Upon completion but prior to covering and backfilling / one test every 750 lm each pipeline
label | 0b05dd18-a3d7-5d3d-8c5a-ec3f5a936680 |  | note | RECORDS: Standard Pressure T est Certificate QA.6
label | 538e565f-011c-51f3-aa7f-74274bee5819 |  | note | SPECIFICATION / STANDARD: AS 5601 ACOR Consultants Civil Specification Section 6.26.8
label | b7be1b16-0bae-536a-a5f6-66eefd4591b3 |  | note | ACCEPTANCE CRITERIA: Pipeline and joints are airtight under the greater of 7 kPa pressure or 1.5 times the working pressure for 5 mins
label | 65955b97-2bf3-5cad-ae7c-c10fb5c55dd8 |  | note | Pipeline is flushed free of all debris
label | 989db3b9-f642-5fc5-a14f-787529b5a55e |  | note | INSPECTION / TEST PROC: Document and Review
label | 1d2470da-4eec-5341-b738-c40a22f5201b |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 0b4cc490-a25e-5a59-909b-5bc5d1a72cfb |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 7.04. Check below ground pipework - bedding, haunching, surrounding and encasing
label | 678f82ed-989a-57ca-8f48-b0c2128f8207 |  | note | STAGE / FREQUENCY: Upon installation but prior to backfilling / Once per Grid
label | 752391f4-4ceb-5091-a6f7-aec47a91b841 |  | note | RECORDS: Photograph
label | 37af61e0-0003-5579-bfa8-ba488af3737b |  | note | SPECIFICATION / STANDARD: AS 1289 3.6.1 ACOR Consultants Civil Specification Section 6.6
label | df175655-2d57-5bc9-8736-f6e136882c68 |  | note | ACCEPTANCE CRITERIA: Constructed using approved WASA material
label | bf555cae-a31f-5c07-9f5e-bb9c6ef18efa |  | note | Thickness of surrounding aggregate shall meet or exceed specified depth
label | 1f5b8960-ed1c-5afd-93fe-93e7286bd07a |  | note | Detector wire/traceable foil backed tape laid 300mm above the pipe alignment
label | 3f9dbcf9-9e49-587e-a740-7ec0ee021fff |  | note | INSPECTION / TEST PROC: Visual Inspection
label | 5d81e7c7-3a65-5400-80b1-a655ac3b13df |  | note | INSPECTOR / APPROVER: Foreman. Geschke
label | 29c18f2e-272c-5c23-9594-fd841a2a8194 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 9. Check Completed Surface - Make Good
label | 01e8af79-ec6f-5255-b3ba-f370f211d2ca |  | note | STAGE / FREQUENCY: Prior to practical completion
label | ad485096-b09c-5f50-8ece-9357159b4a9d |  | note | RECORDS: 'Upon completion' Photographs
label | 2e943770-9711-55a8-a890-903a7546f8b2 |  | note | ACCEPTANCE CRITERIA: Completed surface is free of obstruction/debris and matches finished levels for pipework
label | b5603ac0-496f-520b-9b7d-700777b39cab |  | note | INSPECTION / TEST PROC: Visual Inspection and Document
label | e20abc10-d095-5fb7-94e1-04d4a0a75374 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 74ec5b8b-9f0f-588a-b40c-e1becc90fb20 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 10. Obtain as built documents
label | fa7428ec-ab25-5b54-ae96-eb9d09eb57ed |  | note | STAGE / FREQUENCY: Prior to practical completion
label | e46696ab-ac46-557f-90b4-b578d13b71cc |  | note | RECORDS: As built documents
label | dd4c67ab-b0f3-5a33-8127-82094438b41d |  | note | ACCEPTANCE CRITERIA: Drawings are marked with As-Built
label | 95dae544-ea43-5111-a629-06c68d4e54b8 |  | note | INSPECTION / TEST PROC: Document and Review
label | 71aea24a-4f6b-5759-ae78-ce4dccdc3223 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 09e8405c-5565-5dca-8a23-d1b412c75eeb |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 11. Obtain Regulatory Authorities certificates and approvals
label | 9f0e2b42-a254-532b-bda4-74b145ec82e8 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 0abe8a24-605c-5db4-aa4c-207300878772 |  | note | RECORDS: Certificates; Written approvals
label | e80593d1-9028-54a2-90d9-c4e787bd69de |  | note | ACCEPTANCE CRITERIA: A copy of the certificate for compliance shall be approved by the independent authority.
label | 49c3fe8b-7ada-58fb-871d-c66560d49fbd |  | note | INSPECTION / TEST PROC: Document and Review
label | c6f1dcfb-4ce8-55e4-8c6e-44fabb19f034 |  | note | INSPECTOR / APPROVER: Independent Authority. LLB
label | 339e8698-11aa-5e5f-b052-8535bf25a8c2 |  | note | HOLD OR WITNESS POINT: Hold Point
holdpoint |  |  | signoff | hold point
checkpoint-status |  |  | checkpoint | 12. Obtain operating and maintenance manuals
label | 79e0c08b-0dae-5205-a85e-ac9847272086 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 26cd6238-0569-5297-80cb-d7b728f71a1e |  | note | RECORDS: Manuals
label | 30ce08cc-a649-5ff9-95ee-61aeea8b14b9 |  | note | INSPECTION / TEST PROC: Document and Review
label | c0024638-fd47-504c-925b-be4a72335239 |  | note | INSPECTOR / APPROVER: Engineer. Geschke
label | 441f4cb6-dba8-5e5b-8665-fd25e3a176a8 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 13. Obtain guarantees
label | d198bcee-cd85-5d63-b9b2-2d4b16b9d019 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | 2235cacd-751a-5e41-99c6-95c42dd727be |  | note | RECORDS: Final commissioning checklist
label | 845bbda6-18fe-5c58-9b02-336aca21cb66 |  | note | INSPECTION / TEST PROC: Document and Review
label | 40fdc476-1191-547d-980e-4d113d86a991 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | e8a00238-7392-5ba2-accd-f59593543e64 |  | note | HOLD OR WITNESS POINT: Witness Point
checkpoint-status |  |  | checkpoint | 14. Final commissioning & inspection
label | 5d8cddfd-e471-58dc-a376-37282e09f967 |  | note | STAGE / FREQUENCY: Prior to practical completion
label | bf4bacf6-ca94-5b9d-8280-7a1166715785 |  | note | RECORDS: Final commissioning checklist
label | e266bd23-3f04-5235-b32b-5187e388b10e |  | note | INSPECTION / TEST PROC: Document and Review
label | e84d5907-4791-5a87-9a7a-af8f8d5d1f32 |  | note | INSPECTOR / APPROVER: Subcontractors Authorised Representative. Geschke
label | 872bd20a-6ecf-51a1-82de-c4b90ec1870d |  | note | HOLD OR WITNESS POINT: Witness Point