## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | CC0394 - ITP-009 - Fire Service Installation & Commissioning | itp |  |  |  | Yes | CC0394 - ITP-009 - Fire Service Installation & Commissioning REV1 | 0667404f-8101-4c6f-8b80-3f8b8d570e71
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | b8be2ebd-6cd4-54a8-8781-29a47e12b83f |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 2d8e2d58-e542-5428-ae49-7a8a141bcb37 |  | textbox | Lot opened date:
text | 4964beea-efd9-5d31-9b96-e1663a52988f |  | textbox | Lot opened by:
text | 751baec0-5312-59cb-948c-5d82457e4b3a |  | textbox | Date lot closed:
button | 0942d1ce-a0cc-5e02-8175-b9957420342e |  | button | NCR raised? | Yes, No
text | af430739-b5f4-5314-aaaa-161f8fcf2527 |  | textbox | NCR Raised Date:
button | 1cc4689d-4350-5f1c-8aae-a92711446188 |  | button | NCR closed? | Yes, No
text | 3ed1e243-cd4e-592b-9300-ad320ac13f30 |  | textbox | NCR Closed Date:
text | 3cd398a8-3ca7-5af1-9726-1837dcd26390 |  | textbox | NCR Number:
text | ac9f0e33-c8bf-511e-a9fe-21141b03d141 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Determine Lot Size
label | fd6970a7-2806-5363-a690-1ef9801eacde |  | note | Ref docs - AS3500
label | dfb95725-d98a-5953-bd2e-f906677235c2 |  | note | Acceptance criteria -
text | 9c78cf3e-d527-5eb1-a3ad-884bcaba6a25 |  | textbox | Pipe / lot length:
button | ac109432-f2d5-57e4-a28c-7f810e67ead1 |  | button | Acceptance | Yes,No,N/A
label | 62673b66-a52f-575b-b40f-ecb60f982440 |  | note | See Work Lot Map
label | 5eed4e49-2b92-54d5-adc9-6ce181483447 |  | note | Resp - SE
label | 5e41677f-2789-577c-b67e-7a0298ae39be |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 83e8020e-9713-5eb5-a4dd-0727153b2973 |  | tickbox | Work Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Survey Set-out
label | 5ada8f38-23a4-5464-99f4-b45c0042d4c1 |  | note | Ref docs - IFC Drawings
label | 2def0bcc-7427-52a6-a0f4-1b37eee7f84b |  | note | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all fire lines including hydrants and risers.
button | c18132ec-faae-5580-a01e-8ea16809fc6c |  | button | Acceptance | Yes,No,N/A
label | e370f665-f5a1-5e7b-9ffa-1874a410622e |  | note | Key - W
label | fd6d3171-e549-5d42-8006-d14ebe1d83fd |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.3 - Approved Material Type
label | 4728cf02-6dfe-57a6-8017-9bf3b58e6406 |  | note | Ref docs - IFC Drawings AS3500
label | 7b745eaf-1b45-599f-aeda-a2b78b06238e |  | note | Acceptance criteria - All materials selected in accordance with AS4130 and RJE civil specification and drawings.
button | a4b1c1dd-2f51-5ded-a641-56d9969fef1a |  | button | Acceptance | Yes,No,N/A
label | 0657f73c-3283-593c-9899-06bf88b8606a |  | note | Key - H
label | f03ab2d7-53a9-51c5-82f9-34e705a29ed0 |  | note | Resp - SE
checkpoint-group |  |  | section | 2.0 In Process Works
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | b5907fa2-a94f-5dae-9056-988acaf58abb |  | note | Ref docs - IFC Drawings AS3500, Excavation permit
label | 8a6a9761-34c8-59e8-a736-d178990b07cb |  | note | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | e6471d14-00e4-568d-aa64-fd46e0c64e1d |  | note | ○ Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
button | e31c736d-804f-5ce5-a7db-ee33ffd79b01 |  | button | Acceptance | Yes,No,N/A
label | dc8daeee-820d-5e33-a017-7ed495d970b1 |  | note | Key - S
label | 589b2a74-fea2-583a-b4b4-a317ff133d34 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.2 - Removal of Obstructions
label | e6b95414-3a7c-5c12-bd3a-478087fff4c3 |  | note | Ref docs - IFC Drawings and specifications
label | c2ae272c-5296-5d63-a835-b68d55bc71fe |  | note | Acceptance criteria - Remove obstructions including roots, stumps, boulders, and the like which may, in the opinion of Symal, interfere with the proper functioning of the service.
button | ca62dce9-ea90-5609-8633-e3fbc03eae10 |  | button | Acceptance | Yes,No,N/A
label | 532b1d69-6f4e-599d-b395-e9d77246fe11 |  | note | Key - S
label | 6ee8fcc5-b888-5f0f-b76c-f74ac4936cac |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.3 - Bedding
label | 91c6be5b-2dd1-5653-83bf-2d0ff9e8ae94 |  | note | Ref docs - IFC Drawings and specifications
label | 796da4ed-ffd8-51f8-b77d-e6bffeb5795d |  | note | Acceptance criteria - Pipes should be bedded and supported by class 3 quarry material with a minimum thickness of 75mm.
label | 34bd2350-6d19-50ca-9a9f-a5784c77136c |  | note | ○ 5-10mm crushed rock or sand shall be used as the haunching material.
button | df167c64-bb69-5961-b3f4-d2484736748f |  | button | Acceptance | Yes,No,N/A
label | 36a7fdd1-c906-578f-913a-2b6aa46209e2 |  | note | Key - S
label | eb5ce081-2bbc-5249-a1df-bbd7e9cb96b6 |  | note | Resp - SE
checkpoint-group |  |  | section | 3.0 Installation of pipes
checkpoint-status |  |  | checkpoint | 3.1 - Pipe Installation
label | 5b846cf5-88a3-5468-b265-9bc61c1398cd |  | note | Ref docs - IFC Drawings and specifications
label | ab0e8afb-0e99-55fa-9512-d5b0112d5e2f |  | note | Acceptance criteria - Work shall be carried out by and under the direct supervision of appropriately licenced personnel.
label | bfc672c2-c3c8-5281-9075-50c4a9e7d369 |  | note | ○ During construction, temporarily seal open ends of pipes and valves to prevent the entry of foreign matter into pipe systems.
label | b006cbb4-1dce-5121-bc60-85836e1e8da7 |  | note | ○ Install piping in straight lines at uniform grades without sags.
button | 08d869e5-a0b4-54f5-88d0-cb745c889dea |  | button | Acceptance | Yes,No,N/A
label | 5b64ce0e-ee44-552b-b870-940676c273f1 |  | note | Key - S
label | 293bffb3-1e58-5b10-b65e-f66a2247f3b9 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 3.2 - Electrofusion Weld fittings/pipe/couplings
label | dc6cfb24-d2e3-58f5-a6e3-0f06749f5902 |  | note | Ref docs - as per manufacturers recommendations
label | e84dfade-79ec-5b07-86fc-0359e9c907c7 |  | note | Acceptance criteria - Ensure pipe is cleaned and scraped prior to welding.
label | ac921746-9104-5b69-8ed4-145d30665ef1 |  | note | ○ Ensure pipe is fixed firmly in position.
label | 01960a63-cc9b-5d62-9a56-68aec7969a71 |  | note | ○ Allow curing time as per specific fittings recommendations, Visually check all fittings have been welded.
label | 6a70b8e8-dbaa-58d4-a7f6-8980814d25a8 |  | note | Acceptance - Prior to Backfilling
label | 36fbfcba-d0bf-5397-98df-5902f7e5e2a3 |  | note | Key - W
label | 55e11242-71ce-563a-93a0-41a89dbd6591 |  | note | Resp - SE
label | 1d37fdef-0beb-55d1-baec-90fe86a6a43d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Electrofusion welder calibration certificate.
checkpoint-status |  |  | checkpoint | 3.3 - Cover
label | 46f09761-ba9e-5d53-a326-b2c86efd12c3 |  | note | Ref docs - IFC Drawings and specifications AS3500.1
label | 1ffa0d06-cf87-502c-a0b3-376cfc6f77a8 |  | note | Acceptance criteria - Minimum depth of cover for buried pipes: 600mm to finished surface.
button | 6e976c02-780e-5261-9d4f-a14b2858049a |  | button | Acceptance | Yes,No,N/A
label | 0bdf42a7-7a4a-50df-836f-2db846db5c9a |  | note | Key - H
label | 816bf478-c7f8-5d57-8bb4-5c4a416aa046 |  | note | Resp - SE
label | 9f76efb2-87a8-57b1-ae96-129a97145e52 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | d449b6de-b5c3-51ff-8318-827f664073c9 |  | tickbox | As-Built Attached
checkpoint-group |  |  | section | 4.0 Backfill
checkpoint-status |  |  | checkpoint | 4.1 - Backfill Material
label | d1a13f3c-84de-5074-9989-9dbe4a60a3c1 |  | note | Ref docs - IFC Drawings and specifications AS3500
label | 154bb173-7ca8-5a35-9b0d-7bc979154b39 |  | note | Acceptance criteria - After pipes & fittings have been set in the correct position and jointed, further bedding material shall be used to fill all recesses below sockets, and bottoms of trenches.
label | a83f84fb-5450-5642-9428-37555ad2e3f6 |  | note | ○ Trench backfilled with selected clean excavated material, or the purchased material bought to site.
label | 38c27817-c640-5164-a877-1b5525eefb7a |  | note | ○ 5mm Dust Compliant for bedding
label | d13dc3d3-b181-5b0c-a325-a0aa99bb164b |  | note | ○ BACKFILL Overlay WITH 20mm nominal size class 3 crushed rock
button | f2ec993a-ef9a-5b14-82c9-9948182b15b3 |  | button | Acceptance | Yes,No,N/A
label | a64fb368-778a-5562-92c8-db802dc11534 |  | note | Key - S
label | 1640785f-f998-5168-a3f5-67887c9964d9 |  | note | Resp - SE
label | 38d55ed0-7ced-54e5-a3c1-2910df1c854d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 63ca5766-c7c1-57e5-82af-bd814d9f6563 |  | tickbox | Material dockets
checkpoint-status |  |  | checkpoint | 4.2 - Layer Thickness
label | e10d588d-b480-5c71-b40e-c0cbe3c2ab15 |  | note | Ref docs - IFC Drawings AS3500
label | 01618f23-2240-5c00-ba66-6db0fc1816fb |  | note | Acceptance criteria - Backfill material must be placed and compacted in layers not exceeding 300mm.
label | 9b9e0e4a-cce9-5639-97c8-929f27ed4a09 |  | note | ○ Backfill trenches as soon as possible after approval of laid and bedded service.
label | 42b0e5ea-95e5-5f10-a858-9188dc3075c8 |  | note | ○ Allow adequate cover over pipe (minimum 600mm)
button | 95df8b51-8ae9-535d-8853-c37c8f7fb5f1 |  | button | Acceptance | Yes,No,N/A
label | 5a5c23b4-5ed9-59f3-bf14-87f02b044554 |  | note | Key - H
label | f18766f7-7099-58a8-a650-226d5eb7f9da |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.3 - Compaction
label | 781e2f9a-a13a-5157-8f16-4c0e901fb434 |  | note | Ref docs - IFC Drawings AS1289
label | 4cf30b88-ef5b-5e48-b9b6-ca26b8c5f0aa |  | note | Acceptance criteria - Compaction to be undertaken using hand methods only for first 300mm.
button | a8350870-2d2f-5c3c-9fd7-cf405a8a7e8b |  | button | Acceptance | Yes,No,N/A
label | 5ae59449-f81f-565a-b1a4-255d89751aa1 |  | note | Key - S
label | 5b13b46a-714c-5faa-b466-7e09ddfc9c63 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.4 - Preliminary Pressure testing
label | 7e783465-f234-55d1-8c3f-8e314122a344 |  | note | Ref docs - IFC Drawings RJE NOE AS3500.1
label | f8114e19-0c8e-50f8-b302-0250f55a0557 |  | note | Acceptance criteria - Sign-off items 1.0 – 4.3.
label | 7086c753-bb1f-56ad-852a-a2334f6a6609 |  | note | ○ RJE NOE
label | f5d4fd46-5953-562f-858b-57b9cbab1d0b |  | note | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa. Pressure deviation to be not more than +/- 35Kpa.
button | 40ee819b-b8ad-5681-b1c3-7e07b1000531 |  | button | Acceptance | Yes,No,N/A
label | 0bc86270-0207-5994-9bde-b321253e3236 |  | note | Key - H
label | d4ccde71-5457-56b0-bc66-c7110f778475 |  | note | Resp - SE
label | dfae2ed3-0f6d-57ec-9a56-47953fe5791f |  | note | RJE Key - H
label | c2dd6c5b-58e3-556a-8d65-4981f702d451 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ec9f5283-4f46-5ec1-ae8f-219a69b3d693 |  | tickbox | RJE NOE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.0 Fire Hydrant Install
checkpoint-status |  |  | checkpoint | 5.1 - Survey set-out
label | aaeb0437-daa5-5385-9b7a-d233c29ef940 |  | note | Ref docs - IFC Drawings
label | 9f456aff-0342-5ee0-a4b6-1864358980af |  | note | Acceptance criteria - Prior to the commencement of works, the contractor shall engage a suitably qualified surveyor to set out the works and clearly mark its limits.
button | 82018d57-df01-5778-b459-6c6cc74ae63f |  | button | Acceptance | Yes,No,N/A
label | 044cdcec-0824-5438-955b-84898b24da93 |  | note | Key - W
label | 2dd1130f-cb63-5654-8bbe-c2aff92dc359 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 5.2 - Approved Material Type
label | 2ecbde83-c63c-57d1-9fa3-7f69f6a04dc2 |  | note | Ref docs - IFC Drawings AS3500
label | 4b780914-00e6-5694-964c-6b8cb77a905f |  | note | Acceptance criteria - Materials used for the installation of Hydrants to be in accordance with AS3500
button | a329ce2b-a545-5dec-9edc-17d8958c3a7f |  | button | Acceptance | Yes,No,N/A
label | 9ca1b833-154b-596e-9571-c6c91c420797 |  | note | Key - H
label | 045784ea-d1d0-52b1-a438-865808c76031 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 5.3 - Fire Hydrant Install
label | 0e1e775b-c09a-5cfa-a61c-085fb1c20c1f |  | note | Ref docs - IFC Drawings
label | 4657a635-a3bc-5a0b-8ffd-9d3e2852d42f |  | note | Acceptance criteria - Ensure fire hydrants are located such that they do not impact vehicle access.
label | 35f922c2-8feb-5488-857a-91cdf03cfdab |  | note | ○ Bollards are to be installed for physical protection.
label | 8701a035-f7c9-58f5-9e0d-3cae2be42795 |  | note | ○ Confirm valve operability.
button | 2762da2d-c462-5328-8620-ad4991fa068f |  | button | Acceptance | Yes,No,N/A
label | ca8a5bf9-ce4a-57ad-9ca0-a3e824979d56 |  | note | Key - S
label | 7912cf75-9eba-5aa6-aa75-69f37de6129a |  | note | Resp - SE
checkpoint-group |  |  | section | 6.0 Conformance Check
checkpoint-status |  |  | checkpoint | 6.1 - Clean & Finish
label | 05157fe4-acad-56fa-b3ce-94d47aec5733 |  | note | Ref docs - IFC Drawings
label | 4ab29609-6984-5954-96a6-cb288ad51248 |  | note | Acceptance criteria - On completion, each line shall be free from dirt, debris, or other impediments.
button | 9e370122-899e-537b-bbc0-188c779fe2b0 |  | button | Acceptance | Yes,No,N/A
label | ff8e95ac-9608-567a-b2f5-ac1e9018ac49 |  | note | Key - S
label | c73b4473-ee12-5126-ae56-b3dd35479cb7 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 6.2 - Testing
label | 93ef470c-cf21-573b-a69b-b120dbb98fae |  | note | Ref docs - AS3500.1
label | f396b429-16e8-54e9-aa44-ea4e84485cad |  | note | Acceptance criteria - All pipe and hydrants to be pressure tested in accordance with AS3500.1
label | 098dda88-aedb-568e-b857-cf63a5d67790 |  | note | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa
button | 49733ced-d943-5aaa-bd3b-122fe0493034 |  | button | Acceptance | Yes,No,N/A
label | fd001bf2-c631-5dbb-b51f-e26e11b355eb |  | note | Key - H
label | d1e57c69-9110-5555-873a-718f6e790732 |  | note | Resp - SE
label | fcfee613-1d3b-5fc3-963f-4b014c1c0127 |  | note | RJE Key - H
label | 64e9f9e8-f792-5583-a865-2cb1709d81c4 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 44358af8-4293-529c-9b4d-cfad0dc6432c |  | tickbox | Test certification
boolean | 26821466-f41a-521c-96d9-a87e536232f3 |  | tickbox | Calibration certificates
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.3 - As-Builts
label | a754877a-2d8a-5b67-b2c4-9f12cec9c73c |  | note | Ref docs - IFC Drawings
label | ad723b8c-4eca-5b7c-b161-0401b6b060ec |  | note | Acceptance criteria - Accurately record the routes of all underground pipes before backfilling.
button | 2e108ed4-e467-5aba-85ba-8a4a40d2cd10 |  | button | Acceptance | Yes,No,N/A
label | c4634514-f5f0-5220-a05b-89f0c05d50b4 |  | note | Key - H
label | fedb9a91-0932-56f1-b5df-23a4aa762c38 |  | note | Resp - SE
label | 105bbc00-1dd6-50a0-b3b8-ebc71fd7df8f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 76803a11-fdb7-50b8-98d5-c9ff22422db7 |  | tickbox | As-Built Attached
checklist-flat |  |  | checklist | Concrete Pre-Pour QA |  |  |  |  | Yes | Concrete Pre-Pour QA Checklist | 07c91d3a-6830-4c1d-8fa4-c0e15e9bcdfc
checkpoint-status |  |  | checkpoint | Design items
button | 0750fbdf-00ea-5563-9cea-a7d28184b06d |  | button | Correct concrete MPA and mix design ordered | OK,NOK
button | 6e40f362-1966-5dfc-82f3-66e9704586b1 |  | button | Concrete tester organised and testing as required | OK,NOK
button | 97d7d47a-972c-5354-8107-74898ffd9d80 |  | button | Correct slump for project ordered | OK,NOK
button | 6189717c-729d-5dff-8bc1-5ee5003fc2ea |  | button | Max slump 80 or less if specified. | OK,NOK
button | 0f478721-31f1-5cc2-93e2-870dda0f95c2 |  | button | Correct finish type, please note: | OK,NOK
checkpoint-status |  |  | checkpoint | Pre pour items
label | 783887e0-8e2e-5c5a-b79a-daabf462d07b |  | note | Confirmed area to be poured including:
button | cfd93bee-c3f4-5c62-8fa2-6f67891a39f6 |  | button | Levels | OK,NOK
button | 3e65cf8a-40bf-5abf-80d9-9e5f76823ecc |  | button | Step downs | OK,NOK
button | ef79f8a7-e6ea-5e3d-a9c8-aa4ecaeeca54 |  | button | Items to be stripped during the pour | OK,NOK
button | cb0810c8-6879-59db-9ce7-067b0f779d4e |  | button | Finishes | OK,NOK
button | 0560d9ab-57b8-58f3-a0b1-79e898e68b74 |  | button | Extent | OK,NOK
label | 0c5b234c-74b6-5241-b8cd-1874e6629852 |  | note | Checked reinforcing for the following:
button | 2f6a203b-7594-55c7-8111-818a7ccb0827 |  | button | Cover | OK,NOK
button | 026c9d39-4ccb-5576-935e-7d78dbfe64b2 |  | button | Reinforcing installed vs. drawings | OK,NOK
button | f1c2b35f-3540-5b3e-9533-b7d724e39b7d |  | button | Bar chairs adequate | OK,NOK
button | f7e2493d-1e83-54bc-b945-691e63bbf2d8 |  | button | DJC, SCJ, CJ, and all other joints confirmed | OK,NOK
button | eb62bfc5-f207-5115-9926-e1b167f90999 |  | button | Correct curing organised | OK,NOK
button | 28e6eb9d-da78-538d-8c02-2ca79aabfb4a |  | button | Saw cutting | OK,NOK
holdpoint |  |  | signoff | Hold point do not proceed without an inspection
checkpoint-status |  |  | checkpoint | Post pour items
button | d565d881-8829-57bd-8d55-ab37d2af4831 |  | button | Adequate founding depth achieved | OK,NOK
button | 2c9a1271-3bf1-5219-af3a-c479b55a44b5 |  | button | Strip formwork | OK,NOK
button | 1576adb7-2e93-5f7a-9b80-7e098a55e39d |  | button | Concrete curing | OK,NOK
button | 892f8fc3-c596-52a9-a87b-815f30b4fbbd |  | button | Levels checked | OK,NOK
checkpoint-no-status |  |  | checkpoint | Additional comments:
text | ef2c7c44-07a4-5f3e-8c02-ba9318963451 |  | textbox | Pre-pour checklist completed by:
holdpoint |  |  | signoff | Signature
checklist-sectioned |  |  | checklist | CC0394 - ITP-012 - Asphalt | itp |  |  |  | Yes | CC0394 - ITP-012 - Asphalt REV0 | 1d018ecb-d150-4f4c-8e86-d9d2629449a8
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | fc2830e2-42b9-5fed-8434-67d4159e6f73 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 70386a82-b780-5d63-8971-f467458e0d53 |  | textbox | Lot opened date:
text | 46986412-496e-5fcd-bc58-21f9624152e0 |  | textbox | Lot opened by:
text | bdbfe8fc-15b2-5b2c-a893-70cb2193ce14 |  | textbox | Date lot closed:
button | 5740ac72-fd60-5d61-8b21-ebedeea42f09 |  | button | NCR raised? | Yes, No
text | 387414e4-588e-5eea-a981-db1d67d0604e |  | textbox | NCR Raised Date:
button | 45ca48bb-4687-5d47-bc69-510373929646 |  | button | NCR closed? | Yes, No
text | fd10d8d8-80cf-5222-9a20-9de765b7fe2a |  | textbox | NCR Closed Date:
text | fc949bf8-e8ee-5810-92e7-96f8ee4ed677 |  | textbox | NCR Number:
text | 90a05d25-cc48-5005-b271-5750f6f65ab8 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0
checkpoint-status |  |  | checkpoint | 1.1 - Determine Lot Size
label | 7daf3d14-9c1c-57a5-bb6b-f9e6a85553d6 |  | note | Ref docs - IFC Drawings
label | 90044c78-06e5-52c9-826d-77918909e912 |  | note | Acceptance criteria - Maximum Lot Size = 4000m2
button | e870877b-3d6c-589e-ba05-d466e1820165 |  | button | Acceptance | Yes,No,N/A
label | 03a2210f-1224-5079-892f-a48ae2e1dc20 |  | note | • See Work Lot Map
label | 15bed521-bf5c-5a6f-b6bc-4679facbdfbb |  | note | Resp - SE
label | 8c82a2f1-7b90-57c8-9ae0-eed5a4bb0b58 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 39c1b022-6416-5ac1-88b4-46a896283d8f |  | tickbox | Work Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Survey Set-out
label | 528db78f-a7d4-5245-b573-8d3a226e9000 |  | note | Ref docs - IFC Drawings
label | 50a1de37-603e-5558-8483-c0b2c7cdff5b |  | note | Acceptance criteria - Prior to the commencement of works, the contractor shall engage a suitably qualified surveyor to set out the works and clearly mark its limits.
button | 48028495-a3f5-5f16-a3aa-87cd77da1a50 |  | button | Acceptance | Yes,No,N/A
label | 54cdc47a-114b-5337-8acf-18aed37bc4f9 |  | note | Key - W
label | 519c4a89-9d55-58c4-acd5-1091c895cf4c |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.3 - Approved Material Type
label | a0ed9071-9073-591d-88e6-1a1d323f5737 |  | note | Ref docs - IFC Drawings
label | 5d39d9ab-e1bc-5c0f-8338-7e8837b8a887 |  | note | Acceptance criteria - Asphalt types specified within IFC Drawings.
label | 2f09938a-1967-59d0-bc8f-1d5d2f19728b |  | note | Acceptance
boolean | f1c29091-093f-5fd1-baf7-9982176ff5d8 |  | tickbox | 40mm wearing course size 10mm Type H (C320) Asphalt 7mm Cationic rapid setting (CSR) emulsified primerseal (C170); or primer AMCO
label | e9ff1fd2-06e4-5c83-a407-b45fca8f8210 |  | note | Key - H
label | 81b8d3ff-5ea5-5d83-99e1-863a3bb44f43 |  | note | Resp - SE
checkpoint-group |  |  | section | 2.0
checkpoint-status |  |  | checkpoint | 2.1 - Storage of Asphalt
label | 79256b93-33d5-5ed3-a4e8-f19945365ca6 |  | note | Acceptance criteria - Asphalt mix has not been stored in a hot bin for more than 18 hours prior to use.
button | 60bfa9c8-2498-5d42-ba2c-6d643f883032 |  | button | Acceptance | Yes,No,N/A
label | 24f501e0-c483-546c-8110-1dd0eb2afe7f |  | note | Key - S
label | d316eb05-cf53-5a64-9be7-ce41f36445dd |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.2 - Conditions for Placing
label | c91f9653-c213-5ba0-9025-df419b5d518c |  | note | Acceptance criteria - Surface on which asphalt is to be placed is dry, free from surface water & has a surface temperature >10⁰C
button | 46c9ba72-2d81-5af6-92c9-6414ca0c7c4f |  | button | Acceptance | Yes,No,N/A
label | 1a2a1e75-60a4-5033-a995-a4ab03afdb30 |  | note | Key - S
label | 8c96e1d1-56d0-59a4-a750-0993d7d64f6e |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.3 - Commencement of Placing
label | f6352dd0-a482-5320-90a4-7b59a475fa19 |  | note | Ref docs - IFC Drawings
label | d8e843b4-84a7-58e6-bb47-98f2dcf44cb2 |  | note | Acceptance criteria - Crushed rock surface to be primed prior to placement of asphalt.
button | 06e39577-5661-5510-91b0-0f1158040ea2 |  | button | Acceptance | Yes,No,N/A
label | 1a092c9b-a7c2-5358-bf8d-9f57f1febad8 |  | note | Key - S
label | 28142b4b-ccf3-54fe-90db-89d110bc5063 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.4 - Spreading
label | 18ee5a54-cf4b-50d6-a6ec-ad99da3a2424 |  | note | Ref docs - IFC Drawings
label | 053d423e-f59e-5d73-8635-6450c32e832b |  | note | Acceptance criteria - All asphalt shall be spread with an asphalt paver except for small areas where use of a paver is not practicable.
label | 4f400337-b3b9-5941-901c-49a4ea29193f |  | note | • All asphalt shall be spread to form a uniformly smooth asphalt mat without segregation, tearing or gouging.
button | 747162a8-a6d0-59fe-ba23-2802f3901fa0 |  | button | Acceptance | Yes,No,N/A
label | 1e9a39a7-c515-58af-a4bd-e5715a714d66 |  | note | Key - S
label | 2ca6ebe6-aa4d-5113-9b67-82a40eda0f06 |  | note | Resp - SE
label | 1d9f01bb-643c-5777-9b3e-2de557c48ef7 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | bbf25acc-1bd5-5c05-aa03-c0dc97193d21 |  | tickbox | As-Built Attached
checkpoint-status |  |  | checkpoint | 2.5 - Joints & Junctions
label | 6cd082e9-9af3-597a-bd97-e7ba3460d969 |  | note | Acceptance criteria - If the paver is required to stop & asphalt in front of the screed cools to below 120⁰C, a transverse joint shall be constructed.
label | 1cd562f7-25f8-5a66-ac29-e512e9c7d51e |  | note | • Longitudinal joints in the wearing course shall be parallel to the traffic lanes.
button | 3a9f7f34-8bfb-568c-b6c4-690f858dd989 |  | button | Acceptance | Yes,No,N/A
label | 4955be7c-db8a-5505-9119-43c99bddce74 |  | note | Key - S
label | c95c3713-a4a7-5b44-9f25-221d61a47d53 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.6 - Surface Finish
label | c9476525-ed2f-5448-9fb1-0dc1d041b0ef |  | note | Ref docs - IFC Drawings
label | 8b6aa126-e370-5b0e-a150-84b55b7d291e |  | note | Acceptance criteria - The finished surface of asphalt wearing course shall be of uniform appearance, free of dragged areas, cracks, open textured patches & roller marks.
label | ca746d82-bafc-5449-8872-beba895978f4 |  | note | • Where asphalt is placed against kerb, the surface at the edge of the wearing course shall be either flush with or not more than 5mm above the lip of the channel.
label | 75a37bde-0848-5a41-9cc6-f8e7bad09f59 |  | note | • No point on the finished surface of the wearing course shall lie more than 4mm below a 3m straight edge laid either parallel to the centreline.
button | 1628b6a2-5c8a-50f3-8232-63e3d1be6dee |  | button | Acceptance | Yes,No,N/A
label | 1f78c43c-b9af-59e2-a634-5385d8694767 |  | note | Key - S
label | 3193e980-14e9-58bd-869a-f8bb64dde878 |  | note | Resp - SE
checkpoint-group |  |  | section | 3.0
checkpoint-status |  |  | checkpoint | 3.1 - Compaction Testing
label | 8d98d164-0fc2-5ea3-a7e0-6f123901181c |  | note | Ref docs - IFC Drawings
label | 611b9ab9-4b69-57e3-b1b0-3871e43bae1b |  | note | Acceptance criteria - Testing to be undertaken in accordance with XXX
button | 08f72404-5f56-5762-948d-81e59e823a2e |  | button | Acceptance | Yes,No,N/A
label | 50e1086b-1a8f-53c1-b5aa-b4483224a2d1 |  | note | Key - H
label | 60bcdeb0-8252-5cb6-ab9a-067a16031d5f |  | note | Resp - SE
label | 11ae20b3-057c-53e8-add2-8f1d750b57ac |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 18ad5657-1a33-5dd8-a7fc-f409126575fd |  | tickbox | Testing Attached
checkpoint-status |  |  | checkpoint | 3.2 - As-Builts
label | b12062fd-3508-57c7-9498-b607ac081a49 |  | note | Ref docs - IFC Drawings
label | efad21fb-c54d-5df1-bcfb-48f633c5d9f0 |  | note | Acceptance criteria - Measurements have been taken randomly throughout the lot & are within tolerance.
label | cc1b0125-bd94-515a-ab0b-c2e9076660c1 |  | note | Scale B:
label | d944a5d3-4b43-57a9-bdf5-32063f0dfa7c |  | note | • Measurements: 40
label | 46c2d5dc-d907-55fe-a5bf-a3088ebd43a4 |  | note | • Mean: ±8mm
label | 91b319de-3faa-5633-9ea8-99eb9c5a1838 |  | note | • SD: 10mm
button | ddf96c59-a2b2-5408-817b-df47fdfb4714 |  | button | Acceptance | Yes,No,N/A
label | b0709da3-8fc2-5c48-b07a-d8ce24a5ab80 |  | note | Key - H
label | dc5339af-91db-5795-af69-70c197e89a23 |  | note | Resp - SE
label | b9aaca72-bd5d-5a8e-90c3-fc9b2e2a49b7 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 6451c72e-8e5c-5c13-acff-6198d8e7626a |  | tickbox | Survey Attached
checklist-sectioned |  |  | checklist | CC0394 - ITP-008 - In-situ Pits and Culverts REV0 | itp |  |  |  | Yes | CC0394 - ITP-008 - In-situ Pits and Culverts REV0 | 34b9ca2b-5c5d-4e27-bf49-d08930f8c03f
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 0c74a490-ee98-5d76-9d97-a7462adc6936 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 6d20bceb-56e7-5732-bbd9-3ec9296789cf |  | textbox | Lot opened date:
text | 5fda9b40-4049-5b77-a75b-10eb9d996779 |  | textbox | Lot opened by:
text | 65f28703-7a38-5b65-8ee9-6faa270ae21b |  | textbox | Date lot closed:
button | e310b4bf-493e-5f63-951f-a5c8d4ceb169 |  | button | NCR raised? | Yes, No
text | dd325044-b113-53a9-b278-17e6f5f0f3d7 |  | textbox | NCR Raised Date:
button | c7608da7-dd47-5618-8974-78b1866d1e8b |  | button | NCR closed? | Yes, No
text | f441643c-b054-5d0b-9089-38d0e09f6f9b |  | textbox | NCR Closed Date:
text | eb12cf9a-9710-57c0-9c68-02a0b69233f2 |  | textbox | NCR Number:
text | 845af53d-5b77-525c-8f68-b2da57053201 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Planning
checkpoint-status |  |  | checkpoint | 1.1 - Determine lot size
label | 97f509bd-7920-5385-a745-7bb39f13f84c |  | note | Acceptance criteria - Lot Size = Each construction stage
label | 339d75fd-6e82-548e-be13-1cdc1b11b013 |  | note | Acceptance - Refer Lot Map
label | f82f6c9c-bf61-52dc-80b9-c246a52c2765 |  | note | SI Key - S
label | f061bad0-230e-5a6c-b86b-73092da630d2 |  | note | Resp. - SE
label | 28338d86-6a10-5374-9b04-32e380ac9ad9 |  | note | Remarks / record (e.g., test frequency, reports, certificates, checklist etc) -
boolean | e11a6b9a-5d95-5a19-8c67-8f82eae9a701 |  | tickbox | Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Survey Setout
label | 015e6738-047a-557c-9410-b86ecf91ee06 |  | note | Ref docs - IFC Drawings
label | 2eda739a-ddff-54f0-8f6d-bc239c47f11a |  | note | Acceptance criteria - Base of excavation and extents of pits/culverts pinned and checked to be correct line and level per IFC drawings.
button | 0487bb82-9c99-52dd-92b4-7d9c6af22d59 |  | button | Acceptance | Yes,No,N/A
label | 1351350a-f738-51c6-ab56-d3724aa8f1bc |  | note | SI Key - S
label | f8a110c5-3936-5735-a904-7598d116b8ad |  | note | Resp. - SE
checkpoint-status |  |  | checkpoint | 1.3 - Concrete mix
label | 0fb3c7d2-f763-53ce-b54d-9e4cb39e2520 |  | note | Ref docs - IFC Drawings
label | e3d998a8-6756-5442-a372-5b35bba956e9 |  | note | Acceptance criteria - Confirm correct concrete mix in use prior to commencement of pour
label | 5cdbdbcc-5eeb-5f70-bb15-7bb59eac72b0 |  | note | Acceptance -
text | a7b04606-8c00-5d93-9920-18a5f2fd415c |  | textbox | Concrete mix:
text | ceaad29b-a326-574d-9e15-070208796505 |  | textbox | Strength: |  |  | MPa
text | 01612b23-c4e1-59d1-bb96-c8cb152850ab |  | textbox | Slump: |  |  | mm
text | 56f6b5ce-6527-5252-b006-fc0dad47d7a3 |  | textbox | Aggregate size: |  |  | mm
text | 168ac446-64ae-555f-b9b4-31ab5975b4aa |  | textbox | Additives:
label | 8aa6189a-94fd-59d3-85a4-0a90d9a6478d |  | note | SI Key - H
label | 76dbca76-aaa6-59da-a3e1-be0905b8c3da |  | note | Resp. - SE
checkpoint-group |  |  | section | 2.0 Construction
checkpoint-status |  |  | checkpoint | 2.1 - Install Reinforcement
label | ecc5558b-377d-5e28-a79d-60d86f05d6ce |  | note | Ref docs - IFC Drawings
label | 350b9db4-247a-5737-8a35-cab4d16ec830 |  | note | Acceptance criteria - Reinforcement installed as per IFC Drawings and Specifications.
button | c0a1a608-0780-529a-971b-c07895c94237 |  | button | Acceptance | Yes,No,N/A
label | 77e84dbc-ec62-5d66-9c30-6db62aa692c7 |  | note | SI Key - H
label | 0c5bffc6-06fb-5046-b9ee-3ff4bc3ae9cf |  | note | Resp. - SS
label | 49a24611-7307-5566-9146-e9a849993435 |  | note | RJE Global - H
label | aa25a808-19d2-585e-b4a3-2f3eea8bea02 |  | note | Remarks / record (e.g., test frequency, reports, certificates, checklist etc) -
boolean | 54b29270-60d9-5303-991c-c7f25c672176 |  | tickbox | Pre-pour checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Formwork Setout and positioning correct
label | e64bc3f4-a180-55ba-a201-ef577e1d20a1 |  | note | Ref docs - IFC Drawings
label | 512a3e43-373b-50b8-a606-50fcd1b354f8 |  | note | Acceptance criteria - Formwork installed in accordance with IFC drawings to correct dimensions.
button | 37519b35-3caf-5434-87c3-c3a975a1b572 |  | button | Acceptance | Yes,No,N/A
label | 6e78299e-ae41-5a71-bb78-4bf8df40b28a |  | note | SI Key - H
label | 3aa05e0d-2f61-5a51-8264-e94cf7db54d6 |  | note | Resp. - SS
label | a47a88c7-ac2f-539a-a9f2-ec17d2f80b4a |  | note | RJE Global - H
label | 8c9a56e1-0437-552a-a15f-0866224bc23d |  | note | Remarks / record (e.g., test frequency, reports, certificates, checklist etc) -
boolean | 3f6ebac6-69af-5366-bcd0-25cdd117eb79 |  | tickbox | Pre-pour checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Concrete jointing
label | 716b9fc1-bf5c-535e-a316-f8b02b44225a |  | note | Ref docs - IFC Drawings
label | fe682a31-cbb1-54eb-837a-690f0da123b9 |  | note | Acceptance criteria - Construction joints to be installed in accordance with Civil Drawings and notes using correct materials.
button | 0d19835d-a924-5995-8f8d-ae3cda011747 |  | button | Acceptance | Yes,No,N/A
label | 56c6eed3-bcaa-5959-b1d4-00a98e0c8933 |  | note | SI Key - H
label | b2ffefb4-266c-5309-b174-e57b1cd05c52 |  | note | Resp. - SS
checkpoint-status |  |  | checkpoint | 2.4 - Concrete Placement
label | cbe93fd7-9078-5013-89c9-80b2d108e5f3 |  | note | Ref docs - IFC Drawings
label | 397a9ccc-b612-5768-b530-48ba023db53b |  | note | Acceptance criteria - Check Correct Mix supplied?
text | 6db16507-bd13-50c0-a13e-876e0ceec4b4 |  | textbox | MIX:
label | 98604e94-445b-5608-9863-eef7fa26339b |  | note | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
label | b8054829-1af5-5905-b2c6-cf6a157659dc |  | note | ○ Concrete to be tamped/vibrated to increase density and prevent voids, honeycombing or surface defects.
button | 4337d2ce-3826-5b8a-bc4b-51b47b41e33b |  | button | Acceptance | Yes,No,N/A
label | 6b4e0f52-e0e9-5d8a-87e0-63bb0ed12ced |  | note | SI Key - S
label | 54fc5e10-8ed7-5197-89ae-3e0e35bddfac |  | note | Resp. - SS
label | ec23ee02-cd16-5efa-9521-77284dfd6aa2 |  | note | Remarks / record (e.g., test frequency, reports, certificates, checklist etc) -
boolean | adf63e59-5380-576a-a6ae-4eca23ca9b46 |  | tickbox | Docket
checkpoint-status |  |  | checkpoint | 2.5 - Concrete Testing
label | 35713bb4-bac2-5ab8-bf86-977e29f25b20 |  | note | Ref docs - IFC Drawings
label | 02b5507c-65c0-5374-bdd2-b2c6f3eca439 |  | note | Acceptance criteria - Samples to be taken from chute at a frequency of 1 test per 50m3.
label | 485e3c5d-86e0-5640-a952-2fbe9d6fc8ec |  | note | ○ Each sample shall consist of two cylinder specimens for 28 day testing. Number of samples to be taken from Table 503.051.
button | 9b2d1467-1057-5ec8-9782-a037a22eb61b |  | button | Acceptance | Yes,No,N/A
label | d48b1185-41c0-596e-8eda-d864f0a2e6c2 |  | note | SI Key - S
label | 0c9d2d5c-7c2d-5091-8316-9002d661231d |  | note | Resp. - SE
label | b0b3d355-52e9-5ecb-917d-3aa97d93d1ff |  | note | Remarks / record (e.g., test frequency, reports, certificates, checklist etc) -
boolean | b5ae0260-8c93-56bc-9c9f-d118aab07d4d |  | tickbox | Test report
checkpoint-group |  |  | section | 3.0 Conformance check
checkpoint-status |  |  | checkpoint | 3.1 - Finish
label | 97ebbf21-9a9a-5378-97e0-35b181e8f46f |  | note | Ref docs - IFC Drawings
label | 65c0df29-da0f-5769-850f-a2dd84f2adfe |  | note | Acceptance criteria - Confirm finish is in accordance with IFC Drawings and specification.
button | 9dd69bb4-6695-54ec-b3e1-970198b7b682 |  | button | Acceptance | Yes,No,N/A
label | e5c7836c-fa3d-5c64-bf72-4de8ba5a4ee7 |  | note | SI Key - S
label | fefa9f5a-7381-53ae-bf5e-94d642453350 |  | note | Resp. - SS
checkpoint-status |  |  | checkpoint | 3.2 - Visual Inspection
label | 940101f8-bc3b-5d4e-ac67-e388d94a7c90 |  | note | Ref docs - IFC Drawings
label | 7e32c02c-f0d9-5ea7-beb5-81aae454b193 |  | note | Acceptance criteria - Do not cover or conceal work until it has been inspected by Symal.
button | ae747b40-dc96-507a-a11d-0ecde97af440 |  | button | Acceptance | Yes,No,N/A
label | 6258354a-a117-56f0-916a-24b4b9428d23 |  | note | SI Key - H
label | e0c11548-490c-51a3-a8b9-bd3b1e87122f |  | note | Resp. - SE
checkpoint-status |  |  | checkpoint | 3.3 - Concrete testing
label | 902e88da-a2ea-573c-958c-8520cc99f2f0 |  | note | Ref docs - IFC Drawings
label | d524d9a5-3ce5-5f2b-b93e-95e6da6ec15c |  | note | Acceptance criteria - Confirm specified compressive strength has been achieved
label | be67cc01-c501-59e1-aaf0-aed31afc8a24 |  | note | Acceptance
text | d6931108-7a3e-54b0-8aa5-edd9da87b868 |  | textbox | Specified strength: |  |  | MPa
text | 52125aca-3933-58ec-9962-c06e3784ce7f |  | textbox | Result achieved (28 days): |  |  | MPa
label | 0fc01afd-dd8c-56fa-a101-65b6908a61e5 |  | note | SI Key - H
label | f28f3340-74d3-5729-9657-d10591ece7cf |  | note | Resp. - SE
checkpoint-status |  |  | checkpoint | 3.4 - As-Builts
label | 95e636f1-b828-518b-ae26-c27461a3d9a0 |  | note | Ref docs - IFC Drawings
label | ceb87101-3870-5c23-8eee-c88914d4eb53 |  | note | Acceptance criteria - As-built survey of work lot attached.
label | 1f5dc30e-d149-5a05-b342-09fb2b0b22d1 |  | note | ○ All points within tolerance.
button | afd3f898-c920-5271-be2a-704b9710b516 |  | button | Acceptance | Yes,No,N/A
label | 6b005f70-f63a-5532-a3cc-1d7b852e704e |  | note | SI Key - H
label | cb3a6630-8d37-5cc5-bd1c-aef9f8fad949 |  | note | Resp. - SE
label | 01764cab-7967-5848-bef0-cf6ab3c2d731 |  | note | RJE Global - H
label | 22b33a9a-38dc-5740-b684-3108e19838ff |  | note | Remarks / record (e.g., test frequency, reports, certificates, checklist etc) -
boolean | 5b4a3472-9f88-54f7-a931-982cf095abb3 |  | tickbox | As-Built attached
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | CC0394 - ITP-006 - Concrete Pavements and Crossovers REV1 | itp |  |  |  | Yes | CC0394 - ITP-006 - Concrete Pavements and Crossovers REV1 | 40d3e093-effd-43df-ae2f-6f443fdd9aeb
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 3348630e-aabd-5ab7-98e5-d0a6cf769f0e |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 9e6d9d59-31f8-560e-af94-47a6fa83b8dc |  | textbox | Lot opened date:
text | 5b26d510-e614-5bd6-8f08-7e9140a4bca2 |  | textbox | Lot opened by:
text | 2baada01-88ea-5086-97f0-c9d06bcfc889 |  | textbox | Date lot closed:
button | 838d8bb6-4749-500c-b669-c3c123a93fae |  | button | NCR raised? | Yes, No
text | fff05617-fd37-5581-a4a8-a6ff31e049f8 |  | textbox | NCR Raised Date:
button | 0ba7b409-bb51-5a2b-8f75-56e504c9d06e |  | button | NCR closed? | Yes, No
text | 1bd5f238-f331-5c27-97fb-829785050525 |  | textbox | NCR Closed Date:
text | c4028a18-f278-5709-9fd3-d32ff9a1934e |  | textbox | NCR Number:
text | 87e5779d-7d54-592f-b1d9-d8ff78421519 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Planning
checkpoint-status |  |  | checkpoint | 1.1 - Determine Lot Size
label | 288ff9f0-0c0f-5d24-881b-6745a53bedb3 |  | note | Acceptance criteria - Day’s Productivity
button | 4abf30c6-4fb9-5386-bedb-90bc22c948cc |  | button | Acceptance | Yes,No,N/A
label | 67924608-3dc5-5349-bf69-201d63ab69c1 |  | note | • See Work Lot Map
label | 55767272-7d7a-589d-9281-0f363c571911 |  | note | Resp - SE
label | 131240b5-0a5d-5059-98f1-6e19bcd91d72 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 0dde3435-c3a9-507a-8f1e-30b48f928401 |  | tickbox | Work lot map attached
checkpoint-status |  |  | checkpoint | 1.2 - Survey Set-out
label | 3d3b7e4f-169e-5191-aa2f-5726ed66badb |  | note | Ref docs - IFC Drawings
label | 63c1252a-b256-5dcb-b19e-23c565a7c0b3 |  | note | Acceptance criteria - Has the work area been set out for line and level?
label | a8b8c181-3d13-5551-8946-7a16972326fc |  | note | • Preceding pavement layer has been picked up and confirmed within tolerance.
button | 0361da81-ecad-5d73-8312-cba4cbbb8408 |  | button | Acceptance | Yes,No,N/A
label | f17f06da-8d15-5c99-ab47-de8399176db0 |  | note | Key - W
label | cd6c2845-44d9-519f-8f0a-e1c5c0ea3aaf |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.3 - Confirm Pavement Type
label | b62f9f83-e6bb-573d-81cf-84ab25529657 |  | note | Ref docs - IFC Drawings
label | b6b0425b-fd30-5e32-85c0-38fa122e7953 |  | note | Acceptance criteria - Confirm pavement type/s within the work lot, and the concrete pavement depth associated.
label | 6e8aff10-bb00-5e6a-a217-86355910d0eb |  | note | Acceptance
text | a4c20fae-c602-5e9f-86c2-c0e76f9bf6d4 |  | textbox | Pavement Type:
text | 3d43ba8c-dd3e-5c24-9dd3-b44f518f86a9 |  | textbox | Pavement Depth:
label | 1ede0467-ac04-5062-a218-e06b87305aa7 |  | note | Key - H
label | 29fa6b8a-d342-569c-822a-51bb4d5bf36b |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.4 - Confirm Concrete Strength & Colour Required
label | e971ece6-b23c-5148-b0d1-d5a1b3607d3c |  | note | Ref docs - IFC Drawings
label | fafbd49a-634b-5709-ad9e-cee7decd36b9 |  | note | Acceptance criteria - Confirm correct concrete mix in use prior to commencement of pour.
label | cb3c948e-3321-5302-b4e6-8c064686f6ef |  | note | Acceptance
text | 1eac3363-6ca1-57d0-ae5a-83a154c2dd1b |  | textbox | Concrete mix:
text | 43d8e847-5679-5c97-a391-16b6ae6fdeb9 |  | textbox | Strength:
text | 682bb1df-34e5-5e3e-9e86-ea5bad879208 |  | textbox | Slump:
text | 3ab8973b-02fc-5db9-b777-5b0f47f634fe |  | textbox | Aggregate size:
label | be949665-d298-5a0f-83b9-fc30baca6351 |  | note | Key - H
label | c2f54ffd-58d3-5473-93b2-e72ed5b8c8e5 |  | note | Resp - SE
label | c8289bd4-3c6b-5279-a9f7-88bc80a910b7 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 4bd920c3-ddcf-5de6-a224-1a477b0b60a9 |  | tickbox | Docket attached
boolean | acdd2353-e9de-5a41-87db-f3984247ac1b |  | tickbox | Pre-pour inspection checklist
checkpoint-group |  |  | section | 2.0 Construction
checkpoint-status |  |  | checkpoint | 2.1 - Preparation of Subgrade and Base Pavement
label | 2dc6d343-05ba-5f8a-abe1-89f86b9f5beb |  | note | Ref docs - IFC Drawings
label | 7afc05df-08da-5f67-9ecb-5ffc0811be6d |  | note | Acceptance criteria - Subgrade trimmed and compacted prior to prior to placement of successive pavement layers.
label | 261610e8-4b75-51dc-9619-2857c07260e1 |  | note | • Subbase placed and compacted to the correct line and level. Confirm compaction and tolerance prior to commencement.
button | 0244a041-bf84-56a7-ae8e-b01055c882ca |  | button | Acceptance | Yes,No,N/A
label | e855f438-0927-59b9-9e25-f23e58ef2ab2 |  | note | Key - S
label | 5105aa39-7dcd-53ab-84be-9f3974ceb9fa |  | note | Resp - SE
label | 2f033678-ba10-5eba-8125-e71b887290fe |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 688cadbe-cf21-5d84-8900-1c7f46ddf5c3 |  | tickbox | QA for preceding pavement layers complete
checkpoint-status |  |  | checkpoint | 2.2 - Install Reinforcement
label | c89a864e-7fde-5814-bc61-3c1a7f9803ed |  | note | Ref docs - IFC Drawings
label | 95f3a620-ec2c-59ed-94f2-01b2c6bcf324 |  | note | Acceptance criteria - Reinforcement installed as per IFC Drawings, City of Casey Standard Drawings and Specifications.
label | 8b6c4137-3bd9-5f25-9125-aefe2fd0d23a |  | note | • Symal to confirm prior to commencement of pour.
button | 2fe193ad-559d-57a5-8ea3-e9f372b01d65 |  | button | Acceptance | Yes,No,N/A
label | 17a99b27-8d15-5989-b980-64df9a4a6e02 |  | note | RJE Key - H
label | 00755bba-3cc2-5de8-a7b6-338fed4f39a1 |  | note | Resp - Client
label | 0d879887-b5a0-5a3e-8402-49142ad502ed |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 6c026b9c-644d-583e-ad06-98007602cf25 |  | tickbox | Pre-pour inspection checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Concrete Pour
label | fd110373-94cc-5b85-96af-82e4a9f55a2d |  | note | Ref docs - IFC Drawings
label | 998503c4-e1db-5917-9470-4669ae9c6909 |  | note | Acceptance criteria - Confirm via delivery dockets that concrete is in accordance with that listed above.
label | 84a2961b-9ef7-575b-b80a-5639921d8be9 |  | note | • Contractor shall place concrete to avoid segregation. The placing of concrete in a section shall be carried on continuously until that section is completed.
button | 0633634f-4d7b-5409-bdb7-e5fb5ad56184 |  | button | Acceptance | Yes,No,N/A
label | 7cbfdcf8-b75a-5825-8054-f3e24acaa3a1 |  | note | Key - S
label | f95c0f83-6ea9-5c05-8c2d-9b8670bac086 |  | note | Resp - SE
label | 356c12e1-4a84-520f-843f-dc1304e1b3f1 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 1b9ab45e-ea62-58ce-b613-6e110901b487 |  | tickbox | Docket attached
checkpoint-status |  |  | checkpoint | 2.4 - Jointing
label | 686f4e43-8fae-53ab-a198-cb6ff121e48a |  | note | Ref docs - IFC Drawings, City of Casey Specification
label | 4f9934d1-4f8d-51d1-a055-f488fea9ca7e |  | note | Acceptance criteria - All jointing/saw cutting completed in accordance with IFC Drawings and relevant Specification.
label | 73ad75ea-b41a-5c77-a799-a21665607f85 |  | note | • Joint placement to be confirmed on site.
button | 5df49ff7-4528-538d-85a2-4fdd2f590fa5 |  | button | Acceptance | Yes,No,N/A
label | 25552cea-c7f2-524d-91fa-03a15d559e4d |  | note | Key - S
label | 44f5dea6-66c1-5e35-b7fd-0f50ae1301b0 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.5 - Concrete Testing
label | f09ec6ba-f01d-5375-a092-2a67255a9109 |  | note | Ref docs - IFC Drawings
label | 37707531-0e00-529a-b4f9-0fe628a767f7 |  | note | Acceptance criteria - 1 sample to be taken per 50m3 placed.
label | 99970e1a-9bc5-564a-beb8-81b2876ba2b6 |  | note | • 3 cylinders to be taken per sample.
button | bd010e1b-7158-5056-b7c0-ac2fbc4acf18 |  | button | Acceptance | Yes,No,N/A
label | 6031b5b3-f63e-5e23-a5ca-88b66c62b4df |  | note | Key - S
label | 9a15ccfd-c09a-55f3-931d-6c39ec20e1a2 |  | note | Resp - SE
checkpoint-group |  |  | section | 3.0 Conformance Check
checkpoint-status |  |  | checkpoint | 3.1 - Finish
label | 99206d4e-febd-5093-a941-825ab72a4ff9 |  | note | Ref docs - IFC Drawings
label | 059b1007-2689-5aff-b127-992c3853ec87 |  | note | Acceptance criteria - Confirm finish is in accordance with IFC Drawing and Casey City Council specification
label | fc3ea62a-2820-540d-9570-510e6a246cac |  | note | Acceptance
text | f23320e3-c7fb-5879-99b9-e43681def7ec |  | textbox | Finish Type:
label | 9cb97214-7246-5cee-9059-c345ce4f9182 |  | note | Key - S
label | 1c1e1e6a-dcc5-5736-a42f-80edb74f8cf6 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 3.2 - Visual Inspection
label | 520374a9-74e9-5135-aae0-aad00ede8128 |  | note | Ref docs - IFC Drawings
label | c24cdc43-7c0d-51c6-8bc6-e51a18523122 |  | note | Acceptance criteria - Do not cover or conceal work until it has been inspected by Symal.
button | 3e26c259-b6d8-5230-81fb-69e4938f0bc7 |  | button | Acceptance | Yes,No,N/A
label | 7383cbb4-cbd3-5f66-8c37-6fdbd9f01ebc |  | note | Key - H
label | 6982d7cb-9296-5af0-856d-3d3c699b3077 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 3.3 - As-Builts
label | 091fe252-e0f0-5e63-a71d-5e1be24bd5d6 |  | note | Ref docs - IFC Drawings
label | 62fdcc6d-7b2b-50e6-9012-69bfa421dbf9 |  | note | Acceptance criteria - As-built survey of work lot attached.
label | 6bacebb5-ff73-531a-9fce-cef789f5a4a1 |  | note | • All points within tolerance.
button | 59815728-5702-5b3a-8e73-52295b795207 |  | button | Acceptance | Yes,No,N/A
label | 2be2531d-5b85-54f2-a02a-6a7216f6d46d |  | note | RJE Key - H
label | 40bbc28c-4894-5767-b4f3-5da2bf926487 |  | note | Resp - Client
label | 54450b8d-3d3f-5831-bf5d-ee7185280447 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | e8d5778a-39d1-5897-9273-4a25259f9e9f |  | tickbox | As-Built Attached
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | CC0394 - ITP-002 - Site Clearing | itp |  |  |  | Yes | CC0394 - ITP-002 - Site Clearing REV0 | 58eeac06-ed6b-4de0-a80b-e663e05692aa
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 3b6c3a68-cca1-5a9b-a966-2c70a2dc9fb7 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | e2bd9e23-e0d3-5efa-867a-a3fe7d1073a7 |  | textbox | Lot opened date:
text | 1f55bfc9-1d5d-55ed-aa98-1b99a8d8412e |  | textbox | Lot opened by:
text | 3824323a-1872-5f6e-a2bf-992b26d721a3 |  | textbox | Date lot closed:
button | 2fbf7eed-5d9a-5219-83d4-f50c9199aff3 |  | button | NCR raised? | Yes, No
text | 68c19e9f-9ed7-52ea-bca6-a24e6234bc0e |  | textbox | NCR Raised Date:
button | 3823d64f-ac8c-52ac-ba78-7fd521c46a29 |  | button | NCR closed? | Yes, No
text | 0d3b3894-48f5-51ec-8760-4361fcd27507 |  | textbox | NCR Closed Date:
text | 64c56f7e-73e9-5526-a132-ba9d2b94d79a |  | textbox | NCR Number:
text | 1c578cd2-67f4-5a5d-8ed0-64a4aad89ba6 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Pre-start activities
checkpoint-status |  |  | checkpoint | 1.1 - Determine Lot Size
label | f7807aec-e164-50e6-8aef-5bb5f34cd206 |  | note | Acceptance criteria - What is the lot size?
text | 752ccd74-b74e-542b-8342-a2525389d441 |  | textbox | Acceptance |  |  | m2
label | c97e8986-5ac5-565c-96d6-0d56a614f637 |  | note | • Maximum lot size = 4,000m2
label | d13c00b7-a4e9-5787-9cc8-204c999321f1 |  | note | Resp - SE
label | 69ea02df-ba9a-5a5e-bec4-91cde94baede |  | note | Remarks/record (eg. Test frequency reports, certificates, checklist etc) -
boolean | ed96472e-d01b-5a87-ab0b-4b76f051ca92 |  | tickbox | Work Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Safety
label | 5bf8445e-a109-5e3f-a040-cb303aaf7a79 |  | note | Ensure that the following items have been actioned:
label | cfbfcc5a-1b3e-5a14-8842-2b01efe8b34e |  | note | – SWMS if applicable
label | 3a63f73c-409f-5b62-9b19-b22db6402654 |  | note | – All staff inducted
label | 25616709-ca6a-56d9-8b46-77a1e096e3e3 |  | note | – Plant Pre-start Inspection
label | 04f4e359-26de-5d96-abc6-f93bf0518bb4 |  | note | – Service locations identified
label | 21da4d9a-472c-504a-9706-a35018b68b02 |  | note | – Traffic Management Plans (if req’d)
label | e9a00efd-8bf4-5b76-8e69-3abed64ff6a6 |  | note | Ref docs - SMP
label | 9a020ed8-0fa3-571f-8679-6174a495fed6 |  | note | Acceptance criteria - SWMS submitted reviewed and accepted if required.
label | 95c01732-1db4-561b-bf54-f7bf47ea3bee |  | note | • Personnel inducted to RJE requirements.
label | bd0b4199-f24e-5207-8635-45e6070c1b56 |  | note | • Plant inspections completed and entered.
label | eb780fac-89fc-59b7-9581-2faf322f7a89 |  | note | • Pre-work briefings completed.
label | 04fe9857-e834-5ee7-9be7-8a0b77503e10 |  | note | • Service diagrams available and services located.
button | b91549ef-ba90-5c9a-ae9f-3f84daeb00dd |  | button | Acceptance | Yes,No,N/A
label | 8b4137cf-e920-5b59-a602-4222f279ac8d |  | note | Freq - Once (Pre-Start)
label | 3f3834e7-5fc2-5f66-9a5f-ba4da4b3b55f |  | note | Key - H
label | e3e577dd-18d7-59f8-aa86-22f60a94b3e0 |  | note | Resp - SS
label | f93e0368-54f4-5b98-b419-1a6e768b7441 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.3 - Excavation Permit
label | d500396a-a498-57ed-ac93-761f202e9d90 |  | note | Ref docs - SMP
label | 9b21c6b6-0cd9-5076-b928-73d90b152efd |  | note | Acceptance criteria - All identified underground services marked and potholed to confirm location and depth. No machine excavation within 1m of underground services. Permit available and signed.
button | 8baeda0d-0980-57a7-b90f-89a87167451b |  | button | Acceptance | Yes,No,N/A
label | 10be78ff-4e79-5854-8cfc-63efc51c2fed |  | note | Freq - Prior to start of works
label | 00a46745-b4c7-554d-af65-7775dd9cf7ef |  | note | Key - H
label | 459a4644-9e77-547d-99d5-552f6641e530 |  | note | Resp - SS
label | 424415f6-4300-55be-a842-8336f3624006 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Check Survey Set-out
label | c3d59870-5dde-580c-8680-756f147078ff |  | note | Ref docs - Construction Drawings
label | 28e35b1a-c922-5d89-a1c1-94e41e7f0584 |  | note | Acceptance criteria - Survey setout extend of works
button | 7b2f5a08-ec44-521b-8663-ad06d0edb100 |  | button | Acceptance | Yes,No,N/A
label | 7eccd965-7336-5649-be37-a11f9f0f0b27 |  | note | Freq - Prior to start of Works
label | f58f2e00-b027-5ae9-b7c4-a4ff91ba2237 |  | note | Key - H
label | 262f3c23-b424-5e6a-a1c3-f460381f11cf |  | note | Resp - SV, SS
label | 0b8da06f-bf49-5b9d-8b6a-1dd9cc28a5b7 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.5 - Tree Protection
label | 7e345987-57e6-5bfc-85c2-345593fc6a51 |  | note | Ref docs - Construction Drawings
label | ff63792c-5638-58a1-b19d-d055e1689296 |  | note | Acceptance criteria - Have all trees / native flora and fauna been protected including the establishment of no go zones as indicated in the construction documentation, CHMP and CAB?
button | 63eb3e76-b8b9-5fbe-89ab-f8e1fbbc6c9b |  | button | Acceptance | Yes,No,N/A
label | 7b44ddd0-e98e-564f-bde0-137fd38c85f0 |  | note | Freq - Prior to start of Works
label | 782f597b-8289-59b0-8144-b58b191330d4 |  | note | Key - H
label | 50bac8b5-f075-5a19-b717-de591cde63d0 |  | note | Resp - SE
label | 38256ef8-e1eb-5c2a-877a-bf04a6fc9d54 |  | note | RJE Key - S
checkpoint-group |  |  | section | 2.0 CLEARING AND GRUBBING
checkpoint-status |  |  | checkpoint | 2.1 - Clearing and Grubbing
label | 2462ff2f-10fc-54f7-b2aa-747ec775d92f |  | note | Acceptance criteria - Have the identified areas been cleared of all vegetation, refuse, unsuitable material and obstructions down to natural surface?
label | 7fdd760e-5997-5100-b2e6-2f34b5dd7cfc |  | note | • In areas where excavation will be made, all vegetation, refuse and obstructions shall be totally grubbed.
label | 0bf729ce-679b-53b6-97b3-4b7d4d0efb20 |  | note | • Unsuitable material and topsoil is to be stockpiled in the designated location and is not to be used as fill material.
button | 39bab999-9379-54e0-a5b7-5acbb873c588 |  | button | Acceptance | Yes,No,N/A
label | 1223337b-e247-5f74-886f-cd09dbbac475 |  | note | Freq - Visual Inspection
label | 280715b1-12eb-5faa-9272-f070c305e987 |  | note | Key - H
label | fa6a3fc8-34c2-58f3-b3fa-08d5479e9e99 |  | note | Resp - SS
label | 47d351a8-3e33-5978-9d78-1084df10a062 |  | note | RJE Key - S
checkpoint-group |  |  | section | 3.0 Topsoil Stripping
checkpoint-status |  |  | checkpoint | 3.1 - Stripping
label | a9eac23a-c936-5084-a7a8-31c264dd3616 |  | note | Acceptance criteria - Is the appropriate equipment being used to ensure topsoil and subsoil layers are not mixed.
button | 92d3d99e-91c9-5e8b-b3ac-4b56905450d0 |  | button | Acceptance | Yes,No,N/A
label | 78e4c586-2b95-5960-a9d3-66ea8d2afead |  | note | Freq - Visual Inspection
checkpoint-status |  |  | checkpoint | 3.2 - Stripping
label | 9809ef4a-f775-57bc-b45c-fa88664efca4 |  | note | Acceptance criteria - Has the area been stripped and stockpiled to an appropriate depth (minimum top 50mm) removing surface topsoil and unsuitable material in a way to leave the surface evenly graded and free-draining?
button | 01739821-b188-505f-9232-4d749a03302e |  | button | Acceptance | Yes,No,N/A
label | d52ef1d6-b81f-5e53-9067-6a28c10f1cd4 |  | note | Freq - Visual Inspection
label | 0cf03221-c28a-50bc-b417-c81eda113541 |  | note | Key - W
label | 768fd132-ceca-5c02-808b-165365da6e54 |  | note | Resp - SS
label | bc83a625-d949-5e47-a6b9-1c6b93ab18b8 |  | note | RJE Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Top soil export / stockpiling
label | 069501f5-821a-581a-baaf-4caed7dae7df |  | note | Acceptance criteria - Has the topsoil being stockpiled been approved by RJE (where applicable).
label | 3bfdb715-c098-5b15-8d48-2755f2128040 |  | note | • Have the environmental controls as per CEMP been adhered to?
label | 9119b2cd-93b0-52ae-ba90-cbb84616abbb |  | note | • Dispose material as per CEMP requirements
button | ad46d5fd-b3d9-509e-8d39-3d40fe6eeb0a |  | button | Acceptance | Yes,No,N/A
label | e745af21-8708-5b59-99cc-c24ab531fcd5 |  | note | Freq - Visual inspection
label | 2fc47736-e634-5297-b8d7-4a28fec15c39 |  | note | Key - W
label | 6828553b-1abf-5065-b111-e32de2fb7378 |  | note | Resp - SS
label | 14d4e314-2ccd-57f8-b5f2-0ea97c8b6cb6 |  | note | RJE Key - S
checklist-sectioned |  |  | checklist | CC0394 - ITP-007 - Electrical Trenching and Blinding | itp |  |  |  | Yes | CC0394 - ITP-007 - Electrical Trenching and Blinding REV0 | 92197c99-6a82-4fd4-ab91-ab962d9d1745
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | dd8b00dc-8cab-5de1-8746-0467e13c9ab0 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 25db0c82-560f-5f94-bbf1-ca1f4ccd85d7 |  | textbox | Lot opened date:
text | 2e33025e-b3dc-572e-9872-1e7d37fdae08 |  | textbox | Lot opened by:
text | d47a4330-1ca6-5ae4-b119-1c6e3b8ea07a |  | textbox | Date lot closed:
button | 0b8e5971-008f-503b-bbc5-3aef9ac0f0a1 |  | button | NCR raised? | Yes, No
text | 763366a6-644f-55d8-b587-a1d93162fde4 |  | textbox | NCR Raised Date:
button | caca3108-380b-5b9f-a83a-73fab573aa64 |  | button | NCR closed? | Yes, No
text | 7bef9975-c448-547f-97ba-5b2424bdac9e |  | textbox | NCR Closed Date:
text | f98b3dc7-dc68-59c7-8df9-111e537899b3 |  | textbox | NCR Number:
text | 79060d55-3eb4-5186-9311-01a4bfd8d5b0 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Pre-start activities
checkpoint-status |  |  | checkpoint | 1.1 - Safety
label | 7e667819-06ae-5750-a40b-466af5bdb5ae |  | note | Ensure that the following items have been actioned:
label | ca14772a-e4c7-5b4f-ac8b-7242e7157f5d |  | note | – SWMS if applicable
label | f23cbee1-edbe-5b6b-9ca2-50234c1f69b6 |  | note | – Plant Pre-start Inspection
label | 2af08f78-173e-524e-80e9-b636a7ec74de |  | note | – Service locations identified
label | 6d84558a-35f3-5cfb-b597-71478be1c184 |  | note | – Worksafe notification in place
label | d2899939-167c-5285-9b5d-9d2078e75a68 |  | note | – Traffic Management Plans (if reqd)
label | 8a21da43-3ba4-53fe-a08b-88a6449ef6ce |  | note | – All staff inducted
label | 36a17ce6-5f88-56c8-9f52-0721bb5def20 |  | note | Ref docs - SMP
label | e9e55375-6d56-5c66-ae89-c0c3facc8131 |  | note | Acceptance criteria - SWMS/WMS submitted reviewed & accepted if required.
label | 39eb7ab4-c5c7-5e5c-9143-194ef113c050 |  | note | ○ Plant inspections completed & entered.
label | 24388a4c-a563-50e5-b5c5-588011ad59a9 |  | note | ○ Pre-work briefings completed.
label | 9d0f5a01-a69b-5e9c-b0b0-29d00cf5ef19 |  | note | ○ Service Diagrams available and services located
button | 52fbd892-2b4f-57e1-9345-817d3cec6d66 |  | button | Have any/all of the above SWMS been reviewed and are available to all staff and signed onto every month? | Yes,No,N/A
label | b9e8fad5-f19a-572b-a02f-37a6cb63ca73 |  | note | Frequency - Once (Pre Start)
label | 7a59770d-1bf1-5916-a86c-d18d91b0041a |  | note | Key - H
label | 60939604-6682-5ea7-951b-cae45b94223f |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.2 - Environmental
label | bcb9ca4c-18e8-5b59-a9ac-b261dcd32d76 |  | note | – Air & noise levels
label | 700d2136-33fa-547c-90f6-1cf2051a399a |  | note | – Sediment & erosion controls
label | 7d79f4ac-d8cf-58ae-a235-7f974f76a318 |  | note | – Heritage controls
label | 7ea6fa70-e52c-589f-a035-b22fb1cc4518 |  | note | – Dust control
label | 2d9cd36b-33c4-57d3-a862-b26066b50e3e |  | note | – Water quality
label | 186940ed-e3b5-58d8-ba0a-dac5e0718f7f |  | note | Ref docs - EMP
label | 283c2c5c-45a2-56ea-a142-9fd50d89de2e |  | note | Acceptance criteria - Site Environnemental Management Plans (SEMP) on site.
label | 308032d7-ee5b-53c4-87bb-1905890f5565 |  | note | ○ Controls installed as per CEMP.
label | 388b0a70-a4de-5bb6-bf60-99b097077333 |  | note | ○ Water available for dust suppression.
button | 3cbd7b3b-d428-5f04-87ae-d064817f8c9d |  | button | Have any/all of the above management plans been acquired and are available for review? | Yes,No,N/A
label | 3180aa27-7c40-55a8-99c8-bf62e54a025b |  | note | Frequency - Prior to excavation in each location
label | 30f3e54c-662a-57c9-8d38-2ecd31ae1720 |  | note | Key - H
label | d6f5c501-7861-55f8-a84e-a61af3bd174c |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.3 - Excavation Permit (if required)
label | cbd8c62d-31cf-5eec-8d13-5d734d968ce1 |  | note | Ref docs - Worksafe Excavation Permit. Symal Ground Penetration Permit.
label | 9a2afe90-eeae-544c-8fe7-66773f26b062 |  | note | Acceptance criteria -
boolean | f6ab3966-6320-50f4-9d12-dd7e521cd590 |  | tickbox | Penetration Permit
boolean | a0d40dbc-9a7e-5dc4-94a2-0eaba5d1b1ae |  | tickbox | Excavation Permit
label | 90a02e7e-3235-5122-92d3-4fb014073165 |  | note | Frequency - Prior to start of works
label | 2d27e7b2-3e23-5901-bca6-bc3ae2abb966 |  | note | Key - H
label | 948a2de7-10fc-5a91-b808-4dbbf90e5b77 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.4 - Survey Setout
label | 5467e7cd-eda1-5c4f-ab03-71820a0c74ff |  | note | Ref docs - DWG: 5668-122-1020 Rev 0, DWG: 5668-126-1005 Rev 1
label | 2cd9c501-6118-574e-afa2-38e15399b3c2 |  | note | Acceptance criteria - Peg location of proposed underground services with levels from end to end.
button | 48254d82-3208-5dc8-8ca1-9eccc9123e4d |  | button | Has the above been completed and approved? | Yes,No,N/A
label | 0bc71398-2192-5387-abd1-0d0e4844accf |  | note | Frequency - Every section of Culvert
label | 2edf44dc-161b-5b14-b50b-7b7f3f601be4 |  | note | Key - S
label | a79ebd79-eace-525a-a53c-0f8d6e4d091b |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.5 - Material Classification and Source
label | b9241309-96e1-5dd3-818c-141109312fe0 |  | note | Acceptance criteria - Mix design to be approved prior to placement.
label | 09c36a72-0af6-5853-9240-0fdf671fa932 |  | note | ○ Material properties meet project specification, AS 3600, AS 1379. 25mPa as per construction drawings.
label | 9efa19c3-822c-5731-b4c2-8b61c5d62fda |  | note | Frequency - Ongoing
label | 63169682-885a-5b57-88d4-b9092e2f6cde |  | note | Key - H
label | b7cc97c7-13a6-58f4-b688-20ed0b3607bc |  | note | Resp - PE
label | 7cb29caa-f39a-5c05-9005-96654f2c6851 |  | note | RJE Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.6 - Determine lot size
label | f80bf9f1-52ed-5e01-b93c-7557bb4cd27d |  | note | Acceptance criteria - Lot Size = Each construction stage
label | a9cd204d-1788-55d7-9208-be4236f8486d |  | note | Frequency - Ongoing
label | 13db0833-7281-5829-8e00-921fd602796b |  | note | Key - S
label | 8d6d8a1a-613a-56e6-9397-f37377c0abb3 |  | note | Resp - SE
checkpoint-group |  |  | section | 2.0 Excavation
checkpoint-status |  |  | checkpoint | 2.1 - Excavate to width and depth as per survey pegs
label | 770eaaba-d57f-5f34-a0ce-d90c1ea24cc9 |  | note | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | d3929eba-6b1a-5193-ab90-426a678776aa |  | note | Acceptance criteria - Trench depth nominated tolerance is 0 to -20mm. In reference to the depth of the culvert.
label | 2772ee3c-d794-5578-a655-364c4f357d04 |  | note | ○ Trench Width is as per drawings provided. Typical trench width will be 1.6m.
label | 6794078a-e141-5001-ab56-7a2ca7d2ac29 |  | note | ○ Road Crossing trench width will be 4.5m.
button | 95238d6f-fdae-5da4-8ad6-5c02ab6ea15b |  | button | Have the above depths of cover been achieved and approved? | Yes,No,N/A
label | c5b04092-409e-5839-848b-646ed1cdf7e1 |  | note | Frequency - Entire length of Culvert
label | 9252c1d6-b352-5506-af72-a04973056b73 |  | note | Key - S
label | 030d46b1-7e90-5d80-9a57-08d91ad8ab43 |  | note | Resp - SE
label | 04a6c341-72c9-5c17-9a69-6743626e6854 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos of trench width and depth.
checkpoint-status |  |  | checkpoint | 2.2 - Damp Proof Membrane
label | c48261da-a083-53b2-8035-56d744a12158 |  | note | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | 3153a618-70b2-58b4-a962-5bfc7f532743 |  | note | Acceptance criteria - Has the 0.2mm damp proof membrane been installed with accordance to the design drawings?
label | 86a92dec-3478-5336-9d5c-7b9d902c2251 |  | note | ○ The DPM extends up the sides of the blinding on both edges, above the surface of the blinding.
label | ca625dac-1743-5141-8d51-f47a4cf1b0ea |  | note | ○ Has the DPM been laid and overlapped at 200mm along the length of the culvert trench.
label | e9a3bd8a-4a18-5731-a8a6-b57d5970b2a1 |  | note | Frequency - Entire length of Culvert
label | 910a2045-2f9b-5514-9e31-fb0ad38c316c |  | note | Key - S
label | 9f834a8c-f58f-5296-8b01-e0b36a0a6b98 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.3 - Connoly Joint Installation
label | 23b31ce6-b77e-5169-81b5-b9c7fee52a48 |  | note | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | 99713d60-7666-59fc-b3ff-c82d13bdd395 |  | note | Acceptance criteria - Have Connolly joints been installed at 2500mm spacings. Nominated KJ100.
label | f510f969-71cf-55eb-8906-8f1ec128604a |  | note | Frequency - Entire length of Culvert
label | 9de07bfb-e70b-5c79-94d7-1bac09522301 |  | note | Key - W
label | 9e83795c-6d5e-5f5d-8196-52ae0ce17974 |  | note | Resp - SE
label | 7a3fc468-ba24-5fdc-a548-9b5609ed50ba |  | note | RJE Key - W
checkpoint-status |  |  | checkpoint | 2.4 - Installation of Formwork and boxing/finished levels
label | 9606a5a8-b500-5928-8842-2c8761b03dcb |  | note | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | d941faed-6c9c-5d48-8b96-e32e6937c70e |  | note | Acceptance criteria - Has formwork or boxing or height pins been installed as per the nominated design tolerance of 0 to -10mm of the design finished level of the blinding. As per the nominal datum of 10m.
label | 07416bd0-37e6-5470-991e-6710e8656714 |  | note | ○ Note: RJE are to confirm applicable height of Concrete Culvert segments.
label | 728026f1-28b5-5875-a44a-59a0e711cf50 |  | note | Frequency - Entire length of Culvert
label | 744cc176-ab96-528f-9a87-bf3c1626530a |  | note | Key - H
label | dbb83fd0-f09d-51f0-a0f8-22c2c6716e80 |  | note | Resp - SE, SS
label | b03a6784-3a16-5dd3-bf85-7b938798fbb5 |  | note | RJE Key - W
checkpoint-status |  |  | checkpoint | 2.5 - Pre pour Inspection
label | 25b64100-dba0-548e-ba1c-aa1678deba81 |  | note | Ref docs - Drawing no. 5668-126-1005 Rev 1, Pre-Pour Checklist
label | 8dfea843-fe52-5b3a-bf3d-ac8a02a22b5f |  | note | Acceptance criteria - Pre-pour inspection undertaken, confirming that all requirements have been met and pour can be completed.
button | 6e467a89-cf53-5b3e-9a29-22ef7e141153 |  | button | Has all requirements been met, RJE supervision involved in inspection and approval given and considered ready to pour? | Yes,No,N/A
label | c32499b2-ddfe-599b-baf5-12526b06263d |  | note | Frequency - Entire length of Culvert
label | 2c3fb132-abf7-5cc6-b089-21c2273abdcf |  | note | Key - H
label | 78c1046b-b689-5e21-8227-a2c6ce57515a |  | note | Resp - SE, SS
label | bc04be13-2ef1-51ba-9ea4-8e175013e2fd |  | note | RJE Key - H
label | 14157df4-cd4a-5ff7-bec2-bc2e86c56b7a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre pour checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.6 - Finishing
label | e8e1809e-db2d-519c-b05e-40d4ab7b0656 |  | note | Ref docs - Specifications
label | e1a8fe54-82c7-5e72-8a93-9095dc9bcd1a |  | note | Acceptance criteria - Steel Trowel non-slip finish nominated.
label | abc6fb7c-689d-5fc2-96eb-1b5ea1ed5cf8 |  | note | Frequency - Entire length of Culvert
label | 909cdda4-9044-585b-adef-fa14baacf193 |  | note | Key - W
label | 4db9f074-6c71-59e4-b34c-8838870d1b9c |  | note | Resp - SE
label | 449ad115-bc65-584d-9651-d3c768fa6e25 |  | note | RJE Key - W
checklist-sectioned |  |  | checklist | CC0394 - ITP-004 - Storm Water Drainage | itp |  |  |  | Yes | CC0394 - ITP-004 - Storm Water Drainage REV0 | 97625f6e-fd62-47be-a45c-3f2bef96873d
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | e9730a03-9070-5230-aa8d-9d48ff0a2eb2 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 7282fdfe-a1f6-5e63-aefd-35502f7a368b |  | textbox | Lot opened date:
text | c71139f2-3475-5dcf-944c-a0eda5d455c6 |  | textbox | Lot opened by:
text | 0964c8e1-ec96-598c-87f8-c3d82d19fd3c |  | textbox | Date lot closed:
button | 28809a85-c9a4-5b04-be68-7b04306676ae |  | button | NCR raised? | Yes, No
text | bc2554fb-57ea-5d74-bd01-23d13e8197d7 |  | textbox | NCR Raised Date:
button | e67e745c-6936-5633-be82-169eb6dc5029 |  | button | NCR closed? | Yes, No
text | 402f5e8f-d1f2-5f8e-9d0b-787400626b84 |  | textbox | NCR Closed Date:
text | c31f66b2-41a5-5c8e-972e-8fae9ebc556b |  | textbox | NCR Number:
text | d5e09318-a3c9-58fa-a231-7a00174f40d7 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0
checkpoint-status |  |  | checkpoint | 1.1 - Determine Lot Size
label | b587ef64-134f-5fb8-b0fb-4d7059cfea1e |  | note | Ref docs - IFC Drawings
label | 508c1d6c-f03a-5d77-b4b4-bd8bc6a6087b |  | note | Acceptance criteria - Pit to Pit
label | 62504270-9d96-5acc-8ab5-f158f3d04d4d |  | note | Acceptance
text | c9e40a8b-2a7c-5a48-97c2-3d3bc86db137 |  | textbox
label | ecf2017e-22d0-523b-a36f-c3f2c566f032 |  | note | to
text | 8181fd9d-bfc8-5550-a11b-08b23f949a23 |  | textbox
label | d92550ff-52d2-54e7-b858-ce14be01e924 |  | note | Resp - SE
label | 1a9d58a6-4f98-5648-abd3-064fb72d7481 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 209c4e8f-57e0-5c8d-909e-33dfcfe59cf4 |  | tickbox | Work Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Survey Set-out
label | a15ec3ea-33ef-5417-95b8-9965e83e2d52 |  | note | Ref docs - IFC Drawings
label | cb6c9084-8209-5bd4-b25f-e924a4ae9c11 |  | note | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all drainage lines including manholes, temporary benchmarks, sewage wet wells etc.
label | 4d050374-6c2c-5e11-b3b3-39828758651d |  | note | • Clearly mark limits of works.
label | 4627a097-17b1-5848-bd87-1ca597e08012 |  | note | • Chainage, offsets, cut/fill level, cutting slopes, grades and cross sections specified or shown on the drawings, etc.
button | 3865a30e-5146-5fba-bdae-2079055a66e6 |  | button | Acceptance | Yes,No,N/A
label | b12d63ce-e5cb-556e-a28e-8c5ad8f367a5 |  | note | Key - W
label | 639638e3-2fbc-579b-a341-0168df1d65ea |  | note | Resp - SE
label | 1c504bc0-dd23-512b-a7d5-f92a69392dd1 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.3 - Approved Material Type
label | 4060fb57-94d1-5b5f-b8ab-838caac1692d |  | note | Ref docs - IFC Drawings AS1260
label | 037d16d0-3ef9-5f18-987d-e8876aa2f424 |  | note | Acceptance criteria - In accordance with IFC Drawings:
label | 807a0f30-7bb2-561e-b447-9035c41ac231 |  | note | • Storm Pro
label | f3476ab2-faa1-53c8-9a99-8a6512fadf1f |  | note | • PVC
label | 4ab98be7-0bfd-576c-a53a-121619a5d5b5 |  | note | • All pipework to be clearly labelled & detectable to identify it as stormwater drainage.
text | 23195226-3728-5f70-a673-f27ecf1dd2d4 |  | textbox | Acceptance | Yes,No,N/A | Pipe Size/Class
label | 263c366d-0e49-5407-95ac-a6319f585f42 |  | note | Key - H
label | 03797eed-d44d-54a1-ab67-f809a57646ac |  | note | Resp - SE
label | 94b1121c-105f-5703-bff5-1432f2ecc7cb |  | note | RJE Key - H
label | 472a16a8-fbb2-5511-8847-0d3e60156aa1 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | d5f8de15-b26c-5c9c-89ed-4c78029f9f18 |  | tickbox | Delivery Dockets
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Excavation of Drainage Trench
checkpoint-status |  |  | checkpoint | 2.1 - Excavation
label | 934f8e53-616b-59c0-b49d-c96b884e6759 |  | note | Ref docs - IFC Drawings AS3500
label | cf76e192-5177-59a4-ae06-ade1f6a15bd9 |  | note | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | 425421af-c07a-5af9-8746-d897dc389f7c |  | note | • Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
label | 7260ce23-8e81-5835-a731-3f95b79a3904 |  | note | • Keep trench width & depth to that required by the service & its bedding method.
button | 8f38e0e5-0c8c-57dd-a41f-7c42d8417565 |  | button | Acceptance | Yes,No,N/A
label | d94813f9-8eb7-5b65-8d5b-54fa9c2ebebb |  | note | Key - W
label | c943b201-88db-5ee5-a984-662b62287b1f |  | note | Resp - SE
label | e0e3e507-2ed2-5f6f-a13c-5e53f932b4b5 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Removal of Obstructions
label | c7410587-9149-59f6-ad37-aa1e0e466713 |  | note | Acceptance criteria - Remove obstructions including roots, stumps, boulders and the like which may interfere with the proper functioning of the service
button | 92be3b15-5a04-5a5c-bb7f-c4dd66eaae6a |  | button | Acceptance | Yes,No,N/A
label | 84469ef8-a74a-5ef9-9679-314a295c0a33 |  | note | Key - S
label | 6ae6c82a-f174-55ce-85ee-3e1b57bbb311 |  | note | Resp - SE
label | 6a4f1a79-02cf-5d99-8ca7-f17ccab17080 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 2.3 - Water Management
label | 5b544aff-9b9b-53a6-998b-f041482a1708 |  | note | Acceptance criteria - Symal shall maintain all excavations in a well-drained condition.
label | 65e2aa92-622e-5b4b-a1fc-9cc52f1f61cd |  | note | • No bedding material or pipe work shall be placed in excavations containing standing or running water.
button | 484d5136-5866-52d9-837c-0859525462b2 |  | button | Acceptance | Yes,No,N/A
label | ec57d7e4-dab5-5128-ad1a-03bf17dd63cc |  | note | Key - S
label | 2b5137ae-8c91-50a2-86c6-d7859949df0a |  | note | Resp - SE
label | ad17f790-66be-5f6e-9688-1739f1a4d351 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 2.4 - Bedding Material
label | c55840c5-3eff-5d83-830a-02df30296ec1 |  | note | Ref docs - IFC Drawings
label | 70a9782f-b3cb-5d0d-a8f4-77ce3f0ca97c |  | note | Acceptance criteria - All pipes shall be installed with 5mm A grade crushed rock or similar to AS3725
button | 3bfc5fbc-bf5c-5d80-aeba-f8e24cfe6da4 |  | button | Acceptance | Yes,No,N/A
label | 18964554-5fb5-52ba-ba20-904823f2674c |  | note | Key - W
label | dcdc47c4-70d7-5c55-b65c-df90d8d841c3 |  | note | Resp - SE
label | af9a6f7d-aed0-5ba4-9893-7dc4e0a3b593 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 2.6 - Compaction of Bedding
label | f8044471-afef-504c-b8ec-0516e95f5683 |  | note | Ref docs - IFC Drawings
label | e255f888-b5bd-5388-9dc1-de4516765192 |  | note | Acceptance criteria - Bedding material shall be compacted to refusal handheld mechanical equipment.
button | 1238c908-6c28-5c4a-9703-4b016c5507b7 |  | button | Acceptance | Yes,No,N/A
label | 4adcdb04-7cda-58a6-9d77-bb1cd8c1404e |  | note | Key - W
label | af5fbaa8-cec4-5581-8d42-77672674c811 |  | note | Resp - SE
label | 90081ab3-f823-5440-b3f5-fde3a190d07c |  | note | RJE Key - S
checkpoint-group |  |  | section | 3.0 Installation of Drainage Pipe
checkpoint-status |  |  | checkpoint | 3.1 - Pipe Installation
label | 34e97bbe-8f8f-5854-a4f6-c82ea9c0d64c |  | note | Ref docs - AS 3500
label | 740f4b07-cd1b-5260-9ca5-056e57d3178a |  | note | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | 3a227341-058e-5fa9-aa2b-ca7d6da27e03 |  | note | • Pipes shall be bedded evenly to ensure sockets to not bear on the base of the trench
label | 4184ef72-d258-5190-951e-707c73e0fb92 |  | note | • Pipe laying shall commence at upstream end at downstream end of the run. All pipes shall be laid with sockets pointing upstream.
label | 2246b8f9-4393-5a65-8442-d0bf53c44e38 |  | note | • Lay at min grade 1:100
label | 760c5cab-740e-51dc-8192-6c2b523ac51d |  | note | • Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
label | 6cea8d57-39e6-5ac8-a139-ac666397d6f8 |  | note | • Keep trench width & depth to that required by the service & its bedding method.
button | f7184e7f-1fa0-5dff-af01-aa15ce5cfc66 |  | button | Acceptance | Yes,No,N/A
label | c5f43417-e2c0-577c-a970-9d5725d1d28b |  | note | Key - W
label | 89427b63-af68-58cc-a7ef-966cb46c356e |  | note | Resp - SE
label | be3bb390-b6d8-5f22-9708-c6a47f602965 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 3.2 - Pipe Grade
label | b1348273-3056-58e8-bd2e-d82dbb97f78c |  | note | Ref docs - IFC Drawings
label | 010ed532-1557-5c2f-b022-989300a88ea5 |  | note | Acceptance criteria - Install piping in straight lines at uniform grades without sags.
button | 5adaca6e-ad1b-50a2-b189-cf868beec39f |  | button | Acceptance | Yes,No,N/A
label | 6b20ab11-117c-5fc6-94c1-83768897516d |  | note | Key - W
label | 37fb2dfd-9a9f-50ab-9264-f70521550f63 |  | note | Resp - SE
label | b4b2d19b-69ec-55eb-9de5-13a7222334d3 |  | note | RJE Key - S
label | 2e0cca73-ec07-58d8-a985-afa6c58c6275 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 3ac7c9b1-be35-57d5-87c4-4ab623b9ea31 |  | tickbox | CCTV Report
checkpoint-status |  |  | checkpoint | 3.3 - Tolerances
label | d7549f23-d61d-5eb9-ac4a-eebfe92fa707 |  | note | Acceptance criteria - Unless otherwise specified, tolerances as follows:
label | 09204dec-28f9-56a7-9268-6df87f995b52 |  | note | • Offset of entry pits required to match lines of kerbs or barriers ±20mm
label | f44b2101-2720-5eb9-ab2e-2bbae135a428 |  | note | • Plan location of pits other than offsets to kerb lines or barriers ±100mm
label | 276b8ac4-b7a5-5ea1-9aa2-b3c9c2f2d9ca |  | note | • Invert level of pipes at pits ±50mm
label | 73b679d0-45ea-59c8-8726-c1183a65676d |  | note | • Departure from design grade of pipe runs ±10mm in 10m provided minimum grade is not less than 1:250
button | 6f9d6691-5ab9-5c0b-9252-7f6c0da0bf88 |  | button | Acceptance | Yes,No,N/A
label | 9f7897aa-92ed-5fcc-8a3a-5220c9925df3 |  | note | Key - R
label | 1e9bd445-e9cf-5fc3-9b43-965de9cb1c3b |  | note | Resp - SE
label | d0a45e34-3dd7-50fd-8f1e-da44aa52be11 |  | note | RJE Key - S
label | b76191fd-e687-5ce8-84c2-4557f59969d2 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 7aa1c203-bffb-5a9e-9ef8-01234138bea9 |  | tickbox | As-Built
checkpoint-status |  |  | checkpoint | 3.4 - Pipe Fittings, Supports & Fixings
label | 45b6d54a-cec9-5dc3-a453-305bf80383d9 |  | note | Ref docs - AS3500
label | 511cc929-fa97-5a12-92aa-e432287c1456 |  | note | Acceptance criteria - Provide all bends, junctions, inspection openings and other fittings as necessary for the completion of all systems.
button | 5cac9259-3999-500c-9994-0475ff5174e7 |  | button | Acceptance | Yes,No,N/A
label | fab15048-1b21-5076-b621-83cc29a176de |  | note | Key - H
label | 1bbfe98b-44df-5cf0-9b37-dafcb0992576 |  | note | Resp - SE
label | 47361722-fde8-5f56-a8f8-19efc678234c |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 3.5 - Pit Install
label | 85ce6b89-cf08-505c-b99e-eabbe8af27e8 |  | note | Ref docs - AS3500 IFC Drawings
label | 7afd076e-8ff8-562f-a5a9-58fc957d7cb6 |  | note | Acceptance criteria - Pits are to be constructed in accordance with project specifications, with internal surfaces and exposed surfaces finished smooth & true. All pipe break-ins are to be made neat and finished smooth without gaps/cavities.
button | 5f47c107-0139-5cc7-bf3e-9e4f7087d57b |  | button | Acceptance | Yes,No,N/A
label | 7f2d6afd-2487-5369-bf85-cbdbf3c51118 |  | note | Key - W
label | 36631dd3-2e7b-5bcc-873e-f793c28237cb |  | note | Resp - SE
label | 65d6874f-de97-5bbe-990a-56af892aa979 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 3.6 - Survey of Installed Services
label | c38b188d-3299-55d0-b897-fe55ac03c461 |  | note | Acceptance criteria - Accurately record the routes of underground cables and pipes before backfilling. Include on the record drawings.
button | b723f1f2-3b76-5ca6-8706-e039c920602f |  | button | Acceptance | Yes,No,N/A
label | a9856a9b-9a21-5e9f-9784-67d00aafaaf6 |  | note | Key - R
label | 680ddd35-40d3-5f22-8e54-18c87f489fa2 |  | note | Resp - SE
label | 65e5a25b-2971-54e3-9d43-bdcd31b5779a |  | note | RJE Key - S
checkpoint-group |  |  | section | 4.0 Backfill
checkpoint-status |  |  | checkpoint | 4.1 - Backfill Material
label | 7adc9fb3-ae8b-5b89-801d-13b8e42000f5 |  | note | Ref docs - IFC Drawings
label | b69f8cf3-1135-5be0-83de-8dee35f03ebb |  | note | Acceptance criteria - After pipes & fittings have been set in the correct position, jointed, and tested, further bedding material shall be used to fill all recesses below sockets, and bottoms of trenches.
button | 2cb19dd7-cebb-5684-9de3-4749cf48943d |  | button | Acceptance | Yes,No,N/A
label | e11744b1-d806-5bee-ae3c-3e6480b04f08 |  | note | Key - W
label | 9ef708a9-53ee-59b7-8923-895c4c6cde5c |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.2 - Layer Thickness
label | a71c75af-0389-53ea-a107-bf0fa04ee531 |  | note | Ref docs - IFC Drawings
label | 790c7ebb-4492-5e05-8594-a1b40d66eac1 |  | note | Acceptance criteria - Backfill material must be placed and compacted in maximum 150mm layers.
label | 28bd081a-d042-50a9-a15b-f2a3587fbff3 |  | note | • Backfill trenches as soon as possible after satisfactory testing & approval of laid and bedded service.
button | 3720e05a-6b72-59ff-a4de-adb85e830650 |  | button | Acceptance | Yes,No,N/A
label | d53d6af3-a20e-5e27-901c-477121497305 |  | note | Key - W
label | e8a17355-a73f-5dbc-9e82-65ef8e363fbf |  | note | Resp - SE
label | b9d5e4be-ad16-567f-88ea-413057cb6535 |  | note | RJE Key - S
checkpoint-group |  |  | section | 5.0 Conformance Check
checkpoint-status |  |  | checkpoint | 5.1 - Clean & Finish
label | c97bb797-4481-510e-bbe4-aff6b428ec2a |  | note | Ref docs - IFC Drawings
label | cd7ec6a6-eaa2-539a-bc36-5336994328fd |  | note | Acceptance criteria - On completion, each drainage line shall be free from dirt, debris, or other impediments.
button | f8f60be0-c323-5c46-a54a-6ac03f60c894 |  | button | Acceptance | Yes,No,N/A
label | abbcf80c-0048-576a-a506-9a0103f6fb45 |  | note | Resp - SE
label | 9dba6916-4f05-52d6-9499-734dfb5297f9 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 37b00dc9-bbce-5ab6-a16f-83f9b4ef9d34 |  | tickbox | CCTV Report
checkpoint-status |  |  | checkpoint | 5.2 - Visual Inspection
label | 29c01485-6fca-51bd-b002-3ac38970fa99 |  | note | Acceptance criteria - Do not cover or conceal work until it has been tested. Leave pipe joints exposed to enable witness testing.
button | 67962751-932c-5529-8fc8-22fbbe40e982 |  | button | Acceptance | Yes,No,N/A
label | ecafd4b6-93dd-52e3-8bd4-8f083bb6bf99 |  | note | Key - H
label | 6192e688-fdc9-5d61-85d1-bc45807b96f0 |  | note | Resp - SE
checklist-sectioned |  |  | checklist | CC0394 - ITP-001 - Sediment Control | itp |  |  |  | Yes | CC0394 - ITP-001 - Sediment Control REV0 | 9ad8e190-1c9b-456d-9dd2-f3fc6d871ac8
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 5117c05a-6360-5e38-98bb-a68a4e13d42d |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | c2f0a65a-2cfa-5b28-9801-79aa246cfaf4 |  | textbox | Lot opened date:
text | 6f0010f8-9780-5aa1-9cda-863dbdc1e769 |  | textbox | Lot opened by:
text | 4f68cc96-3b1e-5623-932e-948163e38f88 |  | textbox | Date lot closed:
button | 0d2edc54-1a14-5289-bd42-e00327c632ab |  | button | NCR raised? | Yes, No
text | dcadbe9c-6141-5f27-8270-84aad612cfb1 |  | textbox | NCR Raised Date:
button | 83823997-4585-565a-9475-c7682087d844 |  | button | NCR closed? | Yes, No
text | 707695db-be09-59ae-a559-1228360d118a |  | textbox | NCR Closed Date:
text | 93917143-0e8d-5e10-985a-e5a5cbec2bfd |  | textbox | NCR Number:
text | d9e66458-a2d8-5e86-8401-a438176c3e04 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Pre-start activities
checkpoint-status |  |  | checkpoint | 1.1 - Safety
label | f9bca9f9-7118-5a51-a27e-e35417654545 |  | note | Ensure that the following items have been actioned:
label | 1fd6fe21-5f49-589e-9503-875f7c938b50 |  | note | – SWMS if applicable
label | f8998f38-2cf4-559d-be33-7dc5e6425f25 |  | note | – Plant Pre-start Inspection
label | 6cfaa091-6367-5052-924a-98bb03ecc920 |  | note | – Service locations identified
label | f6527eb9-bed7-56dd-b94e-4f3c08e45ac9 |  | note | – Traffic Management Plans (if req’d)
label | e89df8c0-9490-59b8-b879-48bc7f498366 |  | note | – All staff inducted
label | 12319051-2617-517f-8cea-ed46cd5fc532 |  | note | Ref docs - SMP
label | dfe0e5ae-7fde-5c70-97c6-07a7cb5335e6 |  | note | Acceptance criteria - SWMS submitted reviewed and accepted if required.
label | 6523fdac-ac9d-5c0e-8293-cb210dd29e7a |  | note | • Personnel inducted to RJE requirements.
label | 339e8748-27b5-58f6-b25d-81ac43417c12 |  | note | • Plant inspections completed and entered.
label | 56aab71f-cc42-5a01-9c6c-6749308a7835 |  | note | • Pre-work briefings completed.
label | f91e950a-c9b3-57d3-ab49-110ce5edf75c |  | note | • Service Diagrams available and services located.
label | 264da3d5-4d18-5405-930a-f9d245e7d9b8 |  | note | Freq - Once (Pre-Start)
label | fff8e3fa-afb8-5207-8904-415fef679b5a |  | note | Key - H
label | ae58cf2d-3d22-56fe-8dd3-35ba07334028 |  | note | Resp - SS
label | e05a528d-ef3b-5a3a-968e-824c5a350e12 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Excavation Permit
label | cfd1fc89-6da9-54ce-b796-db228c377395 |  | note | Ref docs - SMP
label | 8713dacb-9f75-5278-9801-0cb17a5d5cfe |  | note | Acceptance criteria - All identified underground services marked and potholed to confirm location and depth. No machine excavation within 1m of underground services. Permit available and signed.
label | d84f2043-9d4f-5208-b91d-f821af09d311 |  | note | Freq - Prior to start of works
label | 9e9b6238-c175-5dcb-864f-22e50210c3bb |  | note | Key - H
label | 811a982b-7297-580b-9907-5b575645dbac |  | note | Resp - SS
label | 4492eb3b-eccb-5d96-a609-3195531732a9 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.3 - Check Survey Set-out
label | ea688e28-f374-544f-a41e-1186e06a889f |  | note | Ref docs - Drawing: 5668-122-1010
label | bd82d330-a493-5aeb-a061-5a0437bd3194 |  | note | Acceptance criteria - Survey Setout extend of works
label | 39f8fbba-a75c-55e3-861b-46cf82636815 |  | note | Freq - Prior to start of Works
label | f8f37293-4526-5ece-a9c3-4b861be263a6 |  | note | Key - H
label | 42760802-fdda-5b00-aeeb-fd11f4f12c07 |  | note | Resp - SV, SS
label | db4c33db-adce-51f3-814b-3bfcad673fef |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Material Specifications Checked and Conforming
label | 39254633-a66e-5d54-91b4-ad427af0cc90 |  | note | Ref docs - RFI Approval
label | 98e79747-02b4-5773-aacb-38474c217162 |  | note | Acceptance criteria - RJE approval of sediment fence material
label | 26685af7-cc14-5d30-b894-9c3a7a121936 |  | note | Freq - Prior to start of Works
label | 502b9014-4c5d-5b9e-a7f3-7d56f2cd684e |  | note | Key - H
label | fa9c4bb1-2514-5d32-8973-fe82cdb60cd0 |  | note | Resp - SE
label | a1e98db5-4da9-518b-a988-cccd29fd66c3 |  | note | RJE Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Install works
checkpoint-status |  |  | checkpoint | 2.1 - Sediment Fence Install
label | dcb71f1f-9bfd-54d3-82a1-23361b2c667b |  | note | Ref docs - Drawing: 5668-122-1010
label | 84763a54-c76f-520b-9a18-992c974e61c1 |  | note | Acceptance criteria - Correct fence material is onsite, Stakes installed at 2000mm spacing, silt fence buried at least 200mm into soil, Fence secured to stakes using appropriate fixtures.
label | 7b7b76fe-cc5c-50cf-8d09-08631b3fcb5d |  | note | Freq - On delivery and installation
label | 0f04efa5-01dc-5f93-9615-fcdfd83a4976 |  | note | Key - H
label | 188bbb49-efa8-534b-ba86-676815ec4c37 |  | note | Resp - SS
label | b0f8977a-4903-5ebc-9c05-bb722801ac6e |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Temporary swale & earth bund construction
label | 2c405fa0-70fe-591b-ba2d-c38a99d8158b |  | note | Ref docs - Drawing: 5668-122-1010
label | f3d43bb8-33df-5dca-abde-af87d2331b71 |  | note | Acceptance criteria - Construction conforms with IFC drawings unless approved otherwise.
label | ed725695-435d-5c44-8371-e84468f28e42 |  | note | Freq - On delivery and installation
label | bd013305-b051-5294-99e5-0fc6d27e06fb |  | note | Key - S
label | 97b03830-1850-5686-bc29-b8ba4d5d856b |  | note | Resp - SS, SE
label | 3dfd7a1d-f28c-57d0-9f3d-ac0df3536bb7 |  | note | RJE Key - S
checkpoint-group |  |  | section | 3.0 Conformance check
checkpoint-status |  |  | checkpoint | 3.1 - Carry out corrections and clean-up
label | 25dc2631-36c6-5e24-b636-f298f635293e |  | note | Acceptance criteria - Area clear of debris, silt fence is sturdy and intact, earth bund and swale sediment controls working as intended – efficiently carries water where required, prevents silt run-off and erosion.
label | 166c06b5-f27b-5d6c-81e7-93d51ac92504 |  | note | Freq - Visual Inspection once complete
label | 9d1b80c0-7043-53b3-9a86-805854b39b94 |  | note | Key - W
label | 3aa78827-30e5-56b7-86e8-6cc2bf2362cc |  | note | Resp - CR
label | feb250f7-ca92-57e9-9b12-61bca9dbab25 |  | note | RJE Key - W
checklist-sectioned |  |  | checklist | CC0394 - ITP-003 - Bulk Earthworks | itp |  |  |  | Yes | CC0394 - ITP-003 - Bulk Earthworks REV1 | 9db0e0ed-b921-49f6-befa-a7f3e727e1b1
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | ef8a81b7-c466-58cb-b6d3-c97e0fd5c873 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 1e78d029-52c3-553d-bfbf-8727f9ac1572 |  | textbox | Lot opened date:
text | 9e83f881-22b8-5c6d-b340-65d7658f1a45 |  | textbox | Lot opened by:
text | 31531237-3df0-5f73-a71a-c23206a1b7af |  | textbox | Date lot closed:
button | cddffddd-0aa2-5467-bf17-de39a6c4dd6c |  | button | NCR raised? | Yes, No
text | e5458257-55be-5b5a-b2a5-fa7c6540d26d |  | textbox | NCR Raised Date:
button | 1deb4272-5e1c-5209-9995-f55dc130bfab |  | button | NCR closed? | Yes, No
text | c7a458f4-b1ea-5e22-8122-7267f54c605a |  | textbox | NCR Closed Date:
text | 694202e3-ed62-5d8b-aaae-7f1128e8c673 |  | textbox | NCR Number:
text | 98c315e4-41d9-5e74-900f-026a2721f64e |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Determine lot size
label | fc1776f4-97b9-5aed-be3b-70e1a8668475 |  | note | Acceptance criteria - What is the lot size?
text | a332a5f3-be05-584f-a2d5-d4b141f0942a |  | textbox | Acceptance |  |  | m2
checkpoint-status |  |  | checkpoint | 1.2 - Survey set-out
label | cdb32dae-1109-5656-aa6a-3ac7459b7961 |  | note | Ref docs - Construction drawings
label | a7c8c96c-a03f-563f-be3b-8e3e5db9a371 |  | note | Acceptance criteria - Is the most current survey file what the team is working to and has the work area been set out for line and level?
button | 60be2e86-9225-5ca7-aa78-98326324035b |  | button | Acceptance | Yes,No,N/A
label | 1392c088-698f-581f-87f9-d0c3dea68b60 |  | note | Key - W
label | d1854ad4-a0db-5747-887d-5628716fe5c5 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.3 - Water management
label | 14ce12a9-ccf7-5b86-bd42-51313415de99 |  | note | Acceptance criteria - Where necessary, have batters been rounded and catch drains constructed to allow for potential surface runoff during the course of excavation?
button | 51f6a97a-8838-5c2c-8253-b674c5b71676 |  | button | Acceptance | Yes,No,N/A
label | 7ffdb910-8812-51b8-92d7-c5e737ce451c |  | note | Key - S
label | fa6e6e2d-70ca-5488-a8ea-373e5aec3ad5 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 1.4 - Clearing
label | d80c516b-9cda-53dc-bb62-e953fbae7ce9 |  | note | Ref docs - CC0394 - ITP-002
label | f3351c9a-4604-536d-a5c8-0a375aeb3649 |  | note | Acceptance criteria - Has the area been cleared and grubbed in accordance with ITP-002?
button | 838b2779-7af8-5866-80ea-0c545879d46e |  | button | Acceptance | Yes,No,N/A
label | 3a190aaa-b6ac-5a44-bbf1-3a5b9a51c68c |  | note | Key - H
label | 09f0d6de-6fa5-58a2-b9a9-465002888fe3 |  | note | RJE Key - S
label | 7620ce3b-089c-587a-9426-512202a8c5b4 |  | note | Is the area in cut / fill / both?
label | 67e66035-ba9a-5769-8427-566392da6338 |  | note | If in cut proceed to step 2.0 and strike out section 3.0.
label | 566c0640-5c5c-53f0-94c7-426a39614305 |  | note | If in fill please strike out section 2.0 and proceed to section 3.0
label | d9729b46-ba2f-5390-b421-cdead975d687 |  | note | If in both proceed to step 2.0 as well as section 3.0
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Bulk earthworks – cut
checkpoint-status |  |  | checkpoint | 2.1 - Excavation material classification
label | 7fc37d66-2014-56d4-b84f-8e42cf6f851d |  | note | Acceptance criteria - Has the material being excavated been inspected with category agreed upon by Superintendent? Tick category below:
boolean | dc446354-914a-51f4-b688-d9bb2b1df894 |  | tickbox | Topsoil
boolean | be4b8bb1-aa0b-5193-814c-d00165909bab |  | tickbox | Unsuitable material
boolean | 97d8c1d7-6360-53ed-96ed-0b876e1e69b2 |  | tickbox | Fill material
boolean | d3ec0687-39cb-5df8-8650-51c5035a7d7d |  | tickbox | Other
text | 0bd8787b-a61d-5c73-be4c-d8120c10d077 |  | textbox | Other:
button | dfe69962-5135-5555-ad10-072a22c45d1a |  | button | Acceptance | Yes,No,N/A
label | 2d0d0d46-efd1-5a9d-a0b5-d658369c94c4 |  | note | Key - H
label | 25254f9c-f6be-58ff-bddf-90fce818370b |  | note | RJE Key - W
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.2 - Stockpile
label | 2ee7bd82-d035-50fc-a2ba-b8b6beaa6410 |  | note | Acceptance criteria - Has the stockpile location been approved by RJE?
button | a12c0ac6-d331-5fd2-8859-3a5b1c5bbefa |  | button | Acceptance | Yes,No,N/A
label | 5b8a9c17-25f9-5487-bba3-cfe25b820ef3 |  | note | Key - H
label | 6e477f30-8cea-53d8-8029-35ed6c8744db |  | note | RJE Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Subgrade preparation
label | 13727532-abfb-5194-b458-aa8f3a11f3fe |  | note | Ref docs - Construction Drawings
label | 952ff7b3-100f-511e-a630-77b4a0bfe024 |  | note | Acceptance criteria - Has the cut surface been trimmed to an even surface free from lose material? Have surface levels been checked to avoid over excavation?
button | a16f62d9-7c8c-5523-bcce-cd4cb82ac90d |  | button | Acceptance | Yes,No,N/A
label | 72aa1204-ed74-5ef3-a5dd-2f3db51c9e3f |  | note | Key - S
label | 585f8196-2df6-518f-bda2-a825d323f086 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 2.4 - Lime mix
label | d5ca6918-61ae-5d23-9b4d-9a403c8abc26 |  | note | Ref docs - Construction Drawings
label | 29e202d4-6014-50b2-b796-ff48f0a11b8e |  | note | Acceptance criteria - Has lime demand testing been completed and submitted?
button | c04a531f-139b-5319-8715-7f17d7572c7e |  | button | Acceptance | Yes,No,N/A
label | 331d9381-79c7-56ba-b8c8-87f474efdd5b |  | note | Key - H
label | 1ac89d48-617d-5d24-a611-f35697d9b96b |  | note | RJE Key - H
boolean | f584bd11-fb09-516f-9f48-d9d8d6e0da9d |  | tickbox | Remarks / Record - Test report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Lime stabilisation
label | fecfb4da-0314-5e5d-aa81-6942a154b1ef |  | note | Ref docs - Construction Drawings
label | 710f75ab-7030-596f-a849-babb4faf3c0b |  | note | Acceptance criteria - Has the prepared subgrade been lime stabilised as per the IFC design?
button | 0d1ec14f-1ede-59bc-bc21-95bda40cec83 |  | button | Acceptance | Yes,No,N/A
label | 32e5ecb1-9e3e-56c0-96ff-938a3a8ced9a |  | note | Key - S
label | 50e67e08-bf23-58b5-a87b-a054c91373a1 |  | note | RJE Key - W
checkpoint-status |  |  | checkpoint | 2.6 - Compaction
label | 4897c588-40fc-5996-a1e7-60c6d2e6a1e1 |  | note | Acceptance criteria - Compaction Scale: minimum 3 tests per lot, or 1 test per 1000m2 Has the stabilised subgrade been adequately compacted achieving 98% SMDD / 95% MMDD (in-situ materials or subgrade preparation), or 75% density index for the in-situ and fill materials. Using a nuclear density gauge. Is the subgrade material with 2% of the optimum moisture content. Minimum 3% CBR achieved?
button | 63123ca7-3962-5fce-a0d5-f2e2cb782067 |  | button | Acceptance | Yes,No,N/A
label | 7c93a2a3-29a6-54bb-ac4e-c52d7bb7c850 |  | note | Key - W
label | 01a9ae6b-39ea-55e6-a923-28e986a7fbdc |  | note | RJE Key - S
boolean | 2c3ba25a-8512-5653-9f6e-ed8f40f49ce6 |  | tickbox | Remarks / Record - Test report
checkpoint-status |  |  | checkpoint | 2.7 - Test Rolling
label | 6ed1d87c-5a95-5d6e-b0ce-1f48085b6506 |  | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation or springing? List Attendees:
button | 81e7450b-af97-5a6b-9218-34d766be610a |  | button | Acceptance | Yes,No,N/A
label | 80077dcb-f67a-572e-b8d8-359a5a9a01d1 |  | note | If ‘no’ please see below.
label | 5dc64e83-5162-55f7-81e4-c6831505be8a |  | note | If ‘yes’ please proceed
label | 56224b35-98eb-57a3-9600-2791a7d1fccd |  | note | Key - H
label | 3c54418c-7cce-5a4b-b51d-f5573789b4e7 |  | note | RJE Key - H
boolean | 210e8b2d-a0d4-5f17-91f9-a2cbcf37e785 |  | tickbox | Remarks / Record - Proof Roll Inspection Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Identification of soft wet or unstable material
label | 5055adda-a08b-5452-a40a-2076d23f050e |  | note | Acceptance criteria - What quantity of soft, wet or unstable material is present?
label | 6f788a9a-c760-5f57-8841-252321965567 |  | note | Acceptance
text | 1f1be11f-6514-5e7b-85f0-eda16823150c |  | textbox |  |  |  | m2
text | 32e4e5b5-c225-5d87-bac7-1598db6537d9 |  | textbox |  |  |  | m3
checkpoint-status |  |  | checkpoint | Treatment of unsuitable material
label | 7f9faacb-b392-5cee-903b-018103df64a5 |  | note | Acceptance criteria - Has rectification process been submitted to RJE for review? What was the rectification process used?
button | 7427e4ee-6ce4-5bd7-91f7-c20825500d4c |  | button | Acceptance | Yes,No,N/A
checkpoint-group |  |  | section | 3.0 Bulk earthworks - fill
checkpoint-status |  |  | checkpoint | 3.1 - Fill material classification
label | 4d1dfc9d-aba1-5ed6-a4de-0d2bf5cea4eb |  | note | Acceptance criteria - Has the material to be used as fill been approved for use?
button | 687f5217-9fd9-5498-ba9d-1a4e5962a2fa |  | button | Acceptance | Yes,No,N/A
label | 1838072a-34cb-5a8d-97b3-2818e1eee6b2 |  | note | Key - H
label | 45d97e70-4dcb-518c-b680-b2532194ab24 |  | note | RJE Key - S
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.2 - Stripped surface - test rolling (If applicable)
label | 2a83c831-029e-5ef2-b0c9-162e797332ea |  | note | Acceptance criteria - Does the stripped surface to be filled withstand test rolling without visible deformation or springing? List Attendees:
button | 831a0745-7e9d-5a7c-b165-4b4ecb248b63 |  | button | Acceptance | Yes,No,N/A
label | 9620c6c6-53fe-59cb-b111-cdb8a3c83707 |  | note | Key - H
label | 9aa7caeb-2cb1-5f74-b0a1-87c5c93532f9 |  | note | RJE Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Identification of soft wet or unstable material
label | f8ab0d09-8ce4-5877-b726-bcc88e79454d |  | note | Acceptance criteria - What quantity of soft, wet or unstable material is present?
label | 0c59fadd-94ba-5253-b2ca-c938168f0f46 |  | note | Acceptance
text | 65b44176-e1e7-5574-8a5a-4a426a31daa0 |  | textbox |  |  |  | m2
text | f8e1ab1a-cda7-5372-a67e-b4bbb6fb3d20 |  | textbox |  |  |  | m3
checkpoint-status |  |  | checkpoint | Treatment of unsuitable material
label | f7226176-decd-527c-a5e2-70da2e6be1cd |  | note | Acceptance criteria - What rectification process is to be undertaken?
checkpoint-status |  |  | checkpoint | 3.3 - Preparation of surface
label | fade68ae-cd3d-588a-8ae2-e80971f6492a |  | note | Acceptance criteria - Has adequate water been added to the stripped surface to ensure adhesion to the next layer?
button | 3954cd61-ede7-5bcc-af5e-83185f76c58e |  | button | Acceptance | Yes,No,N/A
label | 81fcdf5f-16e6-5839-a259-0d45dc2d800a |  | note | Key - S
label | 7b6a2693-ae80-5da0-bbf0-62aa3e75a67c |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 3.4 - Fill Placement
label | 5a96caf7-e44a-53fd-b679-cf49cf1005e2 |  | note | Acceptance criteria - Has fill been placed in maximum 300mm and minimum 100mm compacted layer thickness?
button | 86a01478-083b-5f3c-9dd0-bd53da326412 |  | button | Acceptance | Yes,No,N/A
label | 1a1e41b6-5309-52a0-b160-502b7a18d4ed |  | note | Key - S
label | 696474c1-211c-5af2-82bf-abf18ca8c325 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 3.5 - Moisture
label | bbcd66e9-be56-59ed-86d0-87747cf542cc |  | note | Acceptance criteria - Has the material maintained at optimum moisture content (within 2% of optimum moisture), with additional water being added if required during compaction?
button | 4815d846-8b8e-5cad-bbf4-20447982f8b5 |  | button | Acceptance | Yes,No,N/A
label | 67a7e1a8-f2c1-5227-a7b1-8d586b308cf9 |  | note | Key - S
label | 4b24cfb7-dcef-5de8-8559-467225d52f33 |  | note | RJE Key - S
checkpoint-status |  |  | checkpoint | 3.6 - Lime mix
label | 2b05ff09-be0a-59a9-8a51-b485cd6dff1c |  | note | Ref docs - Construction Drawings
label | 9b4af993-8760-595c-8b96-b2f77357a323 |  | note | Acceptance criteria - Has mix demand testing been completed and submitted?
button | 4c703000-eee2-57a3-8951-a9c93f766dc8 |  | button | Acceptance | Yes,No,N/A
label | f8fb680c-8d84-51fd-9aae-aabf7fa684d2 |  | note | Key - H
label | 5ec9c24a-186a-5d80-8b12-7e39a2f2b2f4 |  | note | RJE Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.7 - Lime stabilisation
label | 57c5f777-fab9-504d-b7a0-c3de4ca076a3 |  | note | Ref docs - Construction Drawings
label | 6d18281c-702b-543a-8645-b1099117457f |  | note | Acceptance criteria - Has the prepared subgrade been lime stabilised as per the IFC design?
button | a6ce94e6-4fe2-5d50-898c-1e1153d63f9c |  | button | Acceptance | Yes,No,N/A
label | 71f19be9-508e-5dd3-aa61-5db3b3642f80 |  | note | Key - S
label | e82e653d-31ba-5e02-b8cf-9e13fb7811f0 |  | note | RJE Key - W
checkpoint-status |  |  | checkpoint | 3.8 - Compaction
label | f0d7f7f9-a105-53f0-84a4-1e8ea653edd7 |  | note | Acceptance criteria - Compaction Scale: minimum 3 tests per lot, or 1 test per 1000m2 Has the stabilised subgrade been adequately compacted achieving 98% SMDD / 95% MMDD (in-situ materials or subgrade preparation), or 75% density index for the in-situ and fill materials. Using a nuclear density gauge. Is the subgrade material with 2% of the optimum moisture content. Minimum 3% CBR achieved?
button | 6470bb79-a68f-5189-9895-1c98d97659b0 |  | button | Acceptance | Yes,No,N/A
label | aa477d23-d040-5926-8ea1-988b725624a1 |  | note | Key - W
label | 5a943cda-67e3-5ce5-96ec-a870bca9be45 |  | note | RJE Key - S
boolean | 666876e2-c768-5274-9b16-ccc54800c74b |  | tickbox | Remarks / Record - Test reports
checkpoint-status |  |  | checkpoint | 3.9 - Test Rolling
label | 750dcbc4-f322-5c68-8333-c5f996e1269c |  | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation or springing? List Attendees:
button | 223bf63c-1f50-5955-995f-3d32bd8e93f2 |  | button | Acceptance | Yes,No,N/A
label | bd38bdd1-8869-5e6f-a79a-aefd0f5c3c8a |  | note | Key - H
label | 7946696d-66d6-59e2-9b73-5fe6108fbc6a |  | note | RJE Key - H
boolean | 1ad069eb-f7c1-5ca0-9149-084e3277fd4a |  | tickbox | Remarks / Record - Proof Roll Inspection Checklist
button | c7218abb-aebe-55a9-9c16-a76e6045e446 |  | button | Acceptance | Yes,No,N/A
label | d6d35184-1208-5823-b969-50bfb543e760 |  | note | If ‘no’ please see below.
label | 2fe472c1-6e34-540a-9245-96e7b489fb55 |  | note | If ‘yes’ please proceed
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | Identification of soft wet or unstable material
label | 7b32894e-5ed0-58a2-8aac-5b1712646dee |  | note | Acceptance criteria - What quantity of soft, wet or unstable material is present?
button | 113b5127-4329-5eef-ba5a-798ad9c4ba2d |  | button | Acceptance | Yes,No,N/A
checkpoint-status |  |  | checkpoint | Treatment of unsuitable material
label | a2858573-c497-58ee-a553-a85e66a31392 |  | note | Acceptance criteria - Has rectification process been submitted to RJE for Review? What was the rectification process used?
button | f2777361-8ecf-58d2-94bb-b9124a0bbaa7 |  | button | Acceptance | Yes,No,N/A
checkpoint-group |  |  | section | 4.0 Conformance check
checkpoint-status |  |  | checkpoint | 4.1 - Width and alignment
label | 906f6dde-d43d-5441-96ad-c793946422d8 |  | note | Acceptance criteria - Has the pavement been constructed at the correct width and alignment as detailed in the construction drawings?
button | 22a324f2-c1b6-5061-b5bf-1f890aa9dfbf |  | button | Acceptance | Yes,No,N/A
label | a7ffe3b1-2520-562d-a5e1-f3fa30a15cb1 |  | note | Key - H
label | 7cecaf1f-f4d2-5c90-b85b-d80f09d343ae |  | note | RJE Key - S
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Subgrade level and shape
label | 64413b86-6520-560d-96bd-b41beb5a999f |  | note | Acceptance criteria - Has the prepared subgrade been surveyed in accordance with and verifying specified requirements? Is the subgrade within +/- 20mm of design surface.
button | 686ba9a7-3f95-5f63-879c-4137efe91d02 |  | button | Acceptance | Yes,No,N/A
label | 98cb9350-4e7f-585d-ae05-b11ea3c01fe7 |  | note | Key - H
label | 5c624972-7265-54ec-b8ef-2540e3e055b5 |  | note | RJE Key - S
boolean | 5dfa4b92-ea77-57e2-8638-e3145b35bfb5 |  | tickbox | Remarks / Record - As built report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | CC0394 - ITP-005 - Crushed Rock Pavement Construction | itp |  |  |  | Yes | CC0394 - ITP-005 - Crushed Rock Pavement Construction REV0 | a0980a32-1eec-4a03-b12e-496e72e0dce7
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 35887d7c-2def-5fba-ad7c-81311119294a |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 71fb8346-dfa2-5425-a684-73e52e0597f2 |  | textbox | Lot opened date:
text | 4c75dafa-a8bb-52c1-b3b5-e89501940f84 |  | textbox | Lot opened by:
text | a543ae91-9503-5fd6-aa72-e0963eabf4e5 |  | textbox | Date lot closed:
button | cc7df93d-5a22-51dc-81ea-4746b45d15c9 |  | button | NCR raised? | Yes, No
text | 09d16c16-7cba-58a9-a538-1b306154c349 |  | textbox | NCR Raised Date:
button | f673fb5b-f414-5a20-a46c-e92640782e81 |  | button | NCR closed? | Yes, No
text | c5d22759-8447-587e-bbeb-b29ac3b60acb |  | textbox | NCR Closed Date:
text | 032d3bc8-e0a2-59be-b805-08436b9f5e51 |  | textbox | NCR Number:
text | 0c32f92d-79e8-523b-88a0-746a583d250b |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0
checkpoint-status |  |  | checkpoint | 1.1 - Determine Lot Size
label | cdf6cd5d-55eb-5d54-a025-a48114e5f52e |  | note | Acceptance criteria - What is the lot size?
text | 709b9433-edf6-5bc5-8f3c-ad4b1242f6b4 |  | textbox | Acceptance |  |  | m2
label | 94195851-fa51-5d80-8569-704d1a9aeec2 |  | note | • Maximum lot size = See pre-approved lot maps
label | 44e1c993-9d8a-5513-b4b4-ceb00636875a |  | note | Resp - SE
label | ea3921d0-44e9-5173-b908-a787e74be51b |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 128ec6c1-f3ec-5f36-be31-87fb09ad371a |  | tickbox | Work Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Survey Set-out
label | a665881f-3d33-5655-9cb3-5cd40133189d |  | note | Ref docs - IFC Drawings
label | dbbc7c1d-4abc-572c-bd87-e358835abad3 |  | note | Acceptance criteria - Has the work area been set out for line and level?
button | 695bd86e-12a1-5fc2-ad2e-9831077e3120 |  | button | Acceptance | Yes,No,N/A
label | e85ddfae-5e1e-5649-bb28-220c7671d607 |  | note | Key - W
label | e21fe9bf-c453-5218-9290-163d0005d3fc |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.3 - Material Classification & Source
label | b90b17c5-c938-504b-858f-958b6b3ee56c |  | note | Ref docs - IFC Drawings
label | 008491aa-d615-5d87-9650-3b754c95f04d |  | note | Acceptance criteria - Is the correct material being used?
button | c97ad939-9caf-5273-ad08-fe26fd30cbf1 |  | button | Acceptance | Yes,No,N/A
label | c3baa1a7-7015-529b-af4c-a2b40e103d0a |  | note | Please tick appropriate Box:
boolean | 9df9dd85-f06f-5b17-a78f-3dbf5b734a26 |  | tickbox | Site Won
boolean | aedb946a-847c-5a06-9cf3-18f4ba542d32 |  | tickbox | 20mm Class 2
boolean | f0039bd3-6656-5f7f-b165-4a61f5c89409 |  | tickbox | 20mm Class 3
boolean | 03821815-54e0-5be1-8250-d818f656cca2 |  | tickbox | 20mm Class 4
text | 7e52d1ac-955b-54fb-84e1-38246021e4d5 |  | textbox | Other
label | 7e3cf997-3b70-5f57-a9d5-ed9883e1b1ea |  | note | Key - H
label | 77f1e18b-bd79-5fc2-b275-6763b0c2b116 |  | note | Resp - SE
checkpoint-group |  |  | section | 2.0
checkpoint-status |  |  | checkpoint | 2.1 - Conformance of Previous Layer
label | 990cfbed-91b4-5099-8c00-399b09f93777 |  | note | Ref docs - IFC Drawings
label | d784cbce-dd68-5cb0-a867-d36e6e37a4e1 |  | note | Acceptance criteria - Has the previous layer passed acceptance criteria?
button | 075347a9-5acf-5739-b6d9-9456c77f6b43 |  | button | Acceptance | Yes,No,N/A
label | 32e4286a-589a-53ba-81c1-65ea5d5d577a |  | note | Key - W
label | b204799c-53da-5a6b-b902-90291f80c51d |  | note | Resp - SE
label | 0e74f50a-4504-5654-abef-7576e9ef74c0 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 9a7d7f44-03cc-5c09-b175-e2874035aebe |  | tickbox | Refer to ITP for previous layer
checkpoint-group |  |  | section | 3.0
checkpoint-status |  |  | checkpoint | 3.1 - Placement
label | df57071a-8818-59df-b216-dbe29735040b |  | note | Ref docs - IFC Drawings
label | e300ad99-0943-5e18-9628-ae6d4f3d6f5d |  | note | Acceptance criteria - Has the fill been placed in a maximum compacted layer as outlined below?
label | 8c005233-6347-56ab-8dfe-975b78840386 |  | note | • Maximum Layer Depth: 200mm
button | d1d25de0-4a39-5635-8dc4-2a097ab3eb87 |  | button | Acceptance | Yes,No,N/A
label | a0f967f6-105d-56e7-ba97-8167b419068e |  | note | Key - S
label | cb95eede-bd62-5f34-b56c-ed8f8f4ef53b |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 3.2 - Moisture
label | f62defce-a951-5e05-8388-9bf876649af4 |  | note | Ref docs - IFC Drawings
label | 3d7eeb1e-7241-54a1-8b73-aef8bedff322 |  | note | Acceptance criteria - Has the material maintained at optimum moisture content (>85%), with additional water being added if required during compaction?
button | 71f44e5a-eb29-5b48-8078-502c771c205f |  | button | Acceptance | Yes,No,N/A
label | 2748664d-5688-508c-8baa-4e6c357080d2 |  | note | Key - S
label | f9e98a1c-9c71-5ee0-add7-22351e084e76 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 3.3 - Compaction
label | b00fc3fe-21e6-5b19-816e-5aaea1356c25 |  | note | Ref docs - IFC Drawings Civil Specification
label | f2274e02-2355-59f7-86ed-8fb7c6e90703 |  | note | Acceptance criteria - Has the layer been adequately compacted achieving a mean value density ratio of:
label | ed88c015-6dd2-5be9-bfea-5a759ac3a9b7 |  | note | • Lower Subbase: 98% Std
label | 35b6f60a-0d0c-59a5-a700-36350c61ad7c |  | note | • Upper Subbase: 95% Mod
label | d06ac943-06d6-52ec-a38d-29b16deae856 |  | note | • 3 x tests to be conducted per compacted layer per approved lot map.
button | 17753ba1-49e8-50fd-a569-ebaf1cf0721d |  | button | Acceptance | Yes,No,N/A
label | f4acfd7b-b677-5f20-958f-b2f7d6589f6b |  | note | Key - W
label | 79cd9298-e759-525e-8bff-cc2a31c196fc |  | note | Resp - SE
label | 53d2fdd7-b5ff-543a-b39d-523e12e0ad34 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 5c72fa10-f344-5776-865a-fd6524e4494f |  | tickbox | Compaction test results
checkpoint-status |  |  | checkpoint | 3.4 - Test Rolling
label | 176159a5-664d-53f2-bc86-5d7018d39126 |  | note | Ref docs - IFC Drawings
label | 3ffcfccb-6777-5870-bfc4-9ca01af1fb14 |  | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation of springing?
text | ac6863c8-1510-5283-b878-be18f149d5ef |  | textbox | List attendees:
button | 5f0b76e1-0fc4-524a-af31-e1a95c79abc3 |  | button | Acceptance | Yes,No,N/A
label | 9bf66fd0-0a9e-5133-9f78-822ab8ba767e |  | note | • If ‘no’, please see sections 3.5 and 3.6.
label | 45505644-99ff-54dc-96c2-1750aad7370f |  | note | • If ‘yes’, proceed to section 4.0.
label | c11841a9-4889-557d-bdef-4fbf0c827ebe |  | note | Key - H
label | bd683620-bc2f-597c-aae2-c7f5cdcc6b6b |  | note | Resp - SE
label | e90c588b-0790-554a-bd1a-2318a1a5fc7f |  | note | RJE Key - W
checkpoint-status |  |  | checkpoint | 3.5 - Identification of soft, wet or unstable material
label | 63bfcd15-a562-5ea0-a660-80143c98f6c1 |  | note | Acceptance criteria - What quantity of soft, wet or unstable material is present?
text | 41160065-0334-5464-b4d0-9b7ba190a902 |  | textbox | Acceptance |  |  | m
label | 516247a6-cbee-542a-85ee-b1fda4c75748 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 3.6 - Treatment of unsuitable material
label | 629d7526-07fe-5223-9177-247204687c9e |  | note | Acceptance criteria - Has rectification process been submitted for review?
label | ff9cbc4f-662b-5e0b-a464-300ec55ef1c4 |  | note | • What was the rectification process used?
button | 3280043d-6e76-55cd-a786-e3f75dbed375 |  | button | Acceptance | Yes,No,N/A
text | d9d71016-bff1-546e-b608-7fafb9355468 |  | textbox | Process Used:
label | 97268a5e-91e6-5423-9b45-b279672887e5 |  | note | Resp - SE
checkpoint-group |  |  | section | 4.0
checkpoint-status |  |  | checkpoint | 4.1 - Pavement Finish
label | 5a78741d-ae8c-58d3-8700-cb16d962429c |  | note | Acceptance criteria - Has the pavement course been finished to a smooth and uniform surface?
button | 3f24f1aa-be3f-5b9b-9ab9-d4c492ebeffd |  | button | Acceptance | Yes,No,N/A
label | 54c29084-a42e-59e3-afe2-e1e1f89ecf92 |  | note | Key - W
label | 7980d070-218c-5a91-a466-fcc6f4f5dc89 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.2 - Width & Alignment
label | 0e228b1b-6a7a-5d93-b6dc-2a7934eae341 |  | note | Acceptance criteria - Has the pavement been constructed at the correct width and alignment as detailed in the construction drawings?
button | 933b2f40-855c-54c7-8158-3e528ed2761e |  | button | Acceptance | Yes,No,N/A
label | 0c9d7578-8148-56ba-a84c-aaefcaf5f19e |  | note | Key - W
label | edf75990-3ac6-554e-b973-aa8f24d78c59 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.3 - Surface Level of Pavement Courses
label | 7920e365-1665-5d36-8c2a-a44195d1477f |  | note | Acceptance criteria - Has the prepared layer been surveyed in accordance with and verifying specified requirements?
label | d342d55e-89ec-5518-a7cc-d0aa63252e84 |  | note | All crushed rock layers:
label | c238dd2b-2aa9-5296-942b-c97ee4508041 |  | note | • Mean Range: +10mm to -10mm
button | 232abf2d-3652-5a97-bdef-2064e47368c0 |  | button | Acceptance | Yes,No,N/A
label | bdcfd733-1704-5b64-92b7-e6c4856e9417 |  | note | Key - H
label | c8000161-a8a8-5cab-b69d-dcc3ecdf1e6f |  | note | Resp - SE
label | 448089fd-716a-585f-a338-f9acd7a9df0c |  | note | RJE Key - H
label | 98c472a2-b726-5b8f-ba88-116cc70c45b6 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 94f4d4de-c80b-5608-928f-be913980e2d5 |  | tickbox | As-Built Reports
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | CC0394 - ITP-011 - Kerb | itp |  |  |  | Yes | CC0394 - ITP-011 - Kerb REV0 | aaf6b5a9-e813-421c-ae01-16979d3d97b5
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 218666c2-27ba-502e-9cad-2c3bad812763 |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | 33008354-9542-54d8-8706-063820a39c07 |  | textbox | Lot opened date:
text | 4c5c8cf6-caa0-5fe4-b6bf-4ce7a42d07a6 |  | textbox | Lot opened by:
text | c524888a-664f-582f-ba74-89f01fa78830 |  | textbox | Date lot closed:
button | cb21b33f-809a-51d7-bbf4-3c03ea3076d3 |  | button | NCR raised? | Yes, No
text | 3efbc0e7-3d5c-5e15-a1d8-e9f31764d729 |  | textbox | NCR Raised Date:
button | 0a017936-6f22-5b77-a33e-1e48b0456b1c |  | button | NCR closed? | Yes, No
text | 1372566d-0ac5-5331-9193-b6df4e8ecf3a |  | textbox | NCR Closed Date:
text | 1633ecbd-1986-5a84-8245-2a6f49ec29a2 |  | textbox | NCR Number:
text | a5f20f96-6cd2-5ca3-82f3-dd3c021d3477 |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0
checkpoint-status |  |  | checkpoint | 1.1 - Survey Set-out
label | 0ae6d879-0ae1-5286-81bb-b2a75801a83a |  | note | Ref docs - IFC Drawings
label | 35863936-8604-5e6b-8120-4845cb85e794 |  | note | Acceptance criteria - Prior to the commencement of works, the contractor shall engage a suitably qualified surveyor to set out the works and clearly mark its limits.
button | 36c858ab-3aef-5d22-a709-2119c76a191e |  | button | Acceptance | Yes,No,N/A
label | abc86fe8-48cc-524d-8214-9cb8f8a3ab46 |  | note | Key - W
label | 927beacf-0c07-518d-ada5-7ce49d6ca835 |  | note | Resp - SE
label | c9957923-1178-591a-a41a-e29da33ed7e8 |  | note | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
boolean | 26078f25-9f57-55ba-b62d-0e525c4aaeea |  | tickbox | Work Lot Map
checkpoint-status |  |  | checkpoint | 1.2 - Approved Material Type
label | 49c41681-404a-56dd-bba4-6ca212f9df95 |  | note | Ref docs - IFC Drawings
label | 4481e486-9152-53d5-ad78-9d7bced254cc |  | note | Acceptance criteria -
label | 03142c48-01bb-515d-9af0-9fbb6e3dbc3f |  | note | Acceptance
text | 3b4af81c-52ce-5c6e-8e6f-fbbdf7c07a1d |  | textbox | Approved kerb mix:
label | 5d1bd4e7-9dcc-5c4e-a64f-11eac0d74552 |  | note | Key - H
label | 7633aa1c-2594-584f-b1f5-040956ecccba |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.3 - Preparation of Bedding
label | 53c2c47e-355d-59e6-81e6-b7556041d397 |  | note | Ref docs - AS2876
label | 13b31c32-eec0-5c9c-b7dc-92f29c542613 |  | note | Acceptance criteria - Where kerb is constructed over pavement layers, bedding shall be provided between the pavement layer & the underside of the edging, or the edging thickened to match the pavement layer.
label | 2ee6adde-c78c-5f37-8ab0-e3f0ee19ec8e |  | note | ○ Where edgings are not constructed over pavement layers, bedding shall be greater than 100mm compacted thickness.
button | d051ef3c-824b-5a51-8f20-8d66e5f3702b |  | button | Acceptance | Yes,No,N/A
label | db75f9f2-6612-5071-9bea-dc20ada939aa |  | note | Key - S
label | 013933fc-6ec8-598a-bcf2-d2297410e03b |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.4 - Air Temperature
label | 2630eaa2-e72a-5bad-a028-b819a8e1f9e9 |  | note | Ref docs - AS2876
label | e96201d9-3214-573a-b891-05563b986953 |  | note | Acceptance criteria - Concrete shall not be mixed when the temperature is lower than 5⁰C or greater than 35⁰C.
button | 06096772-3cf5-5619-8b6e-9886b1161e25 |  | button | Acceptance | Yes,No,N/A
label | 789c82ec-323f-5dc3-9d10-e9399cb36e15 |  | note | Key - S
label | dad0a39e-2262-5362-b56d-b3e5bd075ca2 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.5 - Concrete Placement
label | de757d1f-7d44-5c3e-a712-e62b6e281d59 |  | note | Ref docs - AS3610 AS2876
label | 6b6ab994-342e-554e-9b12-f99916d6c1b2 |  | note | Acceptance criteria - Concrete shall be thoroughly compacted by means of continuous tamping & internal vibration shall be worked around any embedment’s & into corners of formwork to produce a dense concrete free from voids, honeycombing, segregation, or surface defects.
label | 1d13dab3-b156-54c9-b6a5-f5b5a44b37a1 |  | note | ○ Concrete shall be finished to ensure a smooth surface with a uniform colour & appearance, & screeded to achieve the specified level, dimensions, falls & tolerances.
button | 7e7d8020-1cdc-5608-a3e1-d9dc919d9060 |  | button | Acceptance | Yes,No,N/A
label | 500df396-f791-52d5-b810-b7c9b8466110 |  | note | Key - S
label | bc0f26c2-5584-520b-b0bf-e7d4c3e7ab8c |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.6 - Joints
label | 993425b7-1371-5c9c-b201-cd825ec9c568 |  | note | Ref docs - AS3610 AS2876
label | 54fb89f2-8687-592c-a7e6-7d54e1bee095 |  | note | Acceptance criteria - Transverse joints shall be constructed at regular intervals not exceeding 3m. For extruded edgings this shall be done by a method which does not damage or distort the adjacent surfaces.
label | 7a7c17c0-c366-5aca-bad3-5f06373d793a |  | note | ○ 6mm saw cut joints within 24-72hrs post pour
label | 1cef008c-e77f-5762-b01e-bfb76c29c4cb |  | note | ○ Sikaflex polyurethane joint sealant or equivalent used to fill saw cuts.
button | 605f3fe8-313a-5dd0-9d21-acc787dc4597 |  | button | Acceptance | Yes,No,N/A
label | 36636ede-8f00-5a5d-84b9-bb643e6de99b |  | note | Key - S
label | ebf13f6b-3fe9-54cc-ad52-1c97b2029869 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 1.7 - Completion of Works
label | 6e926377-d864-594d-a0af-e92f657e695b |  | note | Ref docs - IFC Drawings
label | 3cd62c15-f223-52c4-a389-236adca77f9a |  | note | Acceptance criteria - Correct kerb type installed as per IFC drawings.
label | c0d83e38-00b9-58f5-94e9-ffb9bc10c719 |  | note | ○ Line & level confirmed at time of pour.
label | cdfcd75b-23ab-406c-a36e-d6cbdfad4619 |  | note | ○ As-built survey completed and As-built data attached to ITP
button | ee7821e4-6360-5c7b-b186-129b1cebde04 |  | button | Acceptance | Yes,No,N/A
label | 1f22de03-75b1-5a57-9d73-e762c0fe8f12 |  | note | Key - H
label | 3956a781-879e-5070-beeb-1a0cf2d048e3 |  | note | Resp - SE
checklist-sectioned |  |  | checklist | CC0394 - ITP-013 - Fencing and Acoustic Wall Construction REV01 |  |  |  |  | Yes | CC0394 - ITP-013 - Fencing and Acoustic Wall Construction REV01 | c1fec3c0-e516-450d-9fc2-b81571d209c8
checkpoint-group |  |  | section | 1.0 Pre-start activities
checkpoint-status |  |  | checkpoint | 1.1 - Safety
label | c5d9c5b2-e55b-5fbc-b74b-8ef09e4d0cb1 |  | note | Ensure that the following items have been actioned: SWMS if applicable; Plant Pre-start Inspection; Service locations identified; Traffic Management Plans (if required); All staff inducted
label | f5151e71-59a7-5031-82f3-0eb3d6cb2535 |  | note | Ref docs - SMP
label | a45688ca-947b-5bf3-82e6-1382eeb56c4e |  | note | Acceptance criteria - SWMS submitted reviewed and accepted if required. Plant inspections completed and entered. Pre-work briefings completed. Service Diagrams available and services located. Has all of the above been completed?
button | d1f65f37-ca58-5b29-a01f-df4b87e7c643 |  | button | Acceptance | Yes, No, N/A
label | 02ec33b9-1341-5296-8de0-02abf044a1d6 |  | note | Freq - Once (Pre-Start)
label | 6e8d6a36-4de8-5cce-838b-b842988acffe |  | note | Verification of acceptance by Symal - Key - H
label | c5de2983-265b-5a9d-9aca-5215001277d2 |  | note | Resp - SE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.2 - Relevant Permits Required
label | ace230d5-c0d9-537f-aeaf-0335ce600b9f |  | note | Ref docs - SMP
label | 3d9984a8-9920-5cfe-83ab-690d777c0e4c |  | note | Acceptance criteria:
boolean | c447a2df-b236-5d11-b504-20b349ad976d |  | tickbox | Permit to Work.
boolean | 1e3a5527-42b5-58c6-96c6-fb6eb3052006 |  | tickbox | Penetration Permit
boolean | 10da44ec-79c1-5f1a-8a00-f59396c298f9 |  | tickbox | Hot Works Permit
boolean | ef38e683-12a9-5d84-88e6-a20b74e3615b |  | tickbox | DBYD
boolean | 4be1f42f-a89a-5898-b7f8-d295777b3e13 |  | tickbox | Excavation Permit.
boolean | 00cdbb2c-4658-5d4f-8291-50be08c738ad |  | tickbox | Vegetation Removal Permit.
label | 22e2bab1-4710-5403-80c9-24e0f8b002b2 |  | note | Have any/all of the above permits been acquired/completed and signed off?
button | 47ca6468-b8ff-5928-836f-7dfc2eec8fa8 |  | button | Acceptance | Yes, No, N/A
label | 506830b0-c5c6-5553-87a9-1d5c99f6baf7 |  | note | Freq - Prior to start of works
label | a4811c51-ddbc-5370-8697-12c955801d99 |  | note | Verification of acceptance by Symal - Key - H
label | 38030f12-33c7-598f-b498-bdf40e452fab |  | note | Resp - SE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.3 - Fencing Materials
label | 177bc0dc-afa9-5de0-a14e-f33d6bb961d4 |  | note | Ref docs - IFC Drawings
label | 956d933d-37f0-5f79-b7d9-69009a525534 |  | note | Acceptance criteria - Fencing or acoustic wall Material complies with specifications and IFC Drawings. Do the construction materials comply with regulations and drawings?
label | 917d3291-d944-57ec-8315-272a1e30f022 |  | note | Fencing Type (Select 1):
boolean | 4debbabe-5065-533b-914d-14b5d9eaf899 |  | tickbox | 2900mm Palisade fence – Black powder coated
boolean | 1ff1a209-34f9-46f6-bfaf-b810dbdd3697 |  | tickbox | 3600mm Acoustic wall post & panel (including 1200mm retaining wall)
boolean | aad3f530-6537-48f1-b745-ac9e8f020df7 |  | tickbox | 4500mm Acoustic wall post & panel
boolean | aa27d82a-1db5-4621-a0ac-691ff552e441 |  | tickbox | 2400mm Acoustic wall post & panel
boolean | 97d31ba3-1eb0-42d1-861c-6fb0331a5185 |  | tickbox | 1800mm Chain mesh fence
boolean | 0a3ca4e7-d3eb-5a26-864b-51f70b7279a7 |  | tickbox | Palisade sliding gate
button | d6d1a04a-87be-5ad5-b3cc-4635c7510351 |  | button | Acceptance | Yes, No, N/A
label | 5334678d-dd7f-562b-8c48-090b39b247e7 |  | note | Freq - Prior to start of works
label | 4a15bb3a-d9d8-51a4-a324-239b4aefe3e8 |  | note | Verification of acceptance by Symal - Key - H
label | 2f34c946-9c5d-5301-8503-6857f0a8f3d2 |  | note | Resp - SE
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Preparation
checkpoint-status |  |  | checkpoint | 2.1 - Clearing Fence Alignment
label | 36e926db-bccf-5d56-8713-442dc21dfb2c |  | note | Acceptance criteria - All logs, stumps, saplings, and undergrowth within 1 m of the fence line, and all trees which will interfere with the proper construction of the fence shall be removed and disposed of safely and correctly. High points shall be cut down to provide the clearance shown on IFC drawings and low spots shall be filled with surplus earth from holes and trimmings. Has all of the above been completed safely and correctly to IFC drawings?
button | 82224463-ebd6-5eb8-8bca-ac68e870edfe |  | button | Acceptance | Yes, No, N/A
label | 25fea686-d733-5828-9725-005d7567fc19 |  | note | Freq - Each possession
label | 846dca06-17b0-5cb3-89cc-a140b42fbad2 |  | note | Verification of acceptance by Symal - Key - I
label | be0ec81d-7305-5415-8f1f-2e3d4c918f1f |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.2 - Set out
label | 5ed41ca6-4af5-5ec5-9af8-f07f5b0defe5 |  | note | Ref docs - IFC Drawings
label | 96654af6-6ddb-5bcc-81c7-3a6d5b29c1db |  | note | Acceptance criteria - Surveyor to set fencing alignment and individual post/sleeve set out in accordance with IFC alignment plan/design model. Has all of the above been completed safely and correctly to IFC drawings?
button | 4aa7abaf-8e1f-5652-b4c6-3fd858b988cf |  | button | Acceptance | Yes, No, N/A
label | 6e0c5e4e-517d-5aaf-a25f-0b22353fb366 |  | note | Freq - Each possession
label | 904543e3-c166-5a05-84e4-d9e3fa9d3a73 |  | note | Verification of acceptance by Symal - Key - I
label | 3cec873a-99fb-5f15-9f88-a73791c21251 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 2.3 - Checking fencing alignment
label | a15f061f-9763-579b-928f-cbc563be9f78 |  | note | Ref docs - IFC Drawings
label | 7073c44c-35a9-57d9-ab3c-4f41004741c9 |  | note | Acceptance criteria - Physically check survey set out of fencing alignment. Has the above been completed complies to IFC drawings ?
button | a6cdf53c-f51e-5dee-8165-8e4c9cf0eef4 |  | button | Acceptance | Yes, No, N/A
label | 12919959-5f76-5fff-8306-687c2f648e1a |  | note | Freq - Each possession
label | 2c2fb60d-f8aa-5d96-8f6d-1c22ebc50252 |  | note | Verification of acceptance by Symal - Key - I
label | 6a299cbe-84c3-5683-a52e-12a4d0c479be |  | note | Resp - SE
checkpoint-group |  |  | section | 3.0 Footing and Post Construction
checkpoint-status |  |  | checkpoint | 1.2 - Set out
label | 1d10197b-9b2f-5621-b987-c187dced90a5 |  | note | Ref docs - IFC Drawings
label | 64e4da87-2d3b-5324-b4cd-c4e840b0cf55 |  | note | Acceptance criteria - Has the footing location and height been set out by a Surveyor?
button | dfa99a16-f8bb-51e8-9303-93d4f67b9e53 |  | button | Acceptance | Yes, No, N/A
label | 4584d2df-d455-5e5e-a784-68ee3627690c |  | note | Verification of acceptance by Symal - Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Excavation of hole
label | ac047b35-247d-52f0-9ac5-badb91aa7bc6 |  | note | Ref docs - IFC Drawings
label | 22f8248f-3886-572a-943d-096aad315f89 |  | note | Acceptance criteria - Hole to be excavated to the depth and diameter specified in the design drawings. The design dimensions are:
text | 9b768947-0beb-5f1b-832f-1137d205c1a5 |  | textbox | Depth:
text | 31eea89a-3b19-5280-81a1-44d661a9c9d5 |  | textbox | Diameter:
label | 27e40e65-ca65-50e8-916d-09a76074c731 |  | note | Verification of acceptance by Symal - Key - S
checkpoint-status |  |  | checkpoint | 2.3 - Inspection of hole
label | 911cef4c-4f47-5954-b3e7-d4fbfa1f2d2d |  | note | Ref docs - IFC Drawings
label | f43d2fb9-b4e4-5988-841e-ee87c29c2dab |  | note | Acceptance criteria - Is the hole clean and free of debris & water?
button | aeae6087-8522-5e9d-a9d6-7c3f543b7275 |  | button | Acceptance | Yes, No, N/A
label | e01e8a05-aa1f-5fdb-a4b6-e7611a0067fa |  | note | Verification of acceptance by Symal - Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.4 - Concrete pour
label | 335bca2d-01b4-5250-a45f-a64874ccfdd3 |  | note | Ref docs - IFC Drawings
label | 11257bf8-4dea-5bbb-a20e-77a8b9c24ea4 |  | note | Acceptance criteria - Confirm concrete grade is 25 Mpa [KN3] or better.
button | 5bdb18fb-d90c-5a7d-9597-98a0dd320c1c |  | button | Acceptance | Yes, No, N/A
label | 261a9bfe-aa0b-575a-82fa-edd97488fddb |  | note | Verification of acceptance by Symal - Key - H
boolean | 2fa4e115-9e98-5cb2-8390-9df129a52668 |  | tickbox | Remarks/record - Concrete docket attached
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.5 - Installation of post
label | 625f4d6f-4618-51d5-98f8-e1d2d59255cb |  | note | Ref docs - IFC Drawings
label | 578f5e44-fa98-505e-8690-2e4195990afc |  | note | Acceptance criteria - The fence post will be inserted into the footing and measured for verticality with spirit level. Has all of the above been completed safely and correctly?
button | 7eded736-1e45-5aea-a9b5-999ec6765aee |  | button | Acceptance | Yes, No, N/A
label | 7b28113e-cd5e-5ac8-bd5d-ba357c0996f9 |  | note | Freq - Each possession
label | e639e25b-6e73-5bbd-b672-6069be12bcf2 |  | note | Verification of acceptance by Symal - Key - I
label | aaa8b1ef-3384-5465-ab08-08c47af013b2 |  | note | Resp - SE
checkpoint-group |  |  | section | 4.0 Fence Construction
checkpoint-status |  |  | checkpoint | 4.1 - Concrete curing
label | 6e5f2a09-6f86-56c7-ae60-13d38fe3a3ec |  | note | Acceptance criteria - Has concrete been allowed to cure for at least 24hrs prior to proceeding?
button | bf95331b-0d65-53ec-999d-7d7fe2ffcce0 |  | button | Acceptance | Yes, No, N/A
label | 73e15420-e209-5a21-b6b9-10bdb6daba28 |  | note | Verification of acceptance by Symal - Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Installation of tension Wires and Bracing
label | f890fb3f-b7b5-5a83-9f8c-b743f8f79a75 |  | note | Ref docs - IFC Drawings
label | 45fe17e4-0c05-54de-b597-6fa2b7c9b317 |  | note | Acceptance criteria - Once post have been installed, tension wire is to be installed as per IFC drawing. CHS Brace to be installed at the end bays and Corners fixed at each end via approved proprietary post and rail clamps. Has all of the above been completed safely and correctly?
button | f400fb0f-b4c4-5285-a975-2e10aecfbf3e |  | button | Acceptance | Yes, No, N/A
label | 0c23e204-9cf6-5307-a977-08d271b22b4c |  | note | Freq - Each possession
label | 9e0d378c-18d9-5629-a4cd-01ecf46867b2 |  | note | Verification of acceptance by Symal - Key - I
label | 077db618-48df-563f-ade0-38a01f06ee31 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.3 - Installation of Wire Mesh
label | 5839959c-3760-5430-8872-9dc7a297ba5b |  | note | Ref docs - IFC Drawings
label | 3ed6c88b-b761-521e-aa5c-556bbb8af92b |  | note | Acceptance criteria - Chain mesh to be installed as per IFC Drawing. Chain wire mesh shall be tightened and securely fastened to posts and spaced at not more than 400 mm intervals online posts and at not more than 500 mm intervals online wires. Has all of the above been completed safely and correctly?
button | 5a2581d4-fec1-5ce4-bc96-308c51aed2e3 |  | button | Acceptance | Yes, No, N/A
label | a877ee4b-340e-5916-a978-7ceeb261d1c6 |  | note | Freq - Each possession
label | a307c58a-fcaa-5735-b55e-fd702b419166 |  | note | Verification of acceptance by Symal - Key - I
label | af4b49f3-8677-5f65-8919-751917ed74a7 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.4 - Installation of acoustic and retaining wall panels
label | bfe8d0e2-a5aa-5e87-b4cb-4c047712ce7d |  | note | Ref docs - IFC Drawings
label | 5e3e46ac-bf21-52f6-b85e-8297857d9518 |  | note | Acceptance criteria - Panels have been installed so that the faces between panels are flush at the joints. Panels have been checked for verticality using a spirit level.
button | 13f7c9ec-377d-56c2-bce2-1da889176f1e |  | button | Acceptance | Yes, No, N/A
label | cc375b90-aeb1-5665-9bac-9571518bb20a |  | note | Freq - Each possession
label | a1e7c052-b7a8-52c5-9aa1-b90ab9394291 |  | note | Verification of acceptance by Symal - Key - I
label | 9e0993a6-779e-5b09-8754-2b147c36b8ed |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.5 - Installation of Gates
label | ffa7b321-6531-520a-a1e4-57a388eec560 |  | note | Ref docs - IFC Drawings
label | 00124c88-100f-5c98-adee-081302abc7d1 |  | note | Acceptance criteria - Install gates of the type, size and location as specified on IFC Drawings. Gate posts are to be of the dimensions and firmly set in the ground to the depth specified on IFC drawings. All gates shall be hung with galvanized hinges securely attached to gate posts and be able to swing freely. Has all of the above been completed safely and correctly?
button | 5609be51-74fa-5592-ad48-4f86091c4077 |  | button | Acceptance | Yes, No, N/A
label | e286dd79-526d-5e04-aac1-2fd2275dda06 |  | note | Freq - Each possession
label | 8f2f2e7a-6cca-532f-9669-3ebdc0b6a8c3 |  | note | Verification of acceptance by Symal - Key - I
label | f28f6ba5-0fe9-5422-9c1d-d973e614fec9 |  | note | Resp - SE
checkpoint-status |  |  | checkpoint | 4.6[KN4] - Earth grid
label | 8921a99b-0664-5a7c-b9c0-c12b50d6a44e |  | note | Ref docs - IFC Drawings
label | 96053640-a4a1-5e9a-b628-c1cf78093130 |  | note | Acceptance criteria - Have earth tabs been welded to the fence at every third post?
button | d1741e56-eeee-5510-ab74-7185fc237c7b |  | button | Acceptance | Yes, No, N/A
checkpoint-status |  |  | checkpoint | 4.7 - Backfill behind retaining wall panels
label | b69bb61d-2117-5f20-86d1-7783e29f97af |  | note | Ref docs - IFC Drawings
label | 9545baa7-2ebe-5283-ad04-a021620beb66 |  | note | Acceptance criteria - Has soil behind the retaining wall been compacted as per the IFC drawings:
text | 66a21988-80b9-5ef6-a311-107c49b41998 |  | textbox | Lift depth:
boolean | 9fe66aa0-ede2-5016-b5b2-3a8c01109328 |  | tickbox | Remarks/record - Compaction test report attached
checkpoint-status |  |  | checkpoint | 4.8 - Construction Tolerances
label | 82ce3f54-bb1d-56e0-a775-2a4937b652bb |  | note | Ref docs - IFC Drawings
label | c73a3144-d540-5d8e-991c-90640f6a5f64 |  | note | Acceptance criteria - Unless stated otherwise, tolerances for the construction of fencing shall be as follows: (a) the vertical tolerance on the height of fencing shall be ± 20 mm from the design line. (b) the longitudinal line tolerance for fencing shall be ± 20 mm in plan view; and (c) the tolerance on the verticality of fencing shall be 1 in 50. Has all of the above been completed safely and correctly?
button | 00946170-8082-59dc-a2a8-266cb983501b |  | button | Acceptance | Yes, No, N/A
label | 478c460a-dfef-5d7c-8ff9-edc593fadb8d |  | note | Freq - Each possession
label | c91ef68c-4c71-545e-92ff-127bcc1d2823 |  | note | Verification of acceptance by Symal - Key - I
label | 048c7646-e7e0-5c64-a6d1-f5b6aa8bf750 |  | note | Resp - SE
boolean | a8f6321a-053f-597a-9bb8-90edb8ddc01e |  | tickbox | Remarks/record - Survey Conformance Report
boolean | 501b05bb-38d5-5356-af7c-ff10ba5f9e19 |  | tickbox | Remarks/record - Third Party Compliance of installed fencing
checkpoint-status |  |  | checkpoint | 4.9 - Signage
label | 652f677c-182e-52e7-9aec-341aa4b0105f |  | note | Ref docs - IFC Drawings
label | 947e4d2f-a7b0-5882-87d5-4c3f4da4649c |  | note | Acceptance criteria - Have ‘Danger, High voltage, authorised personnel only’ signs been attached to the fence?
button | 87b17027-f142-5c2b-8193-a90c66425cee |  | button | Acceptance | Yes, No, N/A
label | d84943a0-a9e5-5ffa-8010-e85b966ecb90 |  | note | Verification of acceptance by Symal - Key - I
label | 1d6775ac-8688-5360-849a-8a0d515149ca |  | note | Resp - SE
checkpoint-group |  |  | section | 5.0 Work Lot Close Out
checkpoint-status |  |  | checkpoint | 5.1[KN5] - Quality Representative to check the above criteria and records to confirm
label | c70e1887-8d5a-514a-977a-a90581ef4d03 |  | note | Acceptance criteria - All above criteria met, and records identified attached.
button | dcc3d1d2-e8c5-53e3-90d7-f91f2aebca67 |  | button | Acceptance | Yes, No, N/A
label | 1ea2b7a6-5741-5b65-b69c-1e01679ec449 |  | note | Freq - Each lot
label | 7220aeca-d75a-54f8-bd1b-c2156ecedcfe |  | note | Verification of acceptance by Symal - Key - R
label | 79e4717f-5163-5fb5-82c5-7256b26a8edc |  | note | Resp - SE
label | 273738ce-f45e-5e89-983f-a7c9f04a50cc |  | note | Completed Checklist (if applicable) and reports and other compliance records attached.
checkpoint-status |  |  | checkpoint | 5.2 - As-Builts
label | 21c9b98f-a066-5fff-ae03-a3c8e52881f7 |  | note | Ref docs - IFC Drawings
label | f571be63-b7f8-5665-b5a4-a46890be2b21 |  | note | Acceptance criteria - As-built survey of work lot attached. All points within tolerance.
button | 33f2bc2a-72c3-5391-acce-37b6a1df4444 |  | button | Acceptance | Yes, No, N/A
label | 83458a18-5e98-51c8-a6e9-c3bf44c31dda |  | note | Freq - Each lot
label | c3aa7ecf-f458-528b-af91-c5b52004364f |  | note | Verification of acceptance by Symal - Key - H
label | 24a72560-d21f-552c-8846-a34df88bf9c1 |  | note | Resp - SE
boolean | 1a3900e9-d9e2-55f2-91b8-fb48fc1a6502 |  | tickbox | Remarks/record - As-Built Attached
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checklist-sectioned |  |  | checklist | CC0394 - ITP-010 - FRP Combi Slabs | itp |  |  |  | Yes | CC0394 - ITP-010 - FRP Combi Slabs REV0 | ddfa3c4a-72cc-4082-afc5-79cd32f3a72f
checkpoint-group |  |  | section | Lot Conformance.
checkpoint-status |  |  | checkpoint | Lot Conformance
select | 83842cb9-b41b-5054-9e07-c2bdf417cb1d |  | dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | f7d0fcbc-0c1b-5486-81b6-c9733c817cd9 |  | textbox | Lot opened date:
text | 25049e25-f996-5df1-941b-6bc338801d8d |  | textbox | Lot opened by:
text | 90f06e5f-8597-5e26-b964-5d242d4f1c95 |  | textbox | Date lot closed:
button | e413726b-287c-51e2-9ff1-71f4865ee590 |  | button | NCR raised? | Yes, No
text | 8657443d-cd8e-5ec8-b32c-1a70375fbdf4 |  | textbox | NCR Raised Date:
button | 0114c979-4353-5114-890d-8d08f9b96cfc |  | button | NCR closed? | Yes, No
text | 5ed7d668-eb79-519d-bd15-90b8a532f8dd |  | textbox | NCR Closed Date:
text | 5bc402f5-4dcd-5cb1-9959-76e0776ae491 |  | textbox | NCR Number:
text | 8e06e785-dd69-5045-8ecf-96ad5e01436a |  | textbox | Comments
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - SWMS approval
label | 7d0ad84c-bfc4-5305-83b7-7d5e9d354a62 |  | note | Acceptance criteria -
button | 80e33489-b225-5357-99d8-20789a49aca2 |  | button | Has the subcontractors SWMS been reviewed and approved by Symal PM and HSE, and client. | Yes,No,N/A
label | aed824a5-bf78-5594-a401-d037562871d8 |  | note | Frequency - Pre-commencement
label | 1c2f0ef5-63a1-5f60-a40f-9385c3efa05a |  | note | Key - H
label | a44f0853-d41a-52cd-a7b7-8081b7a616d5 |  | note | Resp - PE/SE
label | 9840fc8a-9ff0-52aa-8d2c-043c956162a4 |  | note | Client Key - W
label | e23b669a-f562-5d76-8c2c-e8366bea1d64 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | 561b4ff7-4278-5594-bd82-728bf4c56146 |  | textbox | Correspondence Reference #:
checkpoint-status |  |  | checkpoint | 1.2 - AMS Creation
label | d268477c-7a5c-5993-a64e-a2ab3ade292e |  | note | Acceptance criteria -
button | 2f3831d8-9d5e-58e1-a7f3-017e39a2f261 |  | button | Has an AMS been created between Symal and the Subcontractor, reviewed and approved by the Symal engineering and management team. | Yes,No,N/A
label | abe3103d-42f0-5df9-8101-709167b296cd |  | note | Frequency - Pre-commencement
label | d1b9b0e0-b4f7-568a-a150-f3384221e538 |  | note | Key - H
label | 57c1f70c-4b34-515e-b088-766cdffe8fd9 |  | note | Resp - PE
label | 0c79291a-b3a7-5c4f-921e-61185bce8399 |  | note | Client Key - W
label | 548ad30d-0280-579d-bc37-e3e4d1cd5a57 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | 2c0acbda-8c04-5480-9e7b-2fa3ad331e32 |  | textbox | AMS Document Reference #:
checkpoint-status |  |  | checkpoint | 1.3 - Enviro controls
label | f024c200-d847-5cf4-9baf-a908564816a5 |  | note | Acceptance criteria - Are all necessary environmental controls in place in accordance with the AMS
label | 2b6d7339-9424-53e4-81bb-767bbd7e5bcb |  | note | Frequency - Pre-commencement
label | 1da5b112-a0cf-56c1-b365-6658841bf75a |  | note | Key - H
label | 5c10fe32-c54d-5dda-bed0-e087da7aa958 |  | note | Resp - SS
label | 8f73b68d-4274-5fb9-8bf4-3e90e6cb639f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos
checkpoint-status |  |  | checkpoint | 1.4 - Previous Layer Conformance
label | 316a8bd9-0836-5d6a-bf08-d661bd36518a |  | note | Acceptance criteria -
button | e6990e09-0bb9-56aa-9444-d003580e043d |  | button | Has the previous layers been conformed and verified? | Yes,No,N/A
label | 0f87bf34-e777-5a03-8525-da9e5a2b9a21 |  | note | Frequency - Pre-commencement
label | cae88070-3359-5d91-b949-b996d7a6072e |  | note | Key - H
label | 1575a729-a063-5e62-9791-bd66b66f2c6e |  | note | Resp - PE
label | c6dcb6a8-94ec-5524-900c-51cae1f9c082 |  | note | Client Key - W
checkpoint-group |  |  | section | 2.0 Material Approvals and pre-commencement requirements
checkpoint-status |  |  | checkpoint | 2.1 - Manufacturer provide QA and manufacturing control procedure for approval
label | e4e03282-2f40-5e61-9384-f8fd6d4924b8 |  | note | Ref docs - RANGEBANK 200MW BESS SFRC/ COMBI SLAB SPECIFICATION TECHNICAL DOCUMENT 3.17 IFC Drawings 5668-126-1006
label | cacff97d-4f79-5b86-955b-0e59b051f92e |  | note | Acceptance criteria - Mix design to be approved prior to placement.
label | f9a232b9-4708-5fe7-a747-97401ac496f2 |  | note | ○ Material properties meet project specification.
label | 1b4b9f72-6220-54e5-af4d-f584b13c059e |  | note | ○ 32Mpa DRAMIX 4D6560BG @ 35kg/m3
label | 68c42036-c8ae-5ee0-af99-a08d90ff8a1c |  | note | ○ Ensure mix design quotes cementitious content of the mix 320kg/m3 for 32mPa concrete and has a maximum size of 20mm stone.
label | f56dd4d6-6d30-5108-a6fa-a59ab010fbbe |  | note | Frequency - Pre-commencement
label | ce463c0f-22dd-5cc4-a688-c3b6ab289752 |  | note | Key - H
label | 16c8f24e-3b90-5667-907a-ffe8fb974e5b |  | note | Resp - PE
label | 9790e2aa-5d22-519a-8ca0-9aabf6a0bfc7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | 634965e3-3a3a-5e2c-a229-afefbae7fa70 |  | textbox | Procedure approval ref No:
label | 00416e71-80b8-58c5-82b0-be1fcde55f29 |  | note | ○ Daily production reports
text | 8e45f9ac-27f9-53e8-a9f6-e24a82292cd7 |  | textbox | Mix design approval correspondence reference number:
checkpoint-status |  |  | checkpoint | 2.2 - DRAMIX mixing dosage
label | 259925a3-039b-56bf-99d3-c45643e136f9 |  | note | Ref docs - RANGEBANK 200MW BESS SFRC/ COMBI SLAB SPECIFICATION TECHNICAL DOCUMENT 3.17 IFC Drawings 5668-126-1006 5668-132-0005 Rev 2
label | 26015daa-3f35-51a0-9329-e2c926e4ac71 |  | note | Acceptance criteria - Mix design to be approved prior to placement.
label | b1972d00-5287-5ec9-bb8a-df9a635f9341 |  | note | Material properties meet project specification.
label | 54538287-7cce-523a-9d90-084e60dd46a8 |  | note | ○ 32Mpa DRAMIX 4D6560BG @ 35kg/m3
label | 33bf85f9-495a-5a48-884f-5e26e96666b0 |  | note | ○ Ensure mix design quotes cementitious content of the mix 320kg/m3 for 32mPa concrete and has a maximum size of 20mm stone.
label | 287d1dab-4b08-577f-895d-9af891a126ed |  | note | ○ Dramix steel fibre shall be mixed in accordance with the manufacturer's recommendations.
label | 0cb969ec-ecd6-50d7-bd3f-fb3f99ae3723 |  | note | ○ Refer to SFRC pavement details for dosages in kg/m 3. Refer Table 1.
label | a5ed5fd2-1e90-5a8a-9f08-486ff4076adb |  | note | ––––––––––––––––––––
label | 087a7722-f04d-5bf4-b89f-fb4176eebc26 |  | note | Table 1: SFRC Spec
label | fc87d8ce-d9a2-5fe0-8d13-9016f75515bc |  | note | ––––––––––––––––––––
label | c803e7c8-5237-59f7-b855-6d795e1a0923 |  | note | Compressive Strength (@ 28 days) ¦¦ 32 MPa
label | 2514d98f-07ca-52d1-b6c2-0982642994f5 |  | note | Maximum Aggregate Size ¦¦ 20mm
label | 7a1abd13-09c1-5f73-a327-e679aeb959e2 |  | note | Fibre Type ¦¦ Dramix 4D65/60 BG
label | cf4c044a-d9de-56ef-922c-71eb7ec82f30 |  | note | Fibre Dosage ¦¦ 35 kg/m3
label | 8bd72814-3543-566b-a0c2-a806353577e7 |  | note | ––––––––––––––––––––
button | 09b59b2c-dba2-5336-9856-ddffae53cf21 |  | button | Has this been achieved? | Yes,No,N/A
button | eb0bdae4-0bc8-587a-9217-7f34c60f4fa8 |  | button | Have all required pre-production tests been carried out to the satisfaction of the client? | Yes,No
label | a0ced972-9ee4-5c45-b803-96997daa4d92 |  | note | Frequency - Pre-commencement prior to each Planned Pour
label | 53901a0e-99fd-5c3d-99dd-ab1a9a9887f9 |  | note | Key - H
label | 3ebb294c-eb82-5a02-8369-5514726046af |  | note | Resp - SE
label | c36f2a33-6a93-5e2f-bdfc-8bcc3108ef72 |  | note | Client Key - H
label | c2f4b260-b967-52df-a5a5-ff6d0954d8b6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | 15694dd7-7971-500c-b72c-4ccc1cad30c4 |  | textbox | Procedure approval ref No:
label | 4eee02b9-2642-55b4-a2b4-101b7db089d7 |  | note | ○ Daily production reports
text | 8bb771b9-2f19-5596-9da7-3ebcb6a4fa6f |  | textbox | Mix design approval correspondence reference number:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - DRAMIX mxing procedure
label | 8c057a9c-6238-5bea-8cb3-44e526482924 |  | note | Ref docs - 5668-132-0005 Rev 2
label | ac7fd8f9-8bb0-5b0e-bae6-939c20800df8 |  | note | Acceptance criteria - Concrete supplier to provide contractor with QA procedure to ensure correct Dramix steel fibre is being batched and correct quantity of steel fibre is being dosed for each load delivered.
label | 55ac3516-78cf-521a-9517-f4ea2d5eb8df |  | note | ○ While the truck is rotating at full mixing speed, if adding fibres: shall be no faster than the mixing concrete carries them away, approx. 60kg/minute. Do not add the contents of a whole bag in a single action.
label | fa97e5b4-f2fc-5eb6-888a-d32423d5485d |  | note | ○ Is a calibrated auto dispenser present at the batching plant? If not a notification is to be submitted to the designer for review and dispensation granted.
label | c3cfeb6b-9b41-5c3c-a291-aecec4675703 |  | note | ○ Have the fibres been added to the concrete load after all other components have been batched?
label | 4350a487-080d-5596-994d-5159d056d669 |  | note | ○ Add fibres at full mixing speed for a period of 5 minutes?
button | 2d6afdf2-503a-5a8a-bd80-831fae1d4272 |  | button | Has this been achieved? | Yes,No,N/A
label | 8f47d625-e6f7-5e5c-b4ea-f0a5452d24bd |  | note | Frequency - Pre-commencement prior to each Planned Pour
label | 73547a70-0470-5e64-8cc1-e8a89ae0008e |  | note | Key - H
label | c8ff87c2-21e0-593f-8377-f7a148d97187 |  | note | Resp - SE
label | 5699e7e5-0c8a-52d2-a14b-4e9ba8a46ac5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Supplier Certificate
label | 988435fc-2ad2-58d8-8c8f-9d7aa16ccfa2 |  | note | ○ Supplier Procedure
label | 7c7a8046-7c4c-5e03-8951-ade5bf9fc767 |  | note | ○ Calibrated Auto dispenser Certificate
checkpoint-status |  |  | checkpoint | 2.4 - DRAMIX and Supplier mixing documentation provision during concrete supply
label | cc08856c-e1eb-5bff-b108-14d466ca32dc |  | note | Ref docs - 5668-132-0005 Rev 2
label | 75ba22fa-8839-5bcf-92d5-e7e777129d21 |  | note | Acceptance criteria - Has the concrete supplier been engaged to produce documentation in accordance with specification:
label | ba00e651-aaf6-5c56-8b84-a62c07850965 |  | note | ○ Daily reports to be supplied to contractor and presented weekly (by email) to client noting compliance. Report shall consist of a minimum of truck identification, batching time, quantity of concrete, fibre dosage, fibre mixing time, site placement, test sampling.
button | 2e4f0c80-89ca-5177-9262-c845ce4390e8 |  | button | Has this been provided, reviewed and approved? | Yes,No,N/A
label | 2cd22673-f7d6-5318-b74b-cb708f6208c9 |  | note | Frequency - Each Planned Pour
label | 7382b995-cb01-5118-93a9-3bdd4ebb1d02 |  | note | Key - H
label | 89c9f00f-0209-52fa-9c26-0c132c34d65a |  | note | Resp - SE
label | dbaf5437-5a34-51a6-9288-326d1cadef9a |  | note | Client Key - S
label | 9c4ea4b5-5b70-54c8-98f2-afa825f83555 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - QA Procedure required for review
label | 02dee12f-29d9-5371-80ee-108d5c8c5500 |  | note | ○ Daily Reports
text | e4599f72-efd8-5aa0-9d60-92586c6fd4a3 |  | textbox | Email correspondence records (ie dates and addresses):
checkpoint-status |  |  | checkpoint | 2.5 - Curing Compound
label | 59e6d7cb-5468-56ce-9154-6a23cd2de1be |  | note | Ref docs - Cl 3.23 5668-132-0005 Rev 2
label | 8814a469-3316-5a21-a512-74f0bc8ed80d |  | note | Acceptance criteria - Curing of all SFRC pavement shall be undertaken using approved spray seal curing compound complying with AS 3799 and project brief. Curing compound shall be applied in accordance with the manufacturer's recommendations
label | ea4fa891-39de-524c-996b-6b7b53c46295 |  | note | Frequency - Pre-commencement for each planned pour
label | 2c26dd80-231a-52e5-8d55-88b2c4307226 |  | note | Key - H
label | b74b19c4-003c-5c4b-b366-b15d754a32f9 |  | note | Resp - SE
label | cc466c2d-76a9-590f-a1cf-e3e5fed26a93 |  | note | Client Key - H
label | 46c171df-e4ec-52b3-acb0-f14e8f560bb1 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Data sheets and manufacturer installation procedure
text | 72206db7-d632-5f8d-9dc8-94f934a1bc07 |  | textbox | Correspondence record from client for material and method approval:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 3.0 Bedding and Surface Preparation
checkpoint-status |  |  | checkpoint | 3.1 - CBR Testing
label | a2e1418f-5029-5fb8-8461-9369ad184920 |  | note | Ref docs - 5668-132-0005 Rev 2
label | eb86c895-83bc-539e-87f4-3b2c4109d76b |  | note | Acceptance criteria - Has a minimum value of 3% CBR been met on the layers below. The testing needs to be completed as 3 tests per 1000m2 lot. (Note: minimum 3 tests per pour if less than 1000m2)
button | 1848b023-da34-5c21-98c9-c421c8644ce8 |  | button | Has this been completed for the planned pour? | Yes,No,N/A
label | 49d21634-56ce-5839-bfcd-48e88d131b5b |  | note | Frequency - Each Pour
label | 7fe4af6a-c074-52af-bd35-b4aa9a3823a3 |  | note | Key - H
label | 9fe5c144-6e45-5781-905a-e61a9b9213f2 |  | note | Resp - SE
label | 30abaca8-7e46-5e02-b354-0295b99177e9 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test Results showing compliance
checkpoint-status |  |  | checkpoint | 3.2 - Construction Joint Profiling
label | c27c69cf-762c-5db6-b7a5-d96bf50a7f33 |  | note | Ref docs - Drawing 5668-126-1006 5668-132-0005 Rev 2
label | eba13c7d-8466-5be6-8535-40d58ad6e9fe |  | note | Acceptance criteria -
button | 4c594e9c-8ad8-5ea4-9f90-2137d6e03b12 |  | button | Have the 160mm slab construction joints been profiled to 200mm below FSL of the combi slab? | Yes,No,N/A
label | 45b7c376-30fb-5759-a0af-33d57f8177f7 |  | note | Frequency - Each Pour
label | 058932a0-972c-56a5-930e-f33c2b945d75 |  | note | Key - H
label | 3e6934de-217c-5de6-b1ab-d0d3843d08ac |  | note | Resp - SE
label | a54c088d-517f-52c0-93cb-f1e2db0e33ef |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos
label | ae279a65-678b-532f-b16a-c3de16f44c5c |  | note | ○ Prepour inspection including Drawing markup
checkpoint-status |  |  | checkpoint | 3.3 - Base Conformance
label | f7d34ae0-5488-556f-b2e5-9332ec3a3041 |  | note | Ref docs - 5668-132-0005 Rev 2
label | 573c4410-7053-57b2-b6a7-c86477ce4544 |  | note | Acceptance criteria - Has the base been conformed within the allowable tolerances set out in the specification? Including the edge thickening.
button | 21003218-316b-5b2c-8422-bd4ed207a3dc |  | button | Tolerance is 0 to -10mm unless otherwise agreed. | Yes,No,N/A
label | 3baf2154-3b3b-52a7-82aa-54bafa811e73 |  | note | Frequency - Each Pour
label | 85867da3-7335-5d96-9093-55844ae35370 |  | note | Key - H, H
label | 85cd573c-8109-5cd1-ab4c-5b10d9973f7e |  | note | Resp - SE, Surveyor
label | 69b9f94f-59a9-5b5e-a0a7-07a953f8af54 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Results and sign off on the ITP
checkpoint-status |  |  | checkpoint | 3.4 - Water Ponding
label | f1238891-1a0c-5409-b180-e9632e2e5a8d |  | note | Ref docs - 5668-132-0005 Rev 2
label | c960e198-e81e-5ab0-b984-9cbda859ad6e |  | note | Acceptance criteria -
button | 3086a7f4-d4be-5a33-9f20-e9e053ef8c41 |  | button | Is water ponding on the surface? | Yes,No,N/A
button | 286d1b4e-b709-57a3-bb71-3fb7ed4556b4 |  | button | If yes, has the surface been removed and replaced and proof rolled for approval to continue with pouring. | Yes,No
label | 9cc13196-d2aa-5336-841c-c143347bd700 |  | note | Frequency - Each Pour
label | 264fef84-664f-5dfe-a950-f7f3b4e43e72 |  | note | Key - H
label | 6edc4bc9-fd46-54ee-afe2-761e28cf4a29 |  | note | Resp - SE/SS
label | 0e5a3dba-18fc-5738-88a4-2821d003b40c |  | note | Client Key - W (if ponding evident)
label | 902e5070-4e2a-588a-96d2-2e6c3ff7a1f7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos if applicable.
label | 3b8fb988-3755-5c6d-966b-36243fe6c1a0 |  | note | ○ This ITP
checkpoint-status |  |  | checkpoint | 3.5 - Bedding Surface Check
label | cf0b8ac4-b2fb-5714-9f92-2332dfc921cb |  | note | Ref docs - 5668-132-0005 Rev 2
label | 043a66c8-f673-542b-af62-ae1d57738f63 |  | note | Acceptance criteria -
button | a8b9c63b-59bc-5e53-9803-78c5e206360b |  | button | Is the surface free from damage and all other ruts and depressions have been carefully screeded and flattened? | Yes,No
button | 9317cf03-2bb3-5bff-ba65-ce8bcdacf5d2 |  | button | If ruts or depressions found, rectification to be to satisfaction of client. Has client approved rectification | Yes,N/A
label | 57c99afe-7e52-5f7e-bafc-5fe2ef53b8a9 |  | note | Frequency - Each Pour
label | b995f1d6-f80a-597e-9ee2-885b8ab2e050 |  | note | Key - H
label | a5618e25-f51e-5f0b-a0c5-32be6bb7a9b9 |  | note | Resp - SE/SS
label | 5aab7f13-7bec-5a0e-a21c-4b0ab725cb1e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - This ITP
label | 89904bb7-30f0-570b-885a-45f491d24770 |  | note | ○ Supported by General photos of pour area.
label | ee9ff8f6-60bb-5182-ad75-bc605bc581d2 |  | note | ○ Email correspondence from client for approval of rectification if applicable.
checkpoint-status |  |  | checkpoint | 3.6 - 0.2mm Membrane Installation
label | a37de4d4-5a75-5e90-a9ab-fa7634259049 |  | note | Ref docs - 5668-132-0005 Rev 2
label | 740cff01-b2c9-5f46-a7ec-30fa9a13e6ea |  | note | Acceptance criteria - Has the 0.2mm Membrane been installed with 200mm overlap over adjacent sheets and taped on the surface?
button | 9d92dd0a-a2d1-535d-b0be-a856f5bb5761 |  | button | Has the membrane been otherwise lapped in accordance with the manufacturer’s specifications? | Yes,No,N/A
label | d58262b3-5319-54fb-9578-21b51357cb96 |  | note | Frequency - Each Pour
label | 9d2ae204-5528-57ed-b818-3a730e1eb6cb |  | note | Key - H
label | 0c719556-19c5-5802-a6d8-8e10702b7e10 |  | note | Resp - SE
label | c88d2406-9ddb-5935-b63d-0c84295c2921 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - This ITP and Photos of membrane overlap in a couple locations - date and geostamped.
checkpoint-group |  |  | section | 4.0 Formwork and Reinforcement
checkpoint-status |  |  | checkpoint | 4.1 - Set out
label | e5ef7409-d300-5539-92c7-490fbcf31075 |  | note | Acceptance criteria - Extents and levels correct to relevant drawings.
button | 9e5ad08b-d33d-5519-b789-48bc5e04ba4c |  | button | Has this been completed? | Yes,No,N/A
label | 1c3c3c5d-0983-58c6-9228-1fa585fa27b5 |  | note | Frequency - Each Planned Pour
label | 862c14fd-d4ce-532d-9cd9-7441e7bf6165 |  | note | Key - H, S
label | 9dcfec1f-0ee9-55ff-94f0-d6d9c717776d |  | note | Resp - SS/SE (Signature by surveyor)
label | 50da57aa-17bf-52c2-a9fa-86465b3b2f1b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Surveyor attendance record and sign off on this ITP
checkpoint-status |  |  | checkpoint | 4.2 - Formwork and Boxing, including concrete culverts
label | 0fcd58e0-4c6c-5e03-be1b-a0ffd38e3bbe |  | note | Acceptance criteria -
button | b322db64-18a5-5ce1-8bbe-e5e4417acdec |  | button | Has the formwork been set to the correct finished surface level? | Yes,No,N/A
button | 421fcabe-6036-54e9-9c4a-2968b91f3818 |  | button | Have all rebates, recesses, service boxes, pirs and sumps been included from all relevant architect, building civil and structural and electrical engineering drawings? | Yes,No,N/A
label | d6d1a8ba-1223-508c-92dc-95ded3dd3559 |  | note | Frequency - Each Planned Pour
label | 893d02cb-c4c5-5940-8d3d-114722aafd21 |  | note | Key - H
label | fac82d86-35c2-528e-baeb-cdae40e514e8 |  | note | Resp - SS
label | 04e25682-35b3-531b-ae7c-4baf0b417223 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos
text | e4c17c0d-208d-5588-8470-a37b53edcbd0 |  | textbox | Quote drawing numbers for any rebates etc:
checkpoint-status |  |  | checkpoint | 4.3 - Vertical Cover
label | 6da6dbfb-7894-521e-9229-da04aa69bec5 |  | note | Ref docs - 5668-132-0005 Rev 2
label | 678383d3-d40e-5525-931a-e1b2cbfc0611 |  | note | Acceptance criteria -
button | 62be7ec4-5365-57ca-a146-d2e8f2cb2f1c |  | button | Has the minimum cover of 40mm been achieved in all locations across the planned pour? | Yes,No,N/A
label | 7b400e03-8652-5b8a-8470-d71a8e547b74 |  | note | ○ N12 bars to be installed – allowance is 2 sheets + 24mm tolerance.
label | eb498020-96f9-54f2-81ff-208f649a382e |  | note | Frequency - Each Planned Pour
label | b3c7f303-a2fb-5e56-89d7-e5a64d69dbbf |  | note | Key - H
label | 7957cbd5-fce5-51b3-bc6e-302839621222 |  | note | Resp - SE/PE/SS
label | b0a69621-9305-5c38-bf85-fdb8356b0b3b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos of cover measurements
checkpoint-status |  |  | checkpoint | 4.4 - Horizontal Cover
label | 90ceb96d-35c9-5fea-bf32-7aca0cc1660c |  | note | Ref docs - 5668-132-0005 Rev 2
label | 45b9a73a-4087-5568-8a54-c4b97ab219bb |  | note | Acceptance criteria -
button | 046e9535-f48f-56c8-a885-8c98ad8e259d |  | button | Has the minimum horizontal cover of 50mm been achieved in all locations across the planned pour? | Yes,No,N/A
label | 38002e65-11d0-5dee-98b4-f6410cabb609 |  | note | Frequency - Each Planned Pour
label | 4b9f8f7c-8562-5adf-b0ed-36e61f5f1edc |  | note | Key - H
label | 8438f0f7-bd5b-5020-afbc-6aed1dc3bf04 |  | note | Resp - SE/PE/SS
label | 818a1248-a8a0-5032-949f-9bb543ffe856 |  | note | Client Key - W
label | c79bf90f-55db-5512-932f-1bd181460f3e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos of cover measurements
checkpoint-status |  |  | checkpoint | 4.5 - Overlap/Splicing Sufficient Extents
label | 04594699-4fd2-5c80-aded-17486bd2daea |  | note | Ref docs - 5668-132-0005 Rev 2
label | 8d26fffd-967b-5faa-b204-bac3647c08c3 |  | note | Acceptance criteria -
button | 972a342a-420a-5fad-a896-c173c1ca26b9 |  | button | Where there is splicing and overlap required, has the reinforcement been extended greater than 200mm over the adjacent reinforcement? | Yes,No,N/A
label | 9849320d-ebf2-5ce7-b0e7-14d5643fa3a1 |  | note | Frequency - Each Planned Pour
label | 2143a740-9c7f-56d9-9bcf-cabc6951e433 |  | note | Key - H
label | 24bd13a2-a017-5ead-a418-cb554d172403 |  | note | Resp - SE/PE/SS
label | 173da965-9936-506d-8b75-ab1c9d3b562d |  | note | Client Key - W
label | 93b09fb2-590f-5612-9a23-f4a82946a84b |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos with tape measure
checkpoint-status |  |  | checkpoint | 4.6 - Overlap/Splicing Cover Considerations, Mesh Corners
label | 778f4055-5b6d-59fb-8fc4-add2542a191a |  | note | Ref docs - 5668-132-0005 Rev 2 Cl3.3
label | 548ee01c-9405-567c-8fa8-61b120fbdb7c |  | note | Acceptance criteria - Where there are 3 or more overlapping locations of reinforcement, has the middle sheets/reinforcement been cut to ensure that the tolerance as per design drawings and specifications is met?
button | 5779b34d-56ab-5d5a-9903-9f3623d87093 |  | button | Tolerance is between 40mm and 94mm from the surface. | Yes,No,N/A
label | 8eee0460-82a5-5aa6-940d-0fdeeb9be76a |  | note | Has the following been carried out correctly for all mesh laps:
button | 5f8786f7-a089-5fac-a05a-32c6bf2216b2 |  | button | Reinforcement cover shall comply with AS 3600 and shall be 40 mm unless noted otherwise. Minimum N12 bar cover shall be 40mm from surface +48mm to allow for two layers each-way, with 12mm of additional tolerance below. Bar position to be between centre and top of slab. | Yes,No,N/A
label | 18f87caf-f993-55ce-bdd9-b994eb997c89 |  | note | Frequency - Each Planned Pour
label | d0e55beb-4100-56f5-8635-672d2d258c6f |  | note | Key - H
label | a881d143-d9cc-5db8-b7e4-08b3b95adfa2 |  | note | Resp - SE/PE/SS
label | 9ad80daa-65af-503c-90ca-c49cfe2f9241 |  | note | Client Key - W
label | 0ce3985e-9adc-5893-b2fd-f13e1745b313 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos
label | 28abe188-df7e-5cfb-a09f-809d62ed5d98 |  | note | ○ Prepour inspection
checkpoint-status |  |  | checkpoint | 4.7 - RJE Earthing Installation
label | ebb680b5-f0f3-51a8-99b3-200ba52b6c35 |  | note | Acceptance criteria -
button | 3d00776d-4d4f-55fd-ac7a-4d56a2d87a50 |  | button | Has RJE Installed their earthing to the required locations? | Yes,No,N/A
label | 4c8b6591-c514-5ae1-a1e7-580db9720a9d |  | note | Frequency - Each Planned Pour
label | c4b76eba-dc87-57ba-8026-edd725f9768e |  | note | Key - H
label | 37e1319b-52a1-5e8c-9d07-f8aa1c720cf6 |  | note | Client Key - H
label | 8e3234c8-8235-5cda-8b75-91aa75ddf6a5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - RJE to confirm in writing
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.8 - Pre-pour Inspection
label | 6327cafd-2795-53f8-a575-5c5451022879 |  | note | Acceptance criteria -
button | 4c8b3d33-e124-5371-a84d-bcecf38a2928 |  | button | Has a pre-pour inspection been completed with the client and has it been approved for the pour by all relevant parties? | Yes,No,N/A
label | 38725ecc-0b4a-5ed2-a0f2-a18a0a7b64c1 |  | note | Frequency - Each Planned Pour
label | 97fff96d-7ee6-562f-a0fd-9b3e2ef8d83f |  | note | Key - H
label | d9f07d7f-016f-5d0c-91bd-45c6e8a80351 |  | note | Resp - SS/SE/PE
label | e7e7fa3e-2ce7-501f-a6aa-b359792bcd63 |  | note | Client Key - H
label | fc6ca66d-3b7f-577d-a2df-ba6171bd1847 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Prepour Checklist
label | 88a93b78-0296-5b29-981d-caa28d745399 |  | note | ○ Photos
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.0 Placement and Finishing
checkpoint-status |  |  | checkpoint | 5.1 - Concrete Supply
label | 9fd8936f-0098-552b-a9c1-fb2648eff1b6 |  | note | Acceptance criteria -
button | ab80805b-4fae-5b61-bf9f-dda535669b1b |  | button | Material quoted on Delivery Dockets to match approved mix | Yes,No
button | 466d898c-b022-5d16-8e9f-8f060c7d5fee |  | button | Is the mixing procedure quoted on dockets in accordance with approved procedure | Yes,No
label | fe9f4c22-33b9-5f7a-81b5-46f623892c3e |  | note | Frequency - Each Pour (and regular intervals during pour)
label | cf4a31e6-9ddf-5ada-919a-4c971d3da7bb |  | note | Key - H
label | 61722a33-f030-5ac9-814d-d361ff2bbca8 |  | note | Resp - SS/SE
label | dc3a5df2-ac7a-5a94-813c-4100ac3823c9 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery Dockets
checkpoint-status |  |  | checkpoint | 5.2 - Temperature
label | 44e4a831-811e-579c-9d59-1f8db7ca6863 |  | note | Ref docs - 5668-132-0005 Rev 2 CL3.10
label | 5ea996b3-d827-5b99-9f8c-709b69331554 |  | note | Acceptance criteria - Concrete placement shall not occur on days where ambient temperature exceeds 30 degrees centigrade, nor below 5 degrees centigrade.
button | 9ee5d2c7-f577-56cf-ad19-605ba3b131f5 |  | button | Has this been achieved? | Yes,No,N/A
label | 67bcb70c-2601-5030-99c1-09ad5443b8e5 |  | note | Frequency - Each Planned Pour
label | c82db005-cb16-55a3-8ce7-fafab0ca404b |  | note | Key - W
label | b2c04caa-68b5-5585-bc01-f88e6401ee35 |  | note | Resp - SS
label | 1ee69cbd-022a-563b-bcfd-d3ea74338258 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Weather forecast record (eg phone screen shot of willy weather forecast)
checkpoint-status |  |  | checkpoint | 5.3 - Strength testing
label | 9f22e401-a01b-51d0-8a12-5dc37a148ebc |  | note | Ref docs - AS1012.9 5668-132-0005 Rev 2 AS1379 and Section 16.7 of AS3600
label | 2e91ff4f-2ff8-5781-aba7-4fd2761a7291 |  | note | Acceptance criteria - Cylinder compression tests shall be in accordance with AS 1012.9. one test sample (consisting of a minimum of 3 test cylinders) per 50 m 3 of concrete.
button | ddaa2fe4-0557-5094-a0d5-f9b2c90b401b |  | button | Has the tester been engaged to test in accordance with AS1012.9? | Yes,No
label | 088fb812-9494-5906-8257-73bb3915322b |  | note | ○ All 7- and 28-day test results shall be forwarded to the engineer.
button | b91d98f9-718d-5c78-832a-b2b73044ccd3 |  | button | Is the concrete pumped? | Yes,No
label | 60630b9a-b4fa-5d93-9491-a0d2303c9c80 |  | note | ○ If no, Slump is to be 90mm +- 20mm.
label | a580f9c0-6503-5949-aa02-befd35ea115c |  | note | ○ If yes, Slump is to be 140mm +-30mm.
button | e7b06989-df51-566e-bc9a-dd1685fec2a4 |  | button | Has the correct slump been achieved? | Yes,No,N/A
label | e5162e24-9579-544f-bbdb-cadcf46a6753 |  | note | Frequency - Each Planned Pour
label | 475d719c-b090-53db-b15e-a86613a18601 |  | note | Key - H
label | e4501ca0-2b39-5301-b910-272046d862d1 |  | note | Resp - SS/SE
label | d0d451bf-88bd-5ac7-9001-997de5816a8d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - This ITP or preferably a record of the slump test: photo or other
checkpoint-status |  |  | checkpoint | 5.4 - Delivery and Placement
label | 1927c40b-57f8-5626-9c02-a702cd8462cb |  | note | Acceptance criteria - Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
label | 5ea9a965-fbb4-587d-b332-5554683c3f6f |  | note | ○ Concrete to be tamped/vibrated to increase density and prevent voids, honeycombing or surface defects.
label | 123a9b5a-a17c-5e71-bc0d-6a001bebc319 |  | note | ○ Weather Conditions, air temperature and concrete temperature to be recorded at time of pour.
button | f090524d-9ab3-58d3-af70-25a1eece058d |  | button | Has this been completed? | Yes,No,N/A
label | 70745a45-590e-52bf-955d-a53ddb2b25df |  | note | Frequency - Each Planned Pour
label | 11d9466c-91ca-500e-83e9-e8a3dcff79b4 |  | note | Key - H
label | 4abd8c54-688a-52ab-a6c0-32c80649edd1 |  | note | Resp - SS/SE
label | 0522da83-bb14-5940-bacd-ed5cbbdf477d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - This ITP for concrete tamping etc.
label | ee779de9-72f7-51a9-aeff-72aad828efea |  | note | ○ Record of pour conditions on pour progress sheet.
text | 3817ab8f-23e3-5b1a-8fc9-a58d9553f72f |  | textbox | Document Reference Number:
checkpoint-status |  |  | checkpoint | 5.5 - Surface finish
label | bdeedb79-a039-580f-8011-ea879888e4aa |  | note | Ref docs - As per drawings
label | 9b332af2-ec5f-515c-aaae-cc00f37ac458 |  | note | Acceptance criteria - Concrete surfaces shall be true and even, free from honeycombed surface depressions or rejections.
label | f587fb0b-20b2-5f66-aade-c2ee64cf7229 |  | note | ○ All protruding steel fibres to be removed from the surface during pour.
button | c94bb9b4-1125-53c6-8062-17681a484722 |  | button | Has this been completed? | Yes,No,N/A
label | dbec2b40-bd20-5299-9d05-b959a6abd19b |  | note | Frequency - Each Planned Pour
label | b26c5a40-b448-5ca7-9f85-3669ee949f6b |  | note | Key - H
label | 0dea40b4-4665-5e19-b72e-0e718d27af99 |  | note | Resp - SS
label | 0bbbd9de-5d39-5005-a599-77c15c35b02e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - This ITP
label | 84c41e5c-404c-5977-ad3d-7783d0a166b3 |  | note | ○ Photos
checkpoint-status |  |  | checkpoint | 5.6 - Curing
label | 2d40c67d-49d2-58ce-bebc-61b1b4681369 |  | note | Ref docs - Cl 3.23 of 5668-132-0005 Rev 2 AS3799
label | b235f35a-0570-5887-95e0-0e8ac16e4125 |  | note | Acceptance criteria - In accordance with specification, the SFRC pavement will be cured with an approved spray seal curing compound complying with AS3799.
label | 84df12f2-f19f-5078-9520-6a6d76c8db78 |  | note | Note the requirements of 3.19 do not apply.
button | 3d8db73c-b37c-5362-b3f1-889f30629de3 |  | button | Has an approved curing spray been applied to the surface after the pour in accordance with the manufacture’s requirements? | Yes,No,N/A
label | b34438d8-5e42-50bd-a222-f4218362b636 |  | note | Frequency - Each Planned Pour
label | e2be580a-be2f-5bed-8d43-2ac16399e599 |  | note | Key - H
label | 650b7ecd-c647-5fed-a59b-41bf83ec66dc |  | note | Resp - SS
label | f39bf27d-8bfd-54de-87df-3746b77a4744 |  | note | Client Key - H
label | ab73d874-56bb-555b-a284-11fb485ae479 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos of application
text | e1a19348-570f-59b6-88ad-dcce34f3c136 |  | textbox | Delivery docket for Spray:
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 6.0 Conformance and Documentation
checkpoint-status |  |  | checkpoint | 6.1 - Tolerances
label | f7eb75c5-445f-5568-a508-eb4047ec43ea |  | note | Acceptance criteria - The maximum deviation of any point on the pavement surface from a 3-m straightedge should not exceed 12 mm. Minimum slab thickness at any point to be as per design/ drawing specification of 160mm thickness.
label | ff8ff9c9-7eaa-5171-b6d6-ee9b405d56ff |  | note | Frequency - Each Pour
label | e2c4e5ef-c194-55bc-a406-4bdbc015adce |  | note | Key - H
label | c99a44fd-a6f0-56c6-a3d2-0dfb1336ebd9 |  | note | Resp - SE
label | e79cd90c-92c0-5fe3-92a7-f33202b00cc6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | e20caf45-9c76-5ebd-9c9a-dc2f9d7da054 |  | textbox | Survey record including conformance report:
checkpoint-status |  |  | checkpoint | 6.2 - Documentation
label | 781ee8cd-4004-5a0a-b5b2-a931de46ed3a |  | note | Acceptance criteria - Daily reports to be supplied to contractor and presented weekly (by email) to client noting compliance. Report shall consist of a minimum of truck identification, batching time, quantity of concrete, fibre dosage, fibre mixing time, site placement, test sampling.
label | a7b3bf15-5df5-53c9-9dc8-eb50d30730c7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Daily Reports
text | 0f5b8b1c-027c-56fe-81f3-f9813ac849d5 |  | textbox | Email correspondence records (ie dates and addresses):