## res_1630-P200-SYM-QAC-ITP-0021.
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CC0394 - ITP-014 - Hydraulic Service Installation REV0 | itp |  |  |  |  | CC0394 - ITP-014 - Hydraulic Service Installation REV0
section | Lot Conformance.
checkpoint | Lot Conformance
dropdown | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
textbox | Lot opened date:
textbox | Lot opened by:
textbox | Date lot closed:
button | NCR raised? | Yes, No
textbox | NCR Raised Date:
button | NCR closed? | Yes, No
textbox | NCR Closed Date:
textbox | NCR Number:
textbox | Comments
holdpoint | AUTHORITY HOLDPOINT
section | 1.0 Preliminaries
checkpoint | 1.1 - Determine Lot Size
label | Ref docs - AS3500
textbox | Acceptance criteria - Pipe / lot length:
button | Acceptance - See Work Lot Map | Yes,No,N/A
label | Resp - SE
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Work Lot Map
checkpoint | 1.2 - Survey Set-out
label | Ref docs - IFC Drawings
label | Acceptance criteria - Prior to excavations being carried out, the contractor shall engage a suitably qualified surveyor to set out all fire lines including hydrants and risers.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
checkpoint | 1.3 - Approved Material Type
label | Ref docs - IFC Drawings AS3500
label | Acceptance criteria - All materials selected in accordance with AS4130 and RJE civil specification and drawings.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
section | 2.0 In Process Works
checkpoint | 2.1 - Excavation
label | Ref docs - IFC Drawings AS3500, Excavation permit
label | Acceptance criteria - All excavations subject to inspection prior to the installation of services and throughout the duration of the excavation.
label | ○ Excavate to the lines, levels and grades as required for in ground services specified in accordance with the requirements of AS 3500.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 2.2 - Removal of Obstructions
label | Ref docs - IFC Drawings and specifications
label | Acceptance criteria - Remove obstructions including roots, stumps, boulders, and the like which may, in the opinion of Symal, interfere with the proper functioning of the service.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 2.3 - Bedding
label | Ref docs - IFC Drawings and specifications
label | Acceptance criteria - Pipes to be bedded and supported by class 3 quarry material with a minimum thickness of 75mm.
label | ○ 5-10mm crushed rock or sand shall be used as the haunching material.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
section | 3.0 Installation of pipes
checkpoint | 3.1 - Pipe Installation
label | Ref docs - IFC Drawings and specifications
label | Acceptance criteria - Work shall be carried out by and under the direct supervision of appropriately licenced personnel.
label | ○ During construction, temporarily seal open ends of pipes and valves to prevent the entry of foreign matter into pipe systems.
label | ○ Install piping in straight lines at appropriate uniform grades without sags.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 3.2 - Mains Connection
label | Ref docs - SEW Drawings and specifications
label | Acceptance criteria - Mains connections completed by approved South East Water contractor.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 3.2 - Electrofusion Weld fittings/pipe/couplings
label | Ref docs - as per manufacturers recommendations
label | Acceptance criteria - Ensure pipe is cleaned and scraped prior to welding.
label | ○ Ensure pipe is fixed firmly in position.
label | ○ Allow curing time as per specific fittings recommendations,
label | ○ Visually check all fittings have been welded.
button | Acceptance | Yes,No,N/A
label | Key - W
label | Resp - SE
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) - Electrofusion welder calibration certificate.
checkpoint | 3.3 - Cover
label | Ref docs - IFC Drawings and specifications AS3500.1
label | Acceptance criteria - Minimum depth of cover for buried pipes:
label | ○ 600mm to finished surface.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-Built Attached
checkpoint | 5.3 - Pump Chamber Install
label | Ref docs - Pump Chamber Install
label | Acceptance criteria - Approved pump chamber procured for use on site.
label | ○ Pump Chamber installed to correct position and levels including invert levels of all inlets/outlets within pump chamber.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Delivery Docket/Shop Drawing
section | 4.0 Backfill
checkpoint | 4.1 - Backfill Material
label | Ref docs - IFC Drawings and specifications AS3500
label | Acceptance criteria - After pipes, fittings and pits have been set in the correct position and jointed, further bedding material shall be used to fill all recesses below sockets, and bottoms of trenches.
label | ○ Excavation backfilled with selected clean excavated material, or the purchased material bought to site.
label | ○ 5mm Dust Compliant for bedding
label | ○ BACKFILL Overlay WITH 20mm nominal size class 3 crushed rock
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Material dockets
checkpoint | 4.2 - Layer Thickness
label | Ref docs - IFC Drawings AS3500
label | Acceptance criteria - Backfill material must be placed and compacted in layers not exceeding 300mm.
label | ○ Backfill trenches as soon as possible after approval of laid and bedded service.
label | ○ Allow adequate cover over pipe (minimum 600mm)
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
checkpoint | 4.3 - Compaction
label | Ref docs - IFC Drawings AS1289
label | Acceptance criteria - Compaction to be undertaken using hand methods only for first 300mm.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 4.4 - Preliminary Pressure testing
label | Ref docs - IFC Drawings RJE NOE AS3500.1
label | Acceptance criteria - Sign-off items 1.0 – 4.3. RJE NOE
label | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa. Pressure deviation to be not more than +/- 35Kpa.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | RJE Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | RJE NOE
holdpoint | AUTHORITY HOLDPOINT
section | 5.0 Conformance Check
checkpoint | 5.1 - Clean & Finish
label | Ref docs - IFC Drawings
label | Acceptance criteria - On completion, each line shall be free from dirt, debris, or other impediments.
button | Acceptance | Yes,No,N/A
label | Key - S
label | Resp - SE
checkpoint | 5.2 - Testing
label | Ref docs - AS3500.1
label | Acceptance criteria - All pipe to be pressure tested in accordance with AS3500.1
label | ○ Complete Hydrostatic test for 2 Hours @ 1700kpa
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | RJE Key - H
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | Test certification
bool | Calibration certificates
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - As-Builts
label | Ref docs - IFC Drawings
label | Acceptance criteria - Accurately record the routes of all underground pipes before backfilling.
button | Acceptance | Yes,No,N/A
label | Key - H
label | Resp - SE
label | Remarks/record (e.g. Test frequency reports, certificates, checklist etc.) -
bool | As-Built Attached