## ITP LightPoles
LIGHT POLE FOUNDATIONS ITP
Preconstruction
| Design Drawings | Issued for Construction Drawings available | P,F,Attachment
|  | Drawing MSF-EN-ELE-DRG-070 | United Civil Hold Point
| Survey & Setout | Visual Inspection of Light Pole Location setout | P,F,Attachment
|  | Alignment with approved drawings and site plan | United Civil/CHINT Hold Point
| Calibration of Plant | All testing and measuring equipment calibration certificates valid | P,F,Attachment
| Site Clearing | Visual inspection of cleared area | P,F,Attachment
Free from vegetation, debris, and obstructions
Material Procurement
| Review of Concrete, and Reinforcement steel | Compliance with IFC Drawings, Specifications and Standards | P,F,Attachment
|  | All reinforcing bars shall be Grade 500MPa to AS/NZS 4671 | United Civil/CHINT Hold Point
All concrete construction shall be in accordance with NZS3109 and IFC Drawings
Concrete strength shall be 25MPa
Embeded threaded rods, nuts and washers shall all be M16, grade 8.8
Delivery Dockets supplied for each delivery/Pour
Construction - Excavation
| Excavation & Footing Construction | Visual Inspection of each footing location | P,F,Attachment
|  | Check that depth & dimensions comply with IFC Drawings | United Civil Hold Point
Bottom of foundation pad must be at least 350mm below ground level
Compacted hardfill pad 200mm thick of Gap40 under footing locations
Test acceptance to be a clegg test recorded to min of 24.
Construction - Concrete
| Formwork & Reinforcing Installation | Visual inspection of formwork and steel bar placement, cover and tying, alignment and cleanliness | P,F,Attachment
|  | 75mm Cover is maintained to ground and all formwork | United Civil/CHINT Hold Point
Compliance with IFC drawings; no gaps or damage and formwork set for finished level to be minimum of 20mm above finished ground level
Prepour Inspection completed for each pour
| Embedments | Visual inspection of all embedded items before and following pouring | P,F,Attachment
Positioning of anchor bolts or inserts is as per approved IFC Drawings
Hold Down Bolts dimensional check - min. 30mm from underside of plate to top of foundation & 220mm from embeded plate to top of threaded rod
Installed electrical ducting to have a 32mm duct for earthing & 2x 50mm ducts with 400mm radius extending 800mm below the finished foundation and 200mm above the foundation
Prepour Inspection
| Concrete Mixing | Verify Certified Batching Plant is used | P,F,Attachment
Concrete strength to be min of 25MPa
Concrete Mix Delivery Records
| Concrete Placement | Visual Inspection during pouring | P,F,Attachment
Proper compaction of poured concrete, no segregation or honeycombing
Each Pour
| Slump Test | Tests Taken in accordance with NZS3112.2 | P,F,Attachment
Slump Test Report
Delivery Dockets indicating slump
| Concrete Strength | Compression test on cylinders taken in accordance with NZS3112.2 | P,F,Attachment
|  | Meets and exceeds 25MPa at 28 day test | United Civil Hold Point
Test Report
Post Construction
| Curing | Visual Inspection of curing of concrete | P,F,Attachment
| Foundation Alignment | Check position and alignment of foundation | P,F,Attachment
Dimensional checks & compliance with tolerance in drawings
| Surface Finish | Visual Inspection of surface for cracks, voids, and finish quality | P,F,Attachment
No visible defects or honeycombing for each foundation
Post Construction and Handover
| Final Walkthrough & Inspection | Comprehensive inspection of all elements relating to the Light Pole Foundations | P,F,Attachment
|  | Compliance with IFC drawings and specifications | CHINT Hold Point
|  | Verify all Light Pole Foundations meet design and functional requirements | United Civil Hold Point
Light Pole Foundations ready for subsequent construction activities
| Non-Conformance-Reports | Each Non-Conformance Reported, Rectified & Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with Client and Contractor Representative Punch List closed out in a timely mannor | P,F,Attachment
| Documentation | On completion of the Light Pole foundations: | P,F,Attachment
|  | Submission of all test results, ITC's and any as-built drawings | United Civil Hold Point
Complete and approved by client