## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Light Pole Foundations | itp
section | Preconstruction
checkpoint | Design Drawings
label | Issued for Construction Drawings available
label | Drawing MSF-EN-ELE-DRG-070
holdpoint | United Civil Hold Point
checkpoint | Survey & Setout
label | Visual Inspection of Light Pole Location setout
label | Alignment with approved drawings and site plan
holdpoint | United Civil/CHINT Hold Point
checkpoint | Calibration of Plant
label | All testing and measuring equipment calibration certificates valid
checkpoint | Site Clearing
label | Visual inspection of cleared area
label | Free from vegetation, debris, and obstructions
section | Material Procurement
checkpoint | Review of Concrete, and Reinforcement steel
label | Compliance with IFC Drawings, Specifications and Standards
label | All reinforcing bars shall be Grade 500MPa to AS/NZS 4671
label | All concrete construction shall be in accordance with NZS3109 and IFC Drawings
label | Concrete strength shall be 25MPa
label | Embeded threaded rods, nuts and washers shall all be M16, grade 8.8
label | Delivery Dockets supplied for each delivery/Pour
holdpoint | United Civil/CHINT Hold Point
section | Construction - Excavation
checkpoint | Excavation & Footing Construction
label | Visual Inspection of each footing location
label | Check that depth & dimensions comply with IFC Drawings
label | Bottom of foundation pad must be at least 350mm below ground level
label | Compacted hardfill pad 200mm thick of Gap40 under footing locations
label | Test acceptance to be a clegg test recorded to min of 24.
holdpoint | United Civil Hold Point
section | Construction - Concrete
checkpoint | Formwork & Reinforcing Installation
label | Visual inspection of formwork and steel bar placement, cover and tying, alignment and cleanliness
label | 75mm Cover is maintained to ground and all formwork
label | Compliance with IFC drawings; no gaps or damage and formwork set for finished level to be minimum of 20mm above finished ground level
label | Prepour Inspection completed for each pour
holdpoint | United Civil/CHINT Hold Point
checkpoint | Embedments
label | Visual inspection of all embedded items before and following pouring
label | Positioning of anchor bolts or inserts is as per approved IFC Drawings
label | Hold Down Bolts dimensional check - min. 30mm from underside of plate to top of foundation & 220mm from embeded plate to top of threaded rod
label | Installed electrical ducting to have a 32mm duct for earthing & 2x 50mm ducts with 400mm radius extending 800mm below the finished foundation and 200mm above the foundation
label | Prepour Inspection
checkpoint | Concrete Mixing
label | Verify Certified Batching Plant is used
label | Concrete strength to be min of 25MPa
label | Concrete Mix Delivery Records
checkpoint | Concrete Placement
label | Visual Inspection during pouring
label | Proper compaction of poured concrete, no segregation or honeycombing
label | Each Pour
checkpoint | Slump Test
label | Tests Taken in accordance with NZS3112.2
label | Slump Test Report
label | Delivery Dockets indicating slump
checkpoint | Concrete Strength
label | Compression test on cylinders taken in accordance with NZS3112.2
label | Meets and exceeds 25MPa at 28 day test
label | Test Report
holdpoint | United Civil Hold Point
section | Post Construction
checkpoint | Curing
label | Visual Inspection of curing of concrete
checkpoint | Foundation Alignment
label | Check position and alignment of foundation
label | Dimensional checks & compliance with tolerance in drawings
checkpoint | Surface Finish
label | Visual Inspection of surface for cracks, voids, and finish quality
label | No visible defects or honeycombing for each foundation
section | Post Construction and Handover
checkpoint | Final Walkthrough & Inspection
label | Comprehensive inspection of all elements relating to the Light Pole Foundations
label | Compliance with IFC drawings and specifications
label | Verify all Light Pole Foundations meet design and functional requirements
label | Light Pole Foundations ready for subsequent construction activities
holdpoint | United Civil/CHINT Hold Point
checkpoint | Non-Conformance-Reports
label | Each Non-Conformance Reported, Rectified & Closed Out
checkpoint | Punch List
label | Development of Punchlist with Client and Contractor Representative
label | Punch List closed out in a timely mannor
checkpoint | Documentation
label | On completion of the Light Pole foundations:
label | Submission of all test results, ITC's and any as-built drawings
label | Complete and approved by client
holdpoint | United Civil Hold Point