## general
Inspection and Test Plan
Project: |  | Bay Road Foul Sewer Renewal CC1810 |  |  |  | R0: 04/08/25 | Role | Person(s) Responsible
Job nr |  | 25069 |  |  |  | R1: 22/08/25 | Project Engineer | Norbert Jacsek
Location: |  | Bay Road, Grasmere, Invercargill |  |  |  |  | Operations Manager | Bryan Duggan
Action |  | Witness | W | WCL | Wilson Contractors (2003) Ltd | Activity by | Contract Manager | Hamish Lindsay
|  | Hold Point | H | ICC | Invercargill City Council |  | ICC Engineers Representative | Tom Andersen
|  | Monitor | M | Lab / Sur | Independent testing agent / Registered surveyor |  | ICC Engineer | Rob Hayes
Print, sign and date
No | Contract Spec # | Inspection / Test Point | ACTION (W, M, H) | Activity by | Conformance Criteria (What's Required) | Quantity | Frequency / When? | Inspection / Test Method | Records / evidence, WCL form | Standard | Wilson | ICC
Contract
1 | D1.3 | Site Management Plan (QEHS, SSST, KSA) | H | WCL | Ensure Quality, Environment, Health & Safety Management Systems Plan Site Specific Safety Plan and Key Step Analysis are approved. Living document to be adjusted and updated as required. A copy of QEHS plan, SSSP and KSA to be on site at all times. |  | Prior to commencement | Submission (NTE) | Sign This ITP LN-01, FM-83, FM-69 | ICC STANDARD SPECIFICATIONS | YES | YES
2 | D1.18 | TMP | H | WCL | traffic management plan to be submitted and approved by Road Controlling Authority |  | Prior to commencement | Sumission (NTE) | Sign This ITP TMP | Code of practice for temporary traffic management (CoPTTM) | YES | YES
3 | D1.4 | Works Access Permit | H | WCL | TMP and Corridor Access Request to be sumbitted on myWorksites |  | Prior to commencement | Document | Sign This ITP WAP |  | YES | YES
4 |  | Permit to Enter | H | WCL | KiwiRail |  | Prior to any work near the railway area | Document | Permit to Enter |  | YES | YES
5 | D1.14 | Client start-up meeting | H | ICC, WCL |  |  | Prior to commencement | Document | Sign This ITP MoM | ICC STANDARD SPECIFICATIONS | YES | YES
6 | C1.8 D1.6 | NZ Heritage induction | H | WCL, ICC | Contractor briefing is to be completed by all personnel working on the project |  | 48 hours prior to any work | Induction | induction record | ICC STANDARD SPECIFICATIONS | YES | YES
Material
7 | D2.4.2 | Bedding material | H | Lab | Material to comply with contract specification | 650 m3 | Prior to installation | Lab report | Grading Results | ICC STANDARD SPECIFICATIONS G3 of AS/NZS 2566.2 | YES | YES
8 | D2.4.3 D1.29.3 | Sub Base Aggregate AP65 | H | Lab | Materials to comply with contract specification | 2500 m3 | Prior to installation | Lab report | MDD and Grading Results | ICC STANDARD SPECIFICATIONS | YES | YES
9 | D1.29.4 | Crushed Basecource Aggregate M/4 AP40 | H | Lab | Materials to comply with contract specification | 250 m3 | Prior to installation | Lab report | MDD and Grading Results | ICC STANDARD SPECIFICATIONS NZTA M/4 | YES | YES
10 | C1.4 D2.4.1 | Pipe material (F25402 - F25403) | H | WCL | DN300 uPVC SN16 RESTRAIN | 30 m | Prior to commencement | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS AS/NZS 1260:2017 | YES | YES
11 |  | Pipe material (F25403 - F25406) |  |  | DN300 uPVC SN8 | 328 m |  |  |  |  | YES | YES
12 |  | Pipe material (F25406 - F25410) |  |  | DN225 uPVC SN8 | 378 m |  |  |  |  | YES | YES
|  | Pipe material (ridermain connection) |  |  | Dn150 uPVC SN8 | 13 m |  |  |  |  | YES | YES
13 | D4.3 | Pipe material lateral |  |  | DN100 uPVC SN6 | 780 m |  |  |  |  | YES | YES
| D2.5 | Joints | H | WCL | Material to comply with contract specification |  | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS | YES | YES
14 | D18.2 | Precast manhole elements | H | WCL | min. 25 Mpa 1050 mm nominal diameter 150 mm lid (HO loading) | 11 | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS NZS 4058 NZS 3107 | YES | YES
15 | D15.2 | Manhole covers | H | WCL | Heavy Duty Ductile iron, HN-HO-72 hinged, 600 mm clear opening, gas seal | 11 | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS | YES | YES
16 | D15.2 Fig. D9 | Cleaning eye cover | H | WCL | Warrior Surface box clear opening of 380mm x 224mm | 1 | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS | YES | YES
17 | D11.4 | Membrane seal | H | WCL | CRS2 High Bitumen Content Emulsion Binder or Polymer Modified Emulsion Binder | 730 m (main) 700 m (lateral) | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS Other Binders will only be considered should the Contractors Design prove that it is as effective as or more effective than the specified binder for the given site. | YES | YES
18 | D2.8.3 D12.3.1 | Asphalt (carriageways) | H | WCL | mix type: DG10 80/100 penetration grade bitumen | 730 m (main) 700 m (lateral) | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS | YES | YES
19 | D13.3.4 | Asphalt (footpath) | H | WCL | mix type: DG7, 180/200 penetration grade bitumen | 58 x 1 m | Prior to installation | Material approval Document | Sign This ITP Data sheet | ICC STANDARD SPECIFICATIONS | YES | YES
20 |  | Removal of existing pipelines and manholes | M | WCL | Excavation will include the removal of existing redundant mains, manholes and property connections | 273 m D300 378 m D225 780 m D100 8 manholes | Continuous during excavation | Visual inspection Document | Sign this ITP Disposal register | ICC STANDARD SPECIFICATIONS | YES | YES
21 | C1.11 | Disposal of Surplus Materials | M | WCL | The Contractor shall dispose of any surplus materials in a safe and sustainable manner | 3500 m3 | Continuous during excavation | Document | Sign this ITP Disposal register | ICC STANDARD SPECIFICATIONS | YES | YES
Completion
22 | D17 | As-built information | H | WCL | Encountered Services Record Sheet Detailed Water Connection Sheet As-built drawings as per D17 |  | Following/during completion of works | Document | Sign This ITP DWCS, ESRS, As-built | ICC STANDARD SPECIFICATIONS KiwiRail specifications | YES | YES
23 |  | Works Completion Notice | H | WCL | KiwiRail + myWorksites | [5 empty] | YES | YES
24 |  | Site walkover | H | WCL, ICC | Snag list to be compiled, and completed |  | At Completion | Review | Sign This ITP SNAG List | ICC STANDARD SPECIFICATIONS | YES | YES
Wilsons Engineer |  |  |  |  | Wilsons Contract Manager |  |  | ICC Engineers Representative
Signed By : Norbert Jacsek |  |  |  |  | Accepted By : Hamish Lindsay |  |  | Accepted By : Tom Andersen
Signature: |  |  |  |  | Signature: |  |  | Signature:

## 1-10
Inspection and Test Plan | [9 empty] | Construction phases:
Project: |  | Bay Road Foul Sewer Renewal CC1810 |  |  |  | R0: 04/08/25 | Role | Person(s) Responsible | 1 | Ross - Drury (main)
Job nr |  | 25069 |  |  |  | R1: 22/08/25 | Project Engineer | Norbert Jacsek | 2 | Drury – Stobo (main)
Location: |  | Bay Road, Grasmere, Invercargill |  |  |  |  | Operations Manager | Bryan Duggan | 3 | Stobo – Tanner (main)
Action |  | Witness | W | WCL | Wilson Contractors (2003) Ltd | Activity by | Contract Manager | Hamish Lindsay | 4 | Tanner – Harvey (main)
|  | Hold Point | H | ICC | Invercargill City Council |  | ICC Engineers Representative | Tom Andersen | 5 | Harvey – Paterson (main)
|  | Monitor | M | Lab / Sur | Independent testing agent / Registered surveyor |  | ICC Engineer | Rob Hayes | 6 | Paterson – Cunningham (main)
[9 empty] | 7 | Cunningham - End (main)
[9 empty] | 8 | Paterson - End (lateral)
[9 empty] | 9 | Tanner - Paterson (ridermain)
[9 empty] | 10 | Drury - Tanner (lateral)
Print, sign and date
No | Contract Spec # | Inspection / Test Point | ACTION (W, M, H) | Activity by | Conformance Criteria (What's Required) | Quantity | Frequency / When? | Inspection / Test Method | Records / evidence, WCL form | Standard | Wilson | ICC
Pre Construction
1 | D1.5 | Pre-work site inspection | H | WCL | Video or photos near the construction zone to determine their pre construction condition. (landowners property, public area) |  | Prior to commencement | Inspection Document | Sign This ITP Video Photo | ICC STANDARD SPECIFICATIONS | YES | YES
2 | D1.18 | Temporary traffic management set up | H | WCL, ICC | Signs set up as per TMP, with a copy on site with STMS. TMP monitored for practicality. If changes are required these are to be agreed upon with the engineer. |  | Prior to commencement | Engineer's inspection Visual inspection Document | Sign This ITP TM Check daily on-site record Photo | ICC STANDARD SPECIFICATIONS CoPTTM | YES | YES
3 | D2.7.1 | Set out | W | ICC, WCL | Mark out of alignment for mains and laterals |  | Prior to commencement | Surface marking | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
4 | D1.8 | Protection and identification of other Services | H | WCL, asset owners | Mark out on site of all services. Services to be potholed for as per Wilsons company policy |  | Prior to commencement | Surface marking Visual inspection Potholing | Sign This ITP | ICC STANDARD SPECIFICATIONS Wilson's prior to excavate policy | YES | YES
5 | D1.11 D9.5 | Notification to residents and businesses | M | WCL | Letter drop / business visits |  | Prior to commencement (min. two working days prior to access restriction) | Document delivered | Sign This ITP Notification letter | ICC STANDARD SPECIFICATIONS | YES | YES
6 | D1.32.7 | Railway survey | M | WCL, SUR | survey monitoring for track settlement: 1 m increments along the track, 20 m either side of the work centreline, / 3 m of progress of the pipe’s installation under the track. |  | Before and after the works | Surveying | Survey record | KiwiRail Civil Specification Installation of Utility Structures on Railway Land (C-SP-AE-64322) | YES | YES
Foul Sewer renewal
7 | D2.7.2 | Excavation | M | WCL | The finished excavation surface shall be a smooth consistent surface at the appropriate grade. No tolerance on the excavation base level that reduces the depth of the bedding will be allowed. | 743 m main 780 m lateral | continuous | Visual inspection Levelling | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
8 | D2.7.2 | Subgrade inspection | M | WCL, ICC | To determine if improvements are required | 713 m | prior to placement of bedding | Visual inspection | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
9 | D2.4.2 | Free draining material | M | WCL | shelly gravel wrapped in a suitable geotextile up to 100 mm over the trench bed | max 713 m | continous, in accordance with observed groundwater conditions | Visual inspection | Sign This ITP NTE, NTC | ICC STANDARD SPECIFICATIONS Secific approval should be given by the Engineer | YES | YES
10 | C1.4 D2.4.1 | Pipe material | M | WCL, ICC | DN300 uPVC SN16 RESTRAIN DN300 uPVC SN8 DN225 uPVC SN8 DN150 uPVC SN8 DN100 uPVC SN6 | 30 m 323 m 377 m 13 m 780 m | prior to installation WCL and ICC are to inspect all deliveries | Visual inspection | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
11 | D2.7.3 D2.5.1 | Pipe installation open trench (main: F25402 - F25410) | M | WCL | +/- 30mm (horizontal) +/- 5mm (vertical) joints as per manufacturers specifications (lubrication, chamfering, whiteness marking, etc) | 713 m | continous (pipe laser) 1/20 m (independent optical level) | Visual inspection Using calibrated pipe laser Optical levelling | Sign this ITP Leveling record | ICC STANDARD SPECIFICATIONS manufacturers specifications | YES | YES
12 |  | Pipe installation (drilling) | M | WCL | The grade is to be continuously adjusted using the sonde with surface reference points. | 30 m | continous |  |  | Responsibility for any inaccuracy in the longitudinal grade lies with ICC. | YES | YES
13 | D4.4 Fig. D3 Fig. D4 Fig. D5 | Pipe installation (lateral) | M | WCL | grade: min 1:100 (with laser) min 1:60 (with dumpy level) Connection to the main: 45° reducing wye Concrete haunching: 25 MPa Connection at boundary: slip coupler/plumbqwik | 54 laterals | continous | Measurement Document | Sign this ITP Detailed Drainage Connection Sheet | ICC STANDARD SPECIFICATIONS | YES | YES
14 | D2.7.6 | Bedding - DN300 main (F25402 - F25406) | M | WCL, ICC | lb (depth below): min 100 mm lc (width beside): min 200 mm lo (depth above): min 150 mm compacted layers not exceeding ⅓ of the pipe OD | 323 m | continuous During compaction of bedding / pipe laying and prior to placement of subbase material | Measurement Levelling | Sign this ITP | AS/NZS 2566 table 4.2. | YES | YES
15 | D2.7.6 | Bedding - DN225 main (F25406 - F25410) | M | WCL, ICC | lb (depth below): min 100 mm lc (width beside): min 150 mm lo (depth above): min 150 mm compacted layers not exceeding ⅓ of the pipe OD | 377 m | continuous During compaction of bedding / pipe laying and prior to placement of subbase material | Measurement Levelling | Sign this ITP | AS/NZS 2566 table 4.2. | YES | YES
16 | D2.7.6 | Bedding (lateral) | M | WCL, ICC | lb (depth below): min 75 mm lc (width beside): min 100 mm lo (depth above): min 100 mm compacted layers not exceeding ⅓ of the pipe OD | 780 m | continuous During compaction of bedding / pipe laying and prior to placement of subbase material | Measurement Levelling | Sign this ITP | AS/NZS 2566 table 4.2. | YES | YES
17 | D18.2 | Manhole material (base, riser, lid, adjustment ring, cover, cleaning eye) | M | WCL, ICC | Base, riser: D1050, min. 25 Mpa Lid: 150 mm, HO loading Cover: Heavy Duty Ductile iron, HN-HO-72 hinged, 600 mm clear opening, gas seal cleaning eye: Warrior surface box | 11 | prior to installation WCL and ICC are to inspect all deliveries | Visual inspection | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
18 | D18 Fig. D12 | Manhole installation | M | WCL, ICC | Benching. Crossfall - 1 in 4 Opening: min 700 mm long full width of pipe Gritted starter and finisher Flexible joint located within 1 meter All joints to be sealed Neck depth < 350 mm, max 50 mm adjustment ring 25 Mpa in-situ concrete packing lid opening: towards main inlet | 11 | during and after installation | Visual inspection Measurement Levelling Document | Sign this ITP Manhole Inspection Sheet | NZS 3109:1997 | YES | YES
19 | Fig. D13 - D16 | Manhole cover installation | W | WCL, ICC | Cover levels to be adjusted to existing surface levels (+10mm, -0 mm) 25 Mpa concrete packing Hinge position: towards on-coming traffic | 11 | before surface reinstatement | Visual inspection Measurement | Sign this ITP | ICC STANDARD SPECIFICATIONS | YES | YES
20 | D15 Fig. D7 | Cleaning eye installation | W | WCL, ICC | Cover levels to be adjusted to existing surface levels (+10mm, -0 mm) perpendicular / parallel the road alignment. | 1 | before surface reinstatement | Visual inspection Measurement | Sign this ITP | ICC STANDARD SPECIFICATIONS | YES | YES
21 | D2.9.2 | Pressure test | H | WCL, ICC | Main + north side laterals Test length: as per table 6.1 AS/NZS 2566.2 pressure: 25kPa pressure loss < 7Kpa | 11 (mh - mh) + long side laterals independently | Following the completion of adjacent manholes and connecting laterals | Low pressure air test | Sign This ITP Pressure test report FM-119 | AS/NZS 2566:2:2002 6.4.2 | YES | YES
22 | D2.9.3 | CCTV Inspection and Cleaning | H | WCL | to confirm that the lines are free from debris and have no defects | 743 m D150 / D225 / D300 main | prior to the final surface reinstatement after successful pressure test | CCTV inspection | Sign this ITP CCTV survey | New Zealand Pipe Inspection Manual AS/NZS 2566:2 | YES | YES
Surface reinstatement
23 | D13 | Landscaping | W | WCL | The final surface in the berm area should match the existing levels | 54 laterals | following lateral installation | Visual inspection Levelling | Sign this ITP | ICC STANDARD SPECIFICATIONS | YES | YES
24 | D13.7 | Grass seeding | W | WCL | approved seed mixture, 35 g/m2 | 54 laterals | following landscaping | Visual inspection Document | Sign this ITP Blending docket | ICC STANDARD SPECIFICATIONS | YES | YES
25 | D2.7.7 | Subbase (AP65) compaction | H | WCL | Carriageway: 0.3 - 1.5 m deep: min 35 CIV > 1.5 m deep : min 25 CIV | 713 m (main) 780 m (lateral) | During installation, every 200 mm layers at 6 m intervals for all trenches in carriageway above main and connections | Clegg test | Sign This ITP Clegg Test Result Sheet | ICC STANDARD SPECIFICATIONS | YES | YES
26 | D2.11.5 | Subbase (AP65) compaction | H | WCL / Lab ICC | 95% compaction rate It is not required to complete NDM testing on connections | 713 m (main) | At pipe laying commencement and reconfirmed at 120 m intervals for open trench every 200 mm layers | NDM test (direct transmission) | Sign This ITP NDM Test Result Sheet | ICC STANDARD SPECIFICATIONS | YES | YES
27 | D2.7 | Basecourse (AP40) compaction | H | WCL / Lab ICC | minimum depth of 150 mm 98% compaction rate It is not required to complete NDM testing on connections | 713 m (main) | 1 / 20 m of trench including one test at the start and end of the trench | NDM test | Sign This ITP NDM Test Result Sheet | ICC STANDARD SPECIFICATIONS | YES | YES
28 | D2.8.3 | Trench reinstatement - marking out saw cutting | H | ICC, WCL | Engineers rep to mark out saw cutting required 150 mm overcuts 1 m rule | 713 m (main) 54 (lateral) | prior to sealing | Visual inspection, measurements | Sign This ITP Pre seal inspection record (FM-114) | ICC STANDARD SPECIFICATIONS National Code of Practise for Utility Operators' Access to Transport Corridors | YES | YES
29 | D2.7.7.2 | Basecourse (AP40) geometry | H | WCL, ICC | -5 mm +15 mm h = 45-65 mm (carriageways) h = 25-45 mm (footpath) | 713 m - main 54 - lateral 54x1.5 m - footpath | prior to sealing | Visual inspection String line / straight edge inspection | Sign This ITP Pre seal inspection record (FM-114) | ICC STANDARD SPECIFICATIONS NZTA B/2 | YES | YES
30 | D11.4.3 | Membrane Seal | H | WCL, ICC | Residual bitumen application rate: 2.0 l/m2 +/- 10%. (spray truck) ≥ 1.5 l/m2 (hand operated sprayer bar) It is not recommended to carry out sealing works when the shade air temperature is below 10°C. No sealing works shall continue after rain has started to fall. | 713 m - main 54 - lateral | prior to asphalting | Visual inspection | Sign This ITP, Delivery docket | ICC STANDARD SPECIFICATIONS | YES | YES
31 | D12.5 | Asphalt paving (carriageway) | H | WCL, ICC | trenches wider than 1.5 m shall be paver-laid unless approved otherwise by the Engineer. Mix type: DG10 5 mm from a 3 m straight edge laid longitudinally 5 mm from a 1 m straight edge laid transversely lips ≤ 5 mm (where it joins existing seal) | 713 m - main 54 - lateral | 1 / finished surface WCL and ICC are to inspect all deliveries | Post seal surface inspection | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
32 | D12.4.10 | Joint sealing | W | WCL, ICC | Where a joint is required to an existing asphalt / chipseal surface the Contractor is required to seal the joint with hot poured rubber bitumen. | 713 m - main 54 - lateral | 1 / finished surface | Visual inspection | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
33 | D13.6 | Asphalt paving (footpath) | H | WCL, ICC | 30 mm Footpaths and Surfaced Frontages 5mm above kerb edges, and flush with property vehicle accessways The gap under a 3m straight-edge placed longitudinally shall not exceed 5mm lips ≤ 3mm | 54 x 1.5 m | 1 / finished surface WCL and ICC are to inspect all deliveries | Visual inspection straight edge inspection | Sign This ITP, Delivery docket | ICC STANDARD SPECIFICATIONS | YES | YES
34 |  | Road markings | W | WCL, ICC | Reinstatement of the existing markings, RRPMs | 743 m | 1 / finished surface | Post seal surface inspection | Sign This ITP | ICC STANDARD SPECIFICATIONS | YES | YES
Notification to the Engineer should be a minimum of 2 working day prior to work being inspected
Wilsons Engineer |  |  |  |  | Wilsons Contract Manager |  |  | ICC Engineers Representative
Signed By : Norbert Jacsek |  |  |  |  | Accepted By : Hamish Lindsay |  |  | Accepted By : Tom Andersen
Signature: |  |  |  |  | Signature: |  |  | Signature: