## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP - Bay Road FS (General) | itp |  |  |  |  | ITP - Bay Road FS (General)
section | Contract
checkpoint | 1 - D1.3
label | Inspection / Test Point - Site Management Plan (QEHS, SSST, KSA)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Ensure Quality, Environment, Health & Safety Management Systems Plan Site Specific Safety Plan and Key Step Analysis are approved.
label | ○ Living document to be adjusted and updated as required. A copy of QEHS plan, SSSP and KSA to be on site at all times.
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Submission (NTE)
label | Records / evidence, WCL form - Sign This ITP, LN-01, FM-83, FM-69
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 2 - D1.18
label | Inspection / Test Point - TMP
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - traffic management plan to be submitted and approved by Road Controlling Authority
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Sumission (NTE)
label | Records / evidence, WCL form - Sign This ITP, TMP
label | Standard - Code of practice for temporary traffic management (CoPTTM)
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 3 - D1.4
label | Inspection / Test Point - Works Access Permit
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - TMP and Corridor Access Request to be sumbitted on myWorksites
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Document
label | Records / evidence, WCL form - Sign This ITP, WAP
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 4
label | Inspection / Test Point - Permit to Enter
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - KiwiRail
label | Frequency / When? - Prior to any work near the railway area
label | Inspection / Test Method - Document
label | Records / evidence, WCL form - Permit to Enter
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 5 - D1.14
label | Inspection / Test Point - Client start-up meeting
label | ACTION (W, M, H) - H
label | Activity by - ICC, WCL
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Document
label | Records / evidence, WCL form - Sign This ITP, MoM
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 6 - C1.8 D1.6
label | Inspection / Test Point - NZ Heritage induction
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Contractor briefing is to be completed by all personnel working on the project
label | Frequency / When? - 48 hours prior to any work
label | Inspection / Test Method - Induction
label | Records / evidence, WCL form - induction record
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
section | Material
checkpoint | 7 - D2.4.2
label | Inspection / Test Point - Bedding material
label | ACTION (W, M, H) - H
label | Activity by - Lab
label | Conformance Criteria (What's Required) - Material to comply with contract specification
label | Quantity - 650 m3
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Lab report
label | Records / evidence, WCL form - Grading Results
label | Standard - ICC STANDARD SPECIFICATIONS G3 of AS/NZS 2566.2
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 8 - D2.4.3 D1.29.3
label | Inspection / Test Point - Sub Base Aggregate AP65
label | ACTION (W, M, H) - H
label | Activity by - Lab
label | Conformance Criteria (What's Required) - Materials to comply with contract specification
label | Quantity - 2500 m3
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Lab report
label | Records / evidence, WCL form - MDD and Grading Results
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 9 - D1.29.4
label | Inspection / Test Point - Crushed Basecource Aggregate M/4 AP40
label | ACTION (W, M, H) - H
label | Activity by - Lab
label | Conformance Criteria (What's Required) - Materials to comply with contract specification
label | Quantity - 250 m3
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Lab report
label | Records / evidence, WCL form - MDD and Grading Results
label | Standard - ICC STANDARD SPECIFICATIONS NZTA M/4
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 10 - C1.4 D2.4.1
label | Inspection / Test Point - Pipe material (F25402 - F25403)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - DN300 uPVC SN16 RESTRAIN
label | Quantity - 30 m
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS AS/NZS 1260:2017
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 11 - C1.4 D2.4.1
label | Inspection / Test Point - Pipe material (F25403 - F25406)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - DN300 uPVC SN8
label | Quantity - 328 m
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS AS/NZS 1260:2017
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 12 - C1.4 D2.4.1 (1)
label | Inspection / Test Point - Pipe material (F25406 - F25410)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - DN225 uPVC SN8
label | Quantity - 378 m
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS AS/NZS 1260:2017
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 12 - C1.4 D2.4.1 (2)
label | Inspection / Test Point - Pipe material (ridermain connection)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Dn150 uPVC SN8
label | Quantity - 13 m
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS AS/NZS 1260:2017
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 13 - D4.3
label | Inspection / Test Point - Pipe material lateral
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - DN100 uPVC SN6
label | Quantity - 780 m
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS AS/NZS 1260:2017
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 13 - D2.5
label | Inspection / Test Point - Joints
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Material to comply with contract specification
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 14 - D18.2
label | Inspection / Test Point - Precast manhole elements
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - min. 25 Mpa
label | ○ 1050 mm nominal diameter
label | ○ 150 mm lid (HO loading)
label | Quantity - 11
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS NZS 4058, NZS 3107
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 15 - D15.2
label | Inspection / Test Point - Manhole covers
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Heavy Duty Ductile iron, HN-HO-72 hinged, 600 mm clear opening, gas seal
label | Quantity - 11
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 16 - D15.2 Fig. D9
label | Inspection / Test Point - Cleaning eye cover
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Warrior Surface box clear opening of 380mm x 224mm
label | Quantity - 1
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 17 - D11.4
label | Inspection / Test Point - Membrane seal
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - CRS2 High Bitumen Content Emulsion Binder or Polymer Modified Emulsion Binder
label | Quantity - 730 m (main), 700 m (lateral)
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS Other Binders will only be considered should the Contractors Design prove that it is as effective as or more effective than the specified binder for the given site.
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 18 - D2.8.3 D12.3.1
label | Inspection / Test Point - Asphalt (carriageways)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - mix type: DG10 80/100 penetration grade bitumen
label | Quantity - 730 m (main), 700 m (lateral)
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 19 - D13.3.4
label | Inspection / Test Point - Asphalt (footpath)
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - mix type: DG7, 180/200 penetration grade bitumen
label | Quantity - 58 x 1 m
label | Frequency / When? - Prior to installation
label | Inspection / Test Method - Material approval, Document
label | Records / evidence, WCL form - Sign This ITP, Data sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 20
label | Inspection / Test Point - Removal of existing pipelines and manholes
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Excavation will include the removal of existing redundant mains, manholes and property connections
label | Quantity - 273 m D300
label | ○ 378 m D225
label | ○ 780 m D100
label | ○ 8 manholes
label | Frequency / When? - Continuous during excavation
label | Inspection / Test Method - Visual inspection, Document
label | Records / evidence, WCL form - Sign this ITP, Disposal register
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 21 - C1.11
label | Inspection / Test Point - Disposal of Surplus Materials
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - The Contractor shall dispose of any surplus materials in a safe and sustainable manner
label | Quantity - 3500 m3
label | Frequency / When? - Continuous during excavation
label | Inspection / Test Method - Document
label | Records / evidence, WCL form - Sign this ITP, Disposal register
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
section | Completion
checkpoint | 22 - D17
label | Inspection / Test Point - As-built information
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Encountered Services Record Sheet
label | ○ Detailed Water Connection Sheet
label | ○ As-built drawings as per D17
label | Frequency / When? - Following/during completion of works
label | Inspection / Test Method - Document
label | Records / evidence, WCL form - Sign This ITP, DWCS, ESRS, As-built
label | Standard - ICC STANDARD SPECIFICATIONS KiwiRail specifications
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 23
label | Inspection / Test Point - Works Completion Notice
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - KiwiRail + myWorksites
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 24
label | Inspection / Test Point - Site walkover
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Snag list to be compiled, and completed
label | Frequency / When? - At Completion
label | Inspection / Test Method - Review
label | Records / evidence, WCL form - Sign This ITP, SNAG List
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | Signoff
note | Wilsons Engineer
note | Signed By : Norbert Jacsek
note | Wilsons Contract Manager
note | Accepted By : Hamish Lindsay
note | ICC Engineers Representative
note | Accepted By : Tom Andersen
signoff | Signature:
checklist | ITP - Bay Road FS (1-10 blocks) | itp |  |  |  |  | ITP - Bay Road FS (1-10 blocks)
section | Pre Construction
checkpoint | 1 - D1.5
label | Inspection / Test Point - Pre-work site inspection
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Video or photos near the construction zone to determine their pre construction condition. (landowners property, public area)
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Inspection, Document
label | Records / evidence, WCL form - Sign This ITP, Video, Photo
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 2 - D1.18
label | Inspection / Test Point - Temporary traffic management set up
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Signs set up as per TMP, with a copy on site with STMS. TMP monitored for practicality. If changes are required these are to be agreed upon with the engineer.
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Engineer's inspection, Visual inspection Document
label | Records / evidence, WCL form - Sign This ITP, TM Check daily on-site record, Photo
label | Standard - ICC STANDARD SPECIFICATIONS CoPTTM
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 3 - D2.7.1
label | Inspection / Test Point - Set out
label | ACTION (W, M, H) - W
label | Activity by - ICC, WCL
label | Conformance Criteria (What's Required) - Mark out of alignment for mains and laterals
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Surface marking
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 4 - D1.8
label | Inspection / Test Point - Protection and identification of other Services
label | ACTION (W, M, H) - H
label | Activity by - WCL, asset owners
label | Conformance Criteria (What's Required) - Mark out on site of all services. Services to be potholed for as per Wilsons company policy
label | Frequency / When? - Prior to commencement
label | Inspection / Test Method - Surface marking, Visual inspection, Potholing
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS Wilson's prior to excavate policy
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 5 - D1.11 D9.5
label | Inspection / Test Point - Notification to residents and businesses
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Letter drop / business visits
label | Frequency / When? - Prior to commencement (min. two working days prior to access restriction)
label | Inspection / Test Method - Document delivered
label | Records / evidence, WCL form - Sign This ITP Notification letter
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 6 - D1.32.7
label | Inspection / Test Point - Railway survey
label | ACTION (W, M, H) - M
label | Activity by - WCL, SUR
label | Conformance Criteria (What's Required) - survey monitoring for track settlement: 1 m increments along the track, 20 m either side of the work centreline, / 3 m of progress of the pipe’s installation under the track.
label | Frequency / When? - Before and after the works
label | Inspection / Test Method - Surveying
label | Records / evidence, WCL form - Survey record
label | Standard - KiwiRail Civil Specification Installation of Utility Structures on Railway Land (C-SP-AE-64322)
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
section | Foul Sewer renewal
checkpoint | 7 - D2.7.2
label | Inspection / Test Point - Excavation
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - The finished excavation surface shall be a smooth consistent surface at the appropriate grade. No tolerance on the excavation base level that reduces the depth of the bedding will be allowed.
label | Quantity - 743 m main, 780 m lateral
label | Frequency / When? - continuous
label | Inspection / Test Method - Visual inspection, Levelling
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 8 - D2.7.2
label | Inspection / Test Point - Subgrade inspection
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - To determine if improvements are required
label | Quantity - 713 m
label | Frequency / When? - prior to placement of bedding
label | Inspection / Test Method - Visual inspection
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 9 - D2.4.2
label | Inspection / Test Point - Free draining material
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - shelly gravel wrapped in a suitable geotextile up to 100 mm over the trench bed
label | Quantity - max 713 m
label | Frequency / When? - continous, in accordance with observed groundwater conditions
label | Inspection / Test Method - Visual inspection
label | Records / evidence, WCL form - Sign This ITP, NTE, NTC
label | Standard - ICC STANDARD SPECIFICATIONS Secific approval should be given by the Engineer
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 10 - C1.4 D2.4.1
label | Inspection / Test Point - Pipe material
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - DN300 uPVC SN16 RESTRAIN
label | ○ DN300 uPVC SN8
label | ○ DN225 uPVC SN8
label | ○ DN150 uPVC SN8
label | ○ DN100 uPVC SN6
label | Quantity - 30 m
label | ○ 323 m
label | ○ 377 m
label | ○ 13 m
label | ○ 780 m
label | Frequency / When? - prior to installation WCL and ICC are to inspect all deliveries
label | Inspection / Test Method - Visual inspection
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 11 - D2.7.3 D2.5.1
label | Inspection / Test Point - Pipe installation open trench (main: F25402 - F25410)
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - +/- 30mm (horizontal)
label | ○ +/- 5mm (vertical)
label | ○ joints as per manufacturers specifications (lubrication, chamfering, whiteness marking, etc)
label | Quantity - 713 m
label | Frequency / When? - continous (pipe laser), 1/20 m (independent optical level)
label | Inspection / Test Method - Visual inspection, Using calibrated pipe laser, Optical levelling
label | Records / evidence, WCL form - Sign this ITP, Leveling record
label | Standard - ICC STANDARD SPECIFICATIONS manufacturers specifications
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 12
label | Inspection / Test Point - Pipe installation (drilling)
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - The grade is to be continuously adjusted using the sonde with surface reference points.
label | Quantity - 30 m
label | Frequency / When? - continous
label | Standard - Responsibility for any inaccuracy in the longitudinal grade lies with ICC.
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 13 - D4.4 Fig. D3 Fig. D4 Fig. D5
label | Inspection / Test Point - Pipe installation (lateral)
label | ACTION (W, M, H) - M
label | Activity by - WCL
label | Conformance Criteria (What's Required) - grade: min 1:100 (with laser), min 1:60 (with dumpy level)
label | ○ Connection to the main: 45° reducing wye
label | ○ Concrete haunching: 25 MPa
label | ○ Connection at boundary: slip coupler/plumbqwik
label | Quantity - 54 laterals
label | Frequency / When? - continous
label | Inspection / Test Method - Measurement, Document
label | Records / evidence, WCL form - Sign this ITP, Detailed Drainage Connection Sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 14 - D2.7.6
label | Inspection / Test Point - Bedding - DN300 main (F25402 - F25406)
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - lb (depth below): min 100 mm
label | ○ lc (width beside): min 200 mm
label | ○ lo (depth above): min 150 mm
label | ○ compacted layers not exceeding ⅓ of the pipe OD
label | Quantity - 323 m
label | Frequency / When? - continuous, During compaction of bedding / pipe laying and prior to placement of subbase material
label | Inspection / Test Method - Measurement, Levelling
label | Records / evidence, WCL form - Sign this ITP
label | Standard - AS/NZS 2566 table 4.2.
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 15 - D2.7.6
label | Inspection / Test Point - Bedding - DN225 main (F25406 - F25410)
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - lb (depth below): min 100 mm
label | ○ lc (width beside): min 150 mm
label | ○ lo (depth above): min 150 mm
label | ○ compacted layers not exceeding ⅓ of the pipe OD
label | Quantity - 377 m
label | Frequency / When? - continuous, During compaction of bedding / pipe laying and prior to placement of subbase material
label | Inspection / Test Method - Measurement, Levelling
label | Records / evidence, WCL form - Sign this ITP
label | Standard - AS/NZS 2566 table 4.2.
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 16 - D2.7.6
label | Inspection / Test Point - Bedding (lateral)
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - lb (depth below): min 75 mm
label | ○ lc (width beside): min 100 mm
label | ○ lo (depth above): min 100 mm
label | ○ compacted layers not exceeding ⅓ of the pipe OD
label | Quantity - 780 m
label | Frequency / When? - continuous, During compaction of bedding / pipe laying and prior to placement of subbase material
label | Inspection / Test Method - Measurement, Levelling
label | Records / evidence, WCL form - Sign this ITP
label | Standard - AS/NZS 2566 table 4.2.
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 17 - D18.2
label | Inspection / Test Point - Manhole material (base, riser, lid, adjustment ring, cover, cleaning eye)
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Base, riser: D1050, min. 25 Mpa
label | ○ Lid: 150 mm, HO loading
label | ○ Cover: Heavy Duty Ductile iron, HN-HO-72 hinged, 600 mm clear opening, gas seal cleaning eye: Warrior surface box
label | Quantity - 11
label | Frequency / When? - prior to installation WCL and ICC are to inspect all deliveries
label | Inspection / Test Method - Visual inspection
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 18 - D18 Fig. D12
label | Inspection / Test Point - Manhole installation
label | ACTION (W, M, H) - M
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Benching. Crossfall - 1 in 4
label | ○ Opening: min 700 mm long full width of pipe
label | ○ Gritted starter and finisher
label | ○ Flexible joint located within 1 meter
label | ○ All joints to be sealed
label | ○ Neck depth < 350 mm, max 50 mm adjustment ring
label | ○ 25 Mpa in-situ concrete packing lid opening: towards main inlet
label | Quantity - 11
label | Frequency / When? - during and after installation
label | Inspection / Test Method - Visual inspection, Measurement, Levelling, Document
label | Records / evidence, WCL form - Sign this ITP, Manhole Inspection Sheet
label | Standard - NZS 3109:1997
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 19 - Fig. D13 - D16
label | Inspection / Test Point - Manhole cover installation
label | ACTION (W, M, H) - W
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Cover levels to be adjusted to existing surface levels (+10mm, -0 mm)
label | ○ 25 Mpa concrete packing
label | ○ Hinge position: towards on-coming traffic
label | Quantity - 11
label | Frequency / When? - before surface reinstatement
label | Inspection / Test Method - Visual inspection Measurement
label | Records / evidence, WCL form - Sign this ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 20 - D15 Fig. D7
label | Inspection / Test Point - Cleaning eye installation
label | ACTION (W, M, H) - W
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Cover levels to be adjusted to existing surface levels (+10mm, -0 mm) perpendicular / parallel the road alignment.
label | Quantity - 1
label | Frequency / When? - before surface reinstatement
label | Inspection / Test Method - Visual inspection Measurement
label | Records / evidence, WCL form - Sign this ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 21 - D2.9.2
label | Inspection / Test Point - Pressure test
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Main + north side laterals
label | ○ Test length: as per table 6.1 AS/NZS 2566.2
label | ○ pressure: 25kPa
label | ○ pressure loss < 7Kpa
label | Quantity - 11 (mh - mh), + long side laterals independently
label | Frequency / When? - Following the completion of adjacent manholes and connecting laterals
label | Inspection / Test Method - Low pressure air test
label | Records / evidence, WCL form - Sign This ITP, Pressure test report, FM-119
label | Standard - AS/NZS 2566:2:2002 6.4.2
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 22 - D2.9.3
label | Inspection / Test Point - CCTV Inspection and Cleaning
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - to confirm that the lines are free from debris and have no defects
label | Quantity - 743 m, D150 / D225 / D300 main
label | Frequency / When? - prior to the final surface reinstatement after successful pressure test
label | Inspection / Test Method - CCTV inspection
label | Records / evidence, WCL form - Sign this ITP, CCTV survey
label | Standard - New Zealand Pipe Inspection Manual AS/NZS 2566:2
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
section | Surface reinstatement
checkpoint | 23 - D13
label | Inspection / Test Point - Landscaping
label | ACTION (W, M, H) - W
label | Activity by - WCL
label | Conformance Criteria (What's Required) - The final surface in the berm area should match the existing levels
label | Quantity - 54 laterals
label | Frequency / When? - following lateral installation
label | Inspection / Test Method - Visual inspection, Levelling
label | Records / evidence, WCL form - Sign this ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 24 - D13.7
label | Inspection / Test Point - Grass seeding
label | ACTION (W, M, H) - W
label | Activity by - WCL
label | Conformance Criteria (What's Required) - approved seed mixture, 35 g/m2
label | Quantity - 54 laterals
label | Frequency / When? - following landscaping
label | Inspection / Test Method - Visual inspection, Document
label | Records / evidence, WCL form - Sign this ITP, Blending docket
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 25 - D2.7.7
label | Inspection / Test Point - Subbase (AP65) compaction
label | ACTION (W, M, H) - H
label | Activity by - WCL
label | Conformance Criteria (What's Required) - Carriageway:
label | ○ 0.3 - 1.5 m deep: min 35 CIV
label | ○ > 1.5 m deep : min 25 CIV
label | Quantity - 713 m (main), 780 m (lateral)
label | Frequency / When? - During installation, every 200 mm layers at 6 m intervals for all trenches in carriageway above main and connections
label | Inspection / Test Method - Clegg test
label | Records / evidence, WCL form - Sign This ITP, Clegg Test Result Sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 26 - D2.11.5
label | Inspection / Test Point - Subbase (AP65) compaction
label | ACTION (W, M, H) - H
label | Activity by - WCL / Lab, ICC
label | Conformance Criteria (What's Required) - 95% compaction rate
label | ○ It is not required to complete NDM testing on connections
label | Quantity - 713 m (main)
label | Frequency / When? - At pipe laying commencement and reconfirmed at 120 m intervals for open trench every 200 mm layers
label | Inspection / Test Method - NDM test (direct transmission)
label | Records / evidence, WCL form - Sign This ITP, NDM Test Result Sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 27 - D2.7
label | Inspection / Test Point - Basecourse (AP40) compaction
label | ACTION (W, M, H) - H
label | Activity by - WCL / Lab, ICC
label | Conformance Criteria (What's Required) - minimum depth of 150 mm
label | ○ 98% compaction rate
label | ○ It is not required to complete NDM testing on connections
label | Quantity - 713 m (main)
label | Frequency / When? - 1 / 20 m of trench including one test at the start and end of the trench
label | Inspection / Test Method - NDM test
label | Records / evidence, WCL form - Sign This ITP, NDM Test Result Sheet
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 28 - D2.8.3
label | Inspection / Test Point - Trench reinstatement - marking out saw cutting
label | ACTION (W, M, H) - H
label | Activity by - ICC, WCL
label | Conformance Criteria (What's Required) - Engineers rep to mark out saw cutting required
label | ○ 150 mm overcuts
label | ○ 1 m rule
label | Quantity - 713 m (main), 54 (lateral)
label | Frequency / When? - prior to sealing
label | Inspection / Test Method - Visual inspection, measurements
label | Records / evidence, WCL form - Sign This ITP, Pre seal inspection record (FM-114)
label | Standard - ICC STANDARD SPECIFICATIONS National Code of Practise for Utility Operators' Access to Transport Corridors
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 29 - D2.7.7.2
label | Inspection / Test Point - Basecourse (AP40) geometry
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - -5 mm +15 mm
label | ○ h = 45-65 mm (carriageways)
label | ○ h = 25-45 mm (footpath)
label | Quantity - 713 m - main
label | ○ 54 - lateral
label | ○ 54x1.5 m - footpath
label | Frequency / When? - prior to sealing
label | Inspection / Test Method - Visual inspection, String line / straight edge inspection
label | Records / evidence, WCL form - Sign This ITP, Pre seal inspection record (FM-114)
label | Standard - ICC STANDARD SPECIFICATIONS NZTA B/2
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 30 - D11.4.3
label | Inspection / Test Point - Membrane Seal
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Residual bitumen application rate:
label | ○ 2.0 l/m2 +/- 10%. (spray truck)
label | ○ ≥ 1.5 l/m2 (hand operated sprayer bar)
label | ○ It is not recommended to carry out sealing works when the shade air temperature is below 10°C.
label | ○ No sealing works shall continue after rain has started to fall.
label | Quantity - 713 m - main, 54 - lateral
label | Frequency / When? - prior to asphalting
label | Inspection / Test Method - Visual inspection
label | Records / evidence, WCL form - Sign This ITP, Delivery docket
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 31 - D12.5
label | Inspection / Test Point - Asphalt paving (carriageway)
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - trenches wider than 1.5 m shall be paver-laid unless approved otherwise by the Engineer.
label | ○ Mix type: DG10
label | ○ 5 mm from a 3 m straight edge laid longitudinally
label | ○ 5 mm from a 1 m straight edge laid transversely
label | ○ lips ≤ 5 mm (where it joins existing seal)
label | Quantity - 713 m - main, 54 - lateral
label | Frequency / When? - 1 / finished surface WCL and ICC are to inspect all deliveries
label | Inspection / Test Method - Post seal surface inspection
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 32 - D12.4.10
label | Inspection / Test Point - Joint sealing
label | ACTION (W, M, H) - W
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Where a joint is required to an existing asphalt / chipseal surface the Contractor is required to seal the joint with hot poured rubber bitumen.
label | Quantity - 713 m - main, 54 - lateral
label | Frequency / When? - 1 / finished surface
label | Inspection / Test Method - Visual inspection
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | 33 - D13.6
label | Inspection / Test Point - Asphalt paving (footpath)
label | ACTION (W, M, H) - H
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - 30 mm Footpaths and Surfaced Frontages
label | ○ 5mm above kerb edges, and flush with property vehicle accessways
label | ○ The gap under a 3m straight-edge placed longitudinally shall not exceed 5mm
label | ○ lips ≤ 3mm
label | Quantity - 54 x 1.5 m
label | Frequency / When? - 1 / finished surface WCL and ICC are to inspect all deliveries
label | Inspection / Test Method - Visual inspection straight edge inspection
label | Records / evidence, WCL form - Sign This ITP, Delivery docket
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
holdpoint | HOLD POINT
checkpoint | 34
label | Inspection / Test Point - Road markings
label | ACTION (W, M, H) - W
label | Activity by - WCL, ICC
label | Conformance Criteria (What's Required) - Reinstatement of the existing markings, RRPMs
label | Quantity - 743 m
label | Frequency / When? - 1 / finished surface
label | Inspection / Test Method - Post seal surface inspection
label | Records / evidence, WCL form - Sign This ITP
label | Standard - ICC STANDARD SPECIFICATIONS
label | Print, sign and date: Wilson - YES
label | Print, sign and date: ICC - YES
checkpoint | Signoff
note | Wilsons Engineer
note | Signed By : Norbert Jacsek
note | Wilsons Contract Manager
note | Accepted By : Hamish Lindsay
note | ICC Engineers Representative
note | Accepted By : Tom Andersen
signoff | Signature: