## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-020 - Exothermic Welding Rev2 | itp |  |  |  |  | ITP-020 - Exothermic Welding Rev2
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that all employees and contractors are using the most current and complete set of drawings
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.2 Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | • Ensure that all employees and contractors involved in the welding process have been inducted onto the relevant Hotworks permit
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.5 Materials Check
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure the materials and equipment gathered are for the correct type of connection being made. Inspect the mould ID tag to ensure that it corresponds to the application, indicated by the following parameters:
label | 1. Mould part number:
label | 2. Conductor size:
label | 3. Welding material required
label | • Check to ensure the graphite mould is not worn or broken, which could cause leakage of molten weld metal during the reaction.
label | • Ensure a working fire extinguisher is available within 10 metres of the working area.
label | REFERENCE DOCUMENTS: Eritech CADWELD Exothermic Welding Manual Fig. 2, 3, 4
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
section | Construction Works
checkpoint | 2.1 Preparation
label | FREQUENCY: Each Weld
label | ACCEPTANCE CRITERIA: Ensure the position of the conductors being welded is correct.
label | • Heat mould to ensure it is dry.
label | • Strip & clean conductors, ensure they are dry & clean.
label | REFERENCE DOCUMENTS: Design Drawings and Register
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.2 Welding
label | FREQUENCY: Each Weld
label | ACCEPTANCE CRITERIA: Ensure conductors are correctly positioned in the mould, allowing the mould to close tightly.
label | • Ensure welding material has been insected and is intact.
label | • Ensure reaction is completed and molten material has solidified (allow 30 seconds post ignition)
label | REFERENCE DOCUMENTS: Eritech CADWELD Exothermic Welding Manual Fig. 2, 3, 4
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
section | Testing
checkpoint | 3.1 Weld Review
label | FREQUENCY: Each lot
label | ACCEPTANCE CRITERIA: Ensure weld is inspected and that a quality connection has been made.All welds shall be inspected a Fulton Hogan engineer.
label | REFERENCE DOCUMENTS: Eritech CADWELD Exothermic Welding Manual Fig. 2, 3, 4
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | TP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
text | Date: