## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | ITP 001 - Ruddells Bund Construction | itp | ITP 001 - Ruddells Bund Construction | 4bbda6c4-3f6c-4d98-a089-3230a4ebc41b
| section | 1.0 Documentation
| checkpoint | 1.1 Construction Drawings
49338b9b-603f-5750-8da7-d900a897afd4 | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
0f33c498-eeac-59bf-bb60-2dd8ee13c5ef | note | Acceptance Criteria - Latest IFC Drawings
2eeb3371-de70-5e9c-b553-a7c9d9a2e53f | note | Inspection Responsibility: BCL - I
489979f0-79a4-5c1d-b725-aecb0211f879 | note | Inspection Responsibility: Client - S
adc4f627-3c27-5127-9995-6d047a001e7d | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
| checkpoint | 1.2 Concrete mix design
8fda91e0-3343-539c-953b-9c960211ba13 | note | Type of inspect / Test and Frequency - Submitted to Beca for approval
3280cab0-08cf-5a17-b880-3e0485bd97bf | note | Acceptance Criteria - Approved RFI
6e0c78c8-25b2-5c12-ac94-c1c1ee92f4fa | note | Inspection Responsibility: BCL - H
fe009713-17a7-5f00-8a02-346b9dc2ee32 | note | Inspection Responsibility: Client - A
e93b73b7-f8d8-5c7d-ab5d-473403e7e31b | note | Verification Records of Inspection(s) / Test(s) - RFI
| signoff | HOLD POINT
| section | 2.0 Fence Relocation/Swale works
| checkpoint | 2.1 Set Out, as per latest “For Construction” revision
8d216d12-ebf2-52db-9941-e4dd0084d64a | note | Type of inspect / Test and Frequency - Survey and mark the correct location, Check Boundary location
ae72fbd1-4995-5384-9389-0db4bac5d3c3 | note | Acceptance Criteria - IFC Drawings, Survey data check by PM and Beca Engineer
ec92cdf7-a8ce-5cd9-91f5-af4c9d9c7466 | note | Inspection Responsibility: BCL - D
0d7a548d-c7de-58d4-9d99-b2f3b6d3a508 | note | Inspection Responsibility: Client - A
480d629a-1b91-5602-861a-8ce4d409353d | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings, Approved RFI
| checkpoint | 2.2 Install new relocated fence to match existing
f2ab6be0-2eb4-5017-8417-440e99b7f032 | note | Type of inspect / Test and Frequency - New fence matches existing
b2364f1d-9e48-55a9-8bbe-d2351077f445 | note | Acceptance Criteria - Witness by engineer
b5a8574e-ea10-5a0d-ae72-a2384c50f23f | note | Inspection Responsibility: BCL - I
470ee3a1-3668-56b0-aab7-e13dcf80a755 | note | Inspection Responsibility: Client - R
20fd9f06-50d0-522c-95df-7b97254cd74d | note | Verification Records of Inspection(s) / Test(s) - Photos
| checkpoint | 2.3 Place rock riprap
28a42495-5711-5ab2-8ca9-ba311c8e00de | note | Type of inspect / Test and Frequency - 75-200mm size rock, 1m wide at top side to 1.5m wide at bottom end (inspected once at end of works)
8f3a4b0a-8630-5ba5-92ab-6c9c02bbd751 | note | Acceptance Criteria - Witness by Engineer
10a3749a-6ce7-5980-a8f4-19352196b59e | note | Inspection Responsibility: BCL - I
0a0f8211-bcea-59b8-ad2b-4b443b9d0c3e | note | Inspection Responsibility: Client - R
c0d3767c-640d-548a-9081-af5d8c147298 | note | Verification Records of Inspection(s) / Test(s) - Photos
| section | 3.0 Excavation
| checkpoint | 3.1 Set Out, as per latest “For Construction” revision
30c24d19-1bb6-50e9-9ffa-aa6554a99606 | note | Type of inspect / Test and Frequency - Survey and mark the bund location
6d655fd9-9cfd-500d-9c41-3c4f11160ce1 | note | Acceptance Criteria - IFC Drawings, Survey data check by PM
27ff986f-7541-5ac0-b6ca-3a6d20cc4ee8 | note | Inspection Responsibility: BCL - T
c21f1959-c822-5d7f-93c3-10e7df7a02e7 | note | Inspection Responsibility: Client - I
0ae3d889-1cff-5e5a-8a36-69604a739ba3 | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings
| checkpoint | 3.2 Subgrade inspection
e03cb1a4-dd6a-56a9-b367-2bfc56e5b2cb | note | Type of inspect / Test and Frequency - Scala testing to confirm subgrade is of sufficient strength
edb809a7-d20b-5dd7-8fea-5466e64e4646 | note | ○ Witness by engineer
af0d2e77-5277-5ee2-bd5a-db06489379c8 | note | ○ Minimum of 2 tests per bund pour
19f2513e-a220-5dd0-a1e8-7bf47bd17b0a | note | Acceptance Criteria - Minimum of 5 blows per 150mm
b75cd556-d1a3-5469-be43-309fa5a83691 | note | Inspection Responsibility: BCL - H
f7c64104-52a9-55ba-b4bb-d99c79275657 | note | Inspection Responsibility: Client - A
b47e83aa-99c1-52d0-98c3-76ade8ba1290 | note | Verification Records of Inspection(s) / Test(s) - Scala Test Results
| signoff | HOLD POINT
| checkpoint | 3.3 Ground Contaminants
aa240e7d-9037-5a1c-bacc-1b9a52276ba5 | note | Type of inspect / Test and Frequency - Soil testing to confirm no contaminants
a6233f80-d4fb-583a-8e29-ba45d5fac6cc | note | Acceptance Criteria - Test results clear for clean fill
7262bd7d-96ed-5532-85de-50f202d3e412 | note | Inspection Responsibility: BCL - T
ba0a2d74-dc4b-5392-9dbe-bde1eee38d03 | note | Inspection Responsibility: Client - R
c1bcf360-16ef-51ab-9f4c-d3cee6434194 | note | Verification Records of Inspection(s) / Test(s) - Lab test report
| section | 5.0 Post Excavation
| checkpoint | 5.1 >150mm compacted hard fill under bund (GAP20)
275c45a7-11de-5c63-aa68-f87b6f554837 | note | Type of inspect / Test and Frequency - Clegg hammer testing, 5x5 grid, minimum of 4no per bund pour
64aced04-f4dc-546e-a694-1a1004b7891d | note | Acceptance Criteria - Clegg CIV>10
488cb705-d559-5381-8909-de966841c8dd | note | Inspection Responsibility: BCL - T
c442dcf8-a65b-5d8e-a761-ce56aed97b13 | note | Inspection Responsibility: Client - R
caae07e0-8774-504b-ab85-2a715227b604 | note | Verification Records of Inspection(s) / Test(s) - Clegg results
| section | 6.0 Concrete works
| checkpoint | 6.1 Site concrete
9a8e3d85-22bd-5890-bd33-7ab7c343a4d4 | note | Type of inspect / Test and Frequency - Visual inspection and record of site concrete install, completed for each slab pour
a14c2e6f-ac68-5271-9508-554f0f153799 | note | Acceptance Criteria - 50mm site concrete poured to base level of foundation +0mm -10mm tolerance
ce97db2c-aded-520e-b2d0-d707846214cf | note | Inspection Responsibility: BCL - D
9df0e031-3f22-506a-a8b7-78123a107211 | note | Inspection Responsibility: Client - W
afb34cf2-1b5d-520e-ae8a-23f25131d92d | note | Verification Records of Inspection(s) / Test(s) - Photos Concrete pour record
| checkpoint | 6.2 DPM
cea33de3-cf67-5be3-a1c5-ba64822ad76b | note | Type of inspect / Test and Frequency - Visual inspection and record of DPM installed, completed prior to each pour
40c57e0e-b697-5e2f-b780-7ddc729b9165 | note | Acceptance Criteria - Polythene laid on site concrete prior to reinforcing
f978abde-61b8-5a35-aa12-69efd8010b87 | note | Inspection Responsibility: BCL - D
807c6134-35a2-59ac-a67e-af565c3af7ae | note | Inspection Responsibility: Client - W
4ae33cfc-7b90-56eb-9edf-4bfe701002f4 | note | Verification Records of Inspection(s) / Test(s) - Photos, Concrete pour record
| checkpoint | 6.3 Reinforcing (material)
0bfd40f2-e40c-57d9-9886-287b1590fa9f | note | Type of inspect / Test and Frequency - Review documentation for each pour
de3bfba9-3782-5bdb-a28d-ee0c6918365b | note | Acceptance Criteria - Reinforcing to be Grade 500E to ASS/NZS4671
3ad4b1d6-60f3-5dff-b80a-75b42f7d377a | note | Inspection Responsibility: BCL - D
b78dd33b-16d0-5403-9d8a-2cf97d5cf64d | note | Inspection Responsibility: Client - W
6fd56464-0240-51fc-8f75-f6b329142c0e | note | Verification Records of Inspection(s) / Test(s) - Mill certificates, Detail sheet
| checkpoint | 6.4 Sump Construction
f8c0184a-657e-5a09-8e9f-ad036e6982e6 | note | Type of inspect / Test and Frequency - Reinforcing check, dimension check, Formwork check
839cfe41-e569-5f23-8d73-15555db076e4 | note | Acceptance Criteria - As per IFC drawings
8f6be7f0-544d-50a8-8aab-347b61875f63 | note | Inspection Responsibility: BCL - D
7d0da8ef-0d9d-54e1-8abc-86db208e5938 | note | Inspection Responsibility: Client - W
7774fe3b-4be1-55ff-8525-7d4dadf38795 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 6.5 Reinforcing install
d64c2b18-0bd6-5e75-8bf4-9cf30ead9de7 | note | Type of inspect / Test and Frequency - Measure to check cover, bar size and arrangement, lap length and type.
5fba8004-0193-54c0-835c-6ebc2472b917 | note | ○ Complete prior to pouring concrete
8a743d71-fbd5-5a6c-a7b5-9cf6825dce5c | note | Acceptance Criteria - Reinforcing matches IFC drawings, any deviations recorded and acceptance agreed with engineer prior to pour
4c61fa24-b741-5834-a7d9-72d313bd55fd | note | Inspection Responsibility: BCL - D
4f63b391-ef01-54b3-b58c-684b77c604c4 | note | Inspection Responsibility: Client - W
3b40333e-9c01-5b82-a61f-a11d5223a71e | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
| checkpoint | 6.6 Reinforcing install
2b4e62c1-0d21-5ed0-83e2-e282f4a5a59b | note | Type of inspect / Test and Frequency - Starter bars for tank plinth Starter bars for blockwork
a24ade89-35b6-50ea-8e3a-7b7e67661204 | note | Acceptance Criteria - Matches IFC drawing
3c0cee4e-bffa-52bf-b59f-885684b19309 | note | Inspection Responsibility: BCL - D
df0a68b6-d756-5943-a5ba-4f56a38dbfca | note | Inspection Responsibility: Client - W
5e9fbfd2-6577-5bd1-9ade-aed636d72f19 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
| checkpoint | 6.7 Tank plinth
0f8d2fc1-9e32-50b9-bab8-93a3a281e240 | note | Type of inspect / Test and Frequency - Size of plinth, height of plinth, Reinforcing checked, Formwork checked
0ebdd446-e345-55ae-b1cf-db7810ee61e6 | note | Acceptance Criteria - Matches IFC drawing and response of RFI017
32d34ce1-9df0-50f4-9e51-fb16432440e9 | note | Inspection Responsibility: BCL - D
8df737e7-ca8b-52bc-bc99-de634d8ea6b6 | note | Inspection Responsibility: Client - W
0eb043d2-5465-529f-9959-03d8de51961b | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
| checkpoint | 6.8 Concrete pour
17ab1816-9142-5374-8cdf-dd74d6903dc6 | note | Type of inspect / Test and Frequency - Embedded items located in slab
51e5f633-5a00-5d31-bf32-451dbae32bc2 | note | – Ducting
1621cf9b-f86c-51eb-96e8-fdf1a546c483 | note | – Pits
52f3ca44-5394-52ec-abcb-21dd290de162 | note | Acceptance Criteria - Matches IFC drawings
c4cfccc1-e3f6-5d16-be7e-1f1034d962f7 | note | Inspection Responsibility: BCL - D
508ad425-2f8a-5b51-aaf3-1d93573daa26 | note | Inspection Responsibility: Client - W
ac4d2687-71ba-549e-a78b-fc4b3f70d4e2 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, photos
| checkpoint | 6.9 Concrete pour
7adc86b4-ad37-54cc-8f36-ebbfe7635072 | note | Type of inspect / Test and Frequency - Level check, formwork check, cover check.
66c84803-b3f9-5793-b38b-678d1cd05215 | note | ○ Inspections prior to every pour.
c360e48c-a12d-509a-b0f1-c18233064311 | note | Acceptance Criteria - Matches IFC drawing dimensions and notes
ead9f000-4b1f-5914-93e4-9183fbf0ba64 | note | Inspection Responsibility: BCL - D
d347c640-0cd4-5d83-bfa2-47ef44180d13 | note | Inspection Responsibility: Client - W
2ccb3a0b-cc5b-5175-904d-778d1b36dc4b | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 6.10 Pour inspection/Approval to pour
e63ea974-d541-588b-8a9f-13b4ec36180b | note | Type of inspect / Test and Frequency - Pre pour inspection by Beca Engineer (hold Point)
2bedb25b-77e9-55b0-8aae-159d7b9e0845 | note | Acceptance Criteria - Approval from Engineer to pour
faf8497c-65f7-55d7-b639-4fe6ce38220c | note | Inspection Responsibility: BCL - H
21639487-327d-5247-ac05-241decd0391d | note | Inspection Responsibility: Client - A
| signoff | HOLD POINT
| checkpoint | 6.10 Concrete strength
96cb4f5c-6f81-55ec-b1a0-28ed8846c80f | note | Type of inspect / Test and Frequency - Test certificate
797d4c78-d83f-569d-be9e-6133e208388f | note | ○ 7 and 2no 28day tests required for each pour day or per 70m3
64a33ba4-6b36-5ffe-9ac8-8a328459128d | note | Acceptance Criteria - 28 day compressive strength >40mPa
c5279139-23d3-5848-80e5-e640c860f20e | note | Inspection Responsibility: BCL - D
801fe12e-f41b-51a2-b458-4c76f1485708 | note | Inspection Responsibility: Client - R
4e84c90c-9c5e-5bf8-8c03-30721aa559a9 | note | Verification Records of Inspection(s) / Test(s) - Test certificate
| section | 7.0 Blockwork
| checkpoint | 7.1 Blockwork (material)
d46f18fe-3350-5d1f-ad51-64f2f37e728c | note | Type of inspect / Test and Frequency - Manufacturer documentation.
0d6ac1d4-a83c-5269-b3ea-e6206f9b8533 | note | ○ Required once prior to commencement of works
22d51f11-3df8-52bb-ad15-dc49ff5b055d | note | Acceptance Criteria - Masonry units meet AS/NZS4455
3cbaee21-13f7-501d-be88-f0d5b342e84e | note | Inspection Responsibility: BCL - D
9b81cf54-836a-52af-928c-3dbf0ed03497 | note | Inspection Responsibility: Client - R
973dcefb-021b-57dd-bacc-f454af942dda | note | Verification Records of Inspection(s) / Test(s) - Supplier documentation
| checkpoint | 7.2 Blockwork (reinforcing)
dbd706a3-aeef-520f-9b3a-9ab2a65a0541 | note | Type of inspect / Test and Frequency - Inspect bar size, placement, lap length and number (once per pour)
8b4939f7-3d59-55e1-a2ae-8d901507cd75 | note | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
b511e624-126c-56e1-8ac8-515478ae6cc2 | note | Inspection Responsibility: BCL - D
8d3b9575-c605-58bb-9542-6adef6cff52f | note | Inspection Responsibility: Client - R
4c0e65cf-5d9e-5dca-8d4d-d847383fb13e | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 7.3 Blockwork (pour)
e7d863f5-001b-5982-9011-3dc65e5c9ace | note | Type of inspect / Test and Frequency - Inspection prior to pour, check washout location, dimensions, line and level (once per pour)
b998acce-45d7-5a11-81c8-30c5ade26902 | note | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
3c81e1a4-09e4-57f3-bd5a-3d6c02e31638 | note | Inspection Responsibility: BCL - W
3d7e70c5-a58d-5884-ac92-e64d100b6532 | note | Inspection Responsibility: Client - A
c7a3f06b-8b47-5d15-a005-f9d62dfd369b | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 7.4 Concrete strength
4ef32a55-0e97-563e-a8e9-6ab1aa24de19 | note | Type of inspect / Test and Frequency - Test certificate
021bdbd8-23a3-5c08-80c7-b782c9dd0b1b | note | ○ 7 and 2no 28day tests required for each pour day
11b65fc1-3614-587b-a10d-aef380aaee59 | note | Acceptance Criteria - 28 day compressive strength >17.5mPa
8b0fd62e-b676-50fd-a874-82423d8f7555 | note | Inspection Responsibility: BCL - R
542d2bd6-58fb-50e3-9ec3-0f19708869d4 | note | Inspection Responsibility: Client - R
66756447-16ac-5536-bb14-2f429816de02 | note | Verification Records of Inspection(s) / Test(s) - Test certificate
| section | 8.0 Bund Liner
| checkpoint | 8.1 Pre lining check (post pour)
aaaf4652-fcc3-5648-8879-00a99f127aa9 | note | Type of inspect / Test and Frequency - Square edges on all corners
f6ed2896-9940-530b-9858-d70f5473cc2a | note | ○ Concrete surface cleaned – all excess grout/splatters removed
16e93868-a00b-5857-bf0e-591ac2f14c6d | note | Acceptance Criteria - Placon check
f7c5ee13-9026-5d03-95b8-2c4ea85db7fc | note | Inspection Responsibility: BCL - W
a30e8544-6341-5804-be24-f1d08d1183cf | note | Verification Records of Inspection(s) / Test(s) - Photos
| checkpoint | 8.2 Watertightness of bund
abff2b41-8915-587e-97ba-facd4712cfbe | note | Type of inspect / Test and Frequency - Flood test of bund
28a24bba-04ba-5873-9e15-bd5304c6e564 | note | Acceptance Criteria - No leak, Water stable over 3 days (taking into account for evaporation, wind)
bf8c3e97-6b66-5b0e-aab2-c6c763cbd55e | note | Inspection Responsibility: BCL - I
57d2ab4a-2e05-5d4e-aa5a-79566ba0f68e | note | Inspection Responsibility: Client - W
213f6069-5e06-522d-a7ef-1d469a8aa1e5 | note | Verification Records of Inspection(s) / Test(s) - Photos, drop in water height measurement
| section | 9.0 As-builts
| checkpoint | 9.1 Redline Drawings
7a47790c-521b-530d-8bd4-333746ea5558 | note | Type of inspect / Test and Frequency - Redline Civil Drawings Sets post construction
42f92486-1813-51f1-9ac3-3146a97e36c0 | note | Acceptance Criteria - N/A
12eb0021-2293-5463-9734-047b3ee16503 | note | Inspection Responsibility: BCL - D
3db41d1d-bcfc-5d8d-a5e6-e8534b4c1a73 | note | Inspection Responsibility: Client - R
f3f591e4-cf58-5b82-954f-2492e13f3dba | note | Verification Records of Inspection(s) / Test(s) - As built drawings
| checklist | ITP 002 - Ruddells Mechanical Installation | itp | ITP 002 - Ruddells Mechanical Installation | 35a97bc0-4b19-410e-a75d-d3c76bd00737
| section | 2.0 Documentation
| checkpoint | 2.1 Construction Drawings
bf87d416-a32b-57f0-b164-36f7d19bc1e6 | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
f0e2cb44-c617-5022-ae84-369dbeae036b | note | Acceptance Criteria - IFC drawings
b9398855-b269-5c56-800b-e1df119ac15c | note | Inspection Responsibility: BCL - I
fe5d0e20-e01d-5bc4-a18d-f09d0ff33216 | note | Inspection Responsibility: Client - S
8d52a008-eb4e-5583-81c8-112a641ac52b | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
| checkpoint | 2.2 Methodology
07628b18-a639-5e55-9b45-4c48e24e53e4 | note | Type of inspect / Test and Frequency - Approved construction plan & sequence drafted and briefed to all involved with activity prior to construction. Includes any isolation permits for tie ins.
6c71a079-0a2a-5ab0-81f4-4627b3725dd1 | note | Acceptance Criteria - Workpack Approved
8403241d-b4ab-500a-9a7e-1a2e274679e0 | note | Inspection Responsibility: BCL - S
0d84196b-5ebc-552c-a7ad-e7fc9c0d8b1b | note | Inspection Responsibility: Client - A
2641e880-460d-5422-9607-071f44f022b3 | note | Verification Records of Inspection(s) / Test(s) - Approved Workpack Isolation Permit
| section | 3.0 Manufacturing
| checkpoint | 3.1 Pipe & Pipe Fitting (Flanges, Elbows, Tees etc.)
b2283156-7ccc-5290-a65d-33a21752aca0 | note | Type of inspect / Test and Frequency - Confirm pipe and pipe fitting materials are correct; material grade, size, rating etc. on delivery
c59e04c4-71a4-56fe-828b-cd68b1137037 | note | Acceptance Criteria - Pipe Data Sheet, Supplier Packing Slips
a76573c4-656c-57d7-bea4-446c8080e78e | note | Inspection Responsibility: BCL - S
2ce9902f-256c-52c4-bac1-2a5118794525 | note | Inspection Responsibility: Client - I
4aeb5492-7286-5d59-bf01-273d416f560a | note | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
| checkpoint | 3.2 Nuts & Bolts
c9d6f6f0-475f-5a43-bd2b-15782f329292 | note | Type of inspect / Test and Frequency - Confirm nuts and bolt materials are stainless steel grade 316
b27d2471-ddbe-54ff-b36d-4c7dcdc13122 | note | Acceptance Criteria - Supplier Packing Slips
dafd6cb0-6765-56ba-adc4-e92133cb72b3 | note | Inspection Responsibility: BCL - S
5f5d7dce-a85a-5fad-b8c0-a6ea08cf50f6 | note | Inspection Responsibility: Client - I
663f59ff-fc66-5f81-aa78-d44f99ae8d38 | note | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
| checkpoint | 3.3 Consumables
f98a9d46-c035-5f8c-9bc9-45da40a2386b | note | Type of inspect / Test and Frequency - Confirm consumable materials are correct on delivery
17d39c12-da50-5f13-9711-5c992d434cea | note | Acceptance Criteria - Supplier Packing Slips
d419322b-02db-5fce-9611-53e843c8bac8 | note | Inspection Responsibility: BCL - S
1667f7d0-b3d0-5e6e-b781-015387391cdd | note | Inspection Responsibility: Client - A
85f37f86-4545-5485-b3d1-d5e7e0ace37f | note | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
| section | 4.0 Delivery, Storage & Handling
| checkpoint | 4.1 Delivery
94c6e187-2d30-5e24-9cdd-aeb8bde77f2f | note | Type of inspect / Test and Frequency - Check pipe materials, tanks, structural steel and dosing cabinets are undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery
62fd25cf-8972-510e-8759-b8e41393ee74 | note | Acceptance Criteria - N/A
0bb3027b-2202-528a-977d-565dd45ab292 | note | Inspection Responsibility: BCL - I
f81c7cca-d052-5fb5-8534-9db92b30290a | note | Inspection Responsibility: Client - I
eeb277a6-55b0-5829-a100-0b493fd375de | note | Verification Records of Inspection(s) / Test(s) - ITC-002
| checkpoint | 4.2 Storage
f935473c-3aca-5802-99be-26df9430f629 | note | Type of inspect / Test and Frequency - For project entirety store materials in clean environment, protected from external damage; cover flange faces, store off ground using pallets. Ensure materials are free from contaminants and foreign debris.
a187794c-9662-576b-bdd9-6e600ea6a36f | note | Acceptance Criteria - N/A
c4e7ffe0-2f86-5efd-8d11-84968dac69a8 | note | Inspection Responsibility: BCL - W
82cc053d-d586-5cdc-ac40-d84522b15705 | note | Inspection Responsibility: Client - I
ef882d23-dcdd-5d5b-b99b-5be896c53d55 | note | Verification Records of Inspection(s) / Test(s) - N/A
| checkpoint | 4.3 Handling
247330f0-de1d-572c-8277-3b2ebb3a30a6 | note | Type of inspect / Test and Frequency - Handle materials with care and with the correct equipment (gloves, slings etc.)
125ea9db-154d-5a94-8724-31e27cccd13b | note | Acceptance Criteria - N/A
dd79f3a3-f517-5896-9eee-07cd5345c03a | note | Inspection Responsibility: BCL - I
01544cde-ba70-5dbf-a4cb-bafb8cf08ed3 | note | Inspection Responsibility: Client - I
1f9041fa-602f-5c93-8c27-c93d76ee8f75 | note | Verification Records of Inspection(s) / Test(s) - N/A
| section | 5.0 Site Installation
| checkpoint | 5.1 Install Pipe Supports
0334d2ba-34fa-566a-b4c4-9fef66e833e5 | note | Type of inspect / Test and Frequency - Install pipe supports in the correct locations before pipe installation
c57459da-73d0-5b34-b193-28d017f729df | note | Acceptance Criteria - As per pipe manufacturer specifications
863e4e64-09fc-5376-89c9-97837ee992c4 | note | Inspection Responsibility: BCL - I
c0f63876-b23a-5ec2-a39a-34b7b831d571 | note | Inspection Responsibility: Client - I
8aed560c-e0d0-5aec-aac3-94923e5f13dc | note | Verification Records of Inspection(s) / Test(s) - Redline Drawings, ITC-02
| checkpoint | 5.2 Equipment Set-Out
09448f7c-6b2f-599d-8bab-26a2e1803715 | note | Type of inspect / Test and Frequency - Survey and mark the correct locations of all pipes, tanks, structures and equipment before installation
5b248e47-33f2-55c8-8824-aea3b41d746c | note | Acceptance Criteria - IFC Drawings
a7efdcda-7d2b-5ace-a7cc-25499303717e | note | Inspection Responsibility: BCL - I
a69ad78d-8a6c-5730-be9e-e948f4451fd6 | note | Inspection Responsibility: Client - I
3ede0344-110e-511c-b125-2641d0295405 | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings, ITC-02
| checkpoint | 5.3 Install Pipework
e58ed528-a7a2-51fd-bc73-7a1afc8d6d28 | note | Type of inspect / Test and Frequency - Install piping on the pipe supports during construction
84a54507-c196-5005-893e-826fedc3853e | note | Acceptance Criteria - IFC Drawings
98c7a1e9-dc4b-5fb9-ae87-f5be1bf339b2 | note | Inspection Responsibility: BCL - I
d6a1ec06-499a-5052-995a-1fa41f9c8acc | note | Inspection Responsibility: Client - I
703a90d7-beab-5526-83dc-cae58522d5a3 | note | Verification Records of Inspection(s) / Test(s) - ITC-02
| checkpoint | 5.4 Install Dose Tank
81ec58c2-3dce-5bc6-8e76-ec16b2a930d4 | note | Type of inspect / Test and Frequency - Install tank in correct location and orientation as specified in IFC mechanical layout drawings and tank manufacturers drawings
fd6a7e3c-7897-582e-ac29-f0d2a2ecda3d | note | Acceptance Criteria - IFC Drawings
23a8e8e2-136f-5492-b0ca-d3bb5bd6e2ef | note | Inspection Responsibility: BCL - I
4b174ce0-c5b6-51e8-ae10-11c11891f513 | note | Inspection Responsibility: Client - I
51e652ae-6d2b-5cdb-b5ee-72cf3e550d96 | note | Verification Records of Inspection(s) / Test(s) - ITC-02
| checkpoint | 5.5 Install Access Platform
8b9b90d8-cfe9-53f9-bc47-45f2b337f198 | note | Type of inspect / Test and Frequency - Install access platforms in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings
eeada1d3-80bb-5f5b-b9e4-fa7e00cff5fa | note | Acceptance Criteria - IFC Drawings
b0d809de-2d4d-59a9-96a2-d17277497e15 | note | Inspection Responsibility: BCL - I
6b2725b4-18ba-5c6e-807e-d54c75792507 | note | Inspection Responsibility: Client - I
20245821-a991-541e-88df-7d42dfe77f0a | note | Verification Records of Inspection(s) / Test(s) - ITC-02
| checkpoint | 5.6 Install Dosing Cabinet
d54d2cd3-4c7d-5309-a832-9a261725a1e1 | note | Type of inspect / Test and Frequency - Install cabinet in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings
782590be-1faf-5260-8f47-e911038ebe5c | note | Acceptance Criteria - IFC Drawings
8042530c-8b5a-527b-b0a9-c8af916f6a45 | note | Inspection Responsibility: BCL - I
371a37b6-9f44-54ea-a734-d82328cbbf3a | note | Inspection Responsibility: Client - I
363c6d6a-9f21-5b96-9ffd-6b1f73f733fe | note | Verification Records of Inspection(s) / Test(s) - ITC-02
| checkpoint | 5.7 Install Safety Shower
4de71a0c-d651-50fe-8ff6-ba972be6d02f | note | Type of inspect / Test and Frequency - Install safety shower in correct location as specified in IFC mechanical layout drawings
c8a6c1ae-2b6e-5c3a-98e5-adb4970969ae | note | Acceptance Criteria - IFC Drawings
9d5ba74a-a71e-534a-8487-a5352748862f | note | Inspection Responsibility: BCL - I
b433d8ce-4504-56de-9209-03d3f14215d7 | note | Inspection Responsibility: Client - I
69b6e230-d635-5ffe-aacf-af3949b6233f | note | Verification Records of Inspection(s) / Test(s) - ITC-02
| checkpoint | 5.8 Install new nozzles into Existing Raw Water Pipework
1de08fcb-faef-5a1e-af03-b29a389adce1 | note | Type of inspect / Test and Frequency - Hot tap into Raw water pipework for new Flow Switch and Fluoride Dose point at correct locations
7aef93f9-4fa8-510a-9c33-c3581e89d4e4 | note | Acceptance Criteria - IFC Drawings, Flow Switch O&M manual
11ca332d-9a3f-5a18-aabf-d8ba82435edd | note | Verification Records of Inspection(s) / Test(s) - ITC-02
| checkpoint | 5.9 Pressure Testing
bfc4d6a3-b4fd-5287-a396-49ef980666e8 | note | Type of inspect / Test and Frequency - All Fluoride dosing pipelines to be hydrotested 1.5 times the maximum working pressure for 15 minutes and inspected for leaks
73915b04-fa20-5979-9a44-f49daa827d7f | note | Acceptance Criteria - NZS 7643
4400f4ec-a2d2-5f9c-ad30-68e003cccc88 | note | Inspection Responsibility: BCL - W
ab5c71f3-866a-5d1f-ab43-ec278d950550 | note | Inspection Responsibility: Client - A
f4996c9d-c5bb-5869-9775-9c68b6ebd146 | note | Verification Records of Inspection(s) / Test(s) - Pressure Test Records
| section | 6.0 As-builts
| checkpoint | 6.1 Redline Drawings
a72a1876-3308-53f5-9233-efa425c8b8ce | note | Type of inspect / Test and Frequency - Redline P&ID Drawings and Mechanical Drawings Sets post construction
112e3db4-4b82-5394-b94b-7601bc271194 | note | Acceptance Criteria - N/A
4a7e964a-37ab-5a83-86bc-a63b9d7e24da | note | Inspection Responsibility: BCL - S
d503f6c0-7e9e-5743-945d-3b8429e0e77e | note | Inspection Responsibility: Client - A
9688de39-272b-59ad-9da1-4da787bb2bd0 | note | Verification Records of Inspection(s) / Test(s) - Redline Drawings Issued
| checklist | ITP 003 - Structural Steel | itp | ITP 003 - Structural Steel | 9a817ee9-29bb-4a36-9cfe-dd520b69e221
| section | 1.0 Documentation
| checkpoint | 1a Construction Drawings
b67b579b-08e9-5b01-b091-71dda0157ef9 | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
7a3841dd-3e01-5a8c-ac1c-f3b5e2a38275 | note | Acceptance Criteria - IFC Drawings
97f7f8ff-36a9-58ce-b465-4a74d1a04831 | note | Inspection Responsibility: BCL - I
2534d32d-f5d8-56d6-bbbf-53025882df23 | note | Inspection Responsibility: Client - S
adce0c16-53ec-5595-bbb3-c72e0ca61cc4 | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
| checkpoint | 1b Shop Drawings
74781f40-91e4-58ec-ba72-c2ee72ffad36 | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision. (hold Point)
10d95601-aa1d-5fbd-9b83-2790b8d61f05 | note | Acceptance Criteria - AISC Detailing for Steel Construction
d5ee86c9-b755-5ef7-8936-f684a85ebfe1 | note | Inspection Responsibility: BCL - H
9a09be82-fc5f-5714-b3fb-acdd55cfe886 | note | Inspection Responsibility: Client - A
56923599-2018-5349-9092-647a9eaa2bfc | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
| signoff | HOLD POINT
| section | 2.0 Manufacturing
| checkpoint | 2a Structural Steel
c9beee47-f1f5-5dda-aae4-0d435a2ca571 | note | Type of inspect / Test and Frequency - Confirm structural steel grade is correct
a693c76a-f3e1-5bf2-ada7-2793a482a797 | note | Acceptance Criteria - Sec. 19 4.15.1.1 Table 1. Materials
39a480b8-80e6-57b3-b054-628cd07aa043 | note | Inspection Responsibility: BCL - D
b1dc7899-a7fc-5caa-83cb-3c594de4df6e | note | Inspection Responsibility: Client - R
643195b7-f673-526b-808d-a8ef3d65a202 | note | Verification Records of Inspection(s) / Test(s) - Manufacturers Mill Certificates
| checkpoint | 2b Nuts, Bolts, & Washers
e3b7a973-d4ff-570c-b276-767d7021ef48 | note | Type of inspect / Test and Frequency - Confirm nuts, bolt and washer materials are hot dip galvanised
cf197d17-6c6c-50a9-9ee7-618d09ce29eb | note | ○ Approved stainless steel components must be Grade A4 (Austenitic 316) strength 70
a79ff392-89df-502e-890c-49ba3b5984e4 | note | Acceptance Criteria - AS 1214 IFC Shop Drawings Bill of Materials
b044cf10-e725-54b4-a7d4-95d44165d563 | note | Inspection Responsibility: BCL - D
4b9aa9ce-7416-55fc-934d-b71852ff6b74 | note | Inspection Responsibility: Client - R
79465dbf-5685-5c18-8abd-c6817f167d9f | note | Verification Records of Inspection(s) / Test(s) - Manufacturers Mill Certificates
| section | 3.0 Delivery, Storage & Handling
| checkpoint | 3a Delivery
0663b731-202b-59df-aca7-154388851055 | note | Type of inspect / Test and Frequency - Check structural steel is undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery
9b62d5ee-0412-52f7-9bf5-fa21e091cb41 | note | Acceptance Criteria - NZS 3404
381084f8-34b3-5a5b-a731-0d4daa170986 | note | Inspection Responsibility: BCL - D
89c596ca-44bd-5f78-83da-6c38e33b8cb3 | note | Inspection Responsibility: Client - R
509445d1-0365-5bbe-91c2-2514723ffb5b | note | Verification Records of Inspection(s) / Test(s) - Delivery Dockets Photos
| section | 4.0 Welding
| checkpoint | 4a Nominate Inspector
f224957e-c6d2-5cfd-8fc2-12c2fea5462f | note | Type of inspect / Test and Frequency - Employ approved independent Welding Inspector.
8063a093-a130-5dec-b60d-afcf81b88ad3 | note | ○ Submit two weeks before fabrication
7677c2e2-4ddc-5eed-a7e1-5951aa8875a9 | note | Acceptance Criteria - CBIP
cef84662-b28f-521e-8c30-c0ab0db0fb08 | note | Inspection Responsibility: BCL - S
627c6de6-6325-5ff8-8d1e-a68618d482b9 | note | Inspection Responsibility: Client - A
458ecbc8-5af1-5b2b-a112-490cbbb61fcf | note | Verification Records of Inspection(s) / Test(s) - N/A
| checkpoint | 4b Welder Qualifications
6dbe7b3e-6d73-5e8b-9b00-2df7549d9ac0 | note | Type of inspect / Test and Frequency - Ensure welders are competent and accredited to carry out welding activity prior to construction.
ab06b41e-a1fd-5c61-aa75-acfaf4868294 | note | Acceptance Criteria - ASME IX
5f28dd2b-774d-55d2-b4cc-1430540d3274 | note | Inspection Responsibility: BCL - I
3f82328a-a77b-5fd4-8bdc-2949ffe1545f | note | Inspection Responsibility: Client - I
56698b2b-31b7-5eb1-9a5f-f39d2e1618b6 | note | Verification Records of Inspection(s) / Test(s) - Welder Qualification Records
| checkpoint | 4c Weld Procedure
d095b31a-6383-5ff9-851a-ca1ed5ff4dc3 | note | Type of inspect / Test and Frequency - Ensure procedure is Code compliant to weld specification of applicable work being done
7616bd75-e438-54a6-82a9-e948df58734d | note | ○ All welds to be category GP unless category SP nominated
d8ab1382-c663-5175-bd95-d5c5ef2c5d38 | note | Acceptance Criteria - ASME IX
fcbe2135-1a83-5954-96d3-6993aeb70a48 | note | Inspection Responsibility: BCL - A
2bb3344e-d541-512a-8280-7d44d761756a | note | Inspection Responsibility: Client - I
ac7896b1-69d8-5412-9023-3911f26bd895 | note | Verification Records of Inspection(s) / Test(s) - Welding Procedure
| checkpoint | 4d Weld Inspection (Visual)
b3abc3f8-8175-51aa-959b-45ebc31693b3 | note | Type of inspect / Test and Frequency - The extent of Non-Destructive examination listed in Sec. 19 4.15.2.4
cd79b3ab-8c07-5eab-9ad5-95144065acc2 | note | Acceptance Criteria - ASME IX
bb32da98-6123-5e1b-8f44-bf2f1f6f7312 | note | Inspection Responsibility: BCL - I
63f09455-4517-58ac-8960-07e94debaae1 | note | Inspection Responsibility: Client - I
4084571a-3203-5116-9651-677c45e5c60a | note | Verification Records of Inspection(s) / Test(s) - Inspector report
| section | 5.0 Corrosion Protection
| checkpoint | 5a Nominate Inspector
183a1b3b-ee15-5104-b980-91e0917b933f | note | Type of inspect / Test and Frequency - Employ approved independent Painting Inspector
83f413b9-de15-5163-9936-1499ad8e3517 | note | Acceptance Criteria - CBIP
6bce3563-7fff-5509-afa4-ad162852e35b | note | Inspection Responsibility: BCL - D
224f1c2e-e785-577e-9d43-2d7695067634 | note | Inspection Responsibility: Client - R
c905b015-0ee5-5a18-9ea1-1fbd4108c254 | note | Verification Records of Inspection(s) / Test(s) - N/A
| checkpoint | 5b Preparation
a57fc077-8d3e-50fd-bc38-2f0da950f21f | note | Type of inspect / Test and Frequency - Thoroughly clean all surfaces of oil and grease with turpentine, not kerosene.
20ab367c-86b8-58f3-aa50-ace164909890 | note | ○ Visual Inspection
0e77d813-45ea-5851-8395-e97265c5ab7a | note | Acceptance Criteria - Sa 21/2 in S1S 055900
34596ca7-9d19-577c-bd19-e2a887756504 | note | Inspection Responsibility: BCL - D
9fafb592-c43c-58ab-a367-0e86e0b15428 | note | Inspection Responsibility: Client - R
b08962e9-8ee3-5d14-99b1-78c0f0255870 | note | Verification Records of Inspection(s) / Test(s) - Galvanising QA Package
| checkpoint | 5c Galvanising
854b0811-b3eb-53f7-b63c-7bc2f99c804c | note | Type of inspect / Test and Frequency - Apply Zinc coating by hot dip process to give coating weight of not less than 600g/m2
9e7110c4-8c64-562c-a301-82625af4091b | note | Acceptance Criteria - AS/NZS 4680
b4e754d2-5055-5c24-b189-827f689c941d | note | Inspection Responsibility: BCL - D
5cc6c635-932c-5591-a7bd-36436ac5e0a0 | note | Inspection Responsibility: Client - R
ea118955-6380-5020-87fc-6c4bfa338c90 | note | Verification Records of Inspection(s) / Test(s) - Galvanising QA Package
| checkpoint | 5d Galvanising Inspection
86d80fa6-05cb-5b9c-ad7a-13705977c65c | note | Type of inspect / Test and Frequency - Inspect for defects, misses, etc.
beb1174a-29d7-54d9-8162-67a06e05b6a8 | note | ○ Dry film thickness measurements and demonstration that film build up has been achieved
e760dfe8-21bb-5e62-a429-edcb17600f6b | note | Acceptance Criteria - AS3894
910e8523-de60-5988-8f05-44ebc8e716d4 | note | Inspection Responsibility: BCL - D
0b30708e-c459-5f82-92fb-77f352afb802 | note | Inspection Responsibility: Client - R
76fc4f10-5e45-5a3f-b911-e64a53f67cf8 | note | Verification Records of Inspection(s) / Test(s) - Galvanising QA Package Painting Inspector Report
| section | 6.0 Grouting
| checkpoint | 6a Grouting Mix
9546eca1-5676-5009-8935-a90b8596d959 | note | Type of inspect / Test and Frequency - 50MPa grout to be used, mixing as per the manufacturer spec
5325a99b-acac-5541-a06a-ea64b0a22def | note | Acceptance Criteria - NZS 3404
5c73ffc0-3f53-59e9-9050-3b5e430d928d | note | Inspection Responsibility: BCL - D
d51b3727-07ae-5e82-b525-37aef27be580 | note | Inspection Responsibility: Client - R
61c3b1b1-ea07-58b0-9249-ceb47e34ebac | note | Verification Records of Inspection(s) / Test(s) - Delivery docket
| section | 7.0 As-builts
| checkpoint | 7a Redline Drawings
770e2c1f-e92b-57af-a5e8-d00220bfc7ee | note | Type of inspect / Test and Frequency - Redline Structural Drawings Sets post construction
17b82f5e-3bca-5d03-bd49-16732d486620 | note | Acceptance Criteria - N/A
b9481f30-23bf-5c96-b818-71285b3cf585 | note | Inspection Responsibility: BCL - D
f013e141-cf3e-5de9-9bda-aab6a00e6259 | note | Inspection Responsibility: Client - R
45fabb00-6ddc-5602-a2fd-16e339ecfbcf | note | Verification Records of Inspection(s) / Test(s) - As-Builts
| checklist | ITP 006 - Duct Install | itp | ITP 006 - Duct Install | 5d8b1884-e64e-4664-915d-abccb38703b3
| section | 1.0 Documentation
| checkpoint | 1.1 Material approval
ee3ab39f-588d-5d12-b981-119acc8bd1c3 | note | Type of inspect / Test and Frequency - RFI cover the approval of the service ducts
c0cbc17e-ede4-58dc-bf35-682162931b12 | note | Acceptance Criteria - RFI response
7ef188a8-21fe-517b-8ecf-235a69d578f8 | note | Inspection Responsibility: BCL - D
d5465aac-4861-5968-8fca-995796faab02 | note | Inspection Responsibility: Client - A
272e031d-0090-5f8b-b104-13d620296fc3 | note | Verification Records of Inspection(s) / Test(s) - RFI
| checkpoint | 1.2 Service duct Order
ebf01d38-5937-5b8c-8b8d-18d83da7c708 | note | Type of inspect / Test and Frequency - Humes Drawings – HN-HO-72
bc556fce-f9a4-5e0a-91dc-11c58d546cd2 | note | Acceptance Criteria - Drawings
b67db67a-3368-533a-a8dd-d15491fbacc0 | note | Inspection Responsibility: BCL - D
025192ef-f24c-5c6c-a793-343b29b94f8b | note | Inspection Responsibility: Client - I
07b607e8-d7f9-5d6b-ac4b-46b13e243fa2 | note | Verification Records of Inspection(s) / Test(s) - Humes Drawings
| checkpoint | 1.3 Delivery docket
14621f08-ac0f-521a-841c-c12296087308 | note | Type of inspect / Test and Frequency - Confirmation that ducts delivered match RFI016 material approval
aeccfb25-8a6f-5c3e-8963-249d6e4abcb2 | note | Acceptance Criteria - Delivery docket
0baf211e-1d04-56c2-b5fe-275a514d15bf | note | Inspection Responsibility: BCL - D
1dadae54-be75-5a6d-bfdf-90dfa1b827f7 | note | Inspection Responsibility: Client - I
e284fdf8-3561-5152-a0f0-e72eb1a96479 | note | Verification Records of Inspection(s) / Test(s) - Delivery Docket
| section | 2.0 Install
| checkpoint | 2.1 Subgrade
a4de0ad5-af4a-5725-8e8f-f89e4fdc4acd | note | Type of inspect / Test and Frequency - Confirm uniform subgrade under the duct
1d74aba0-74ff-5dab-80ee-d0e67e0ff682 | note | Acceptance Criteria - Subgrade uniform, soft spots removed
1b57cb57-e8b9-5f30-8aef-78e656613426 | note | Inspection Responsibility: BCL - V
0d47a4db-4daf-542d-b42f-19892eb12ba4 | note | Inspection Responsibility: Client - I
b963132f-0f56-5ddc-8812-f190f5dcb16c | note | Verification Records of Inspection(s) / Test(s) - Photo of works
| checkpoint | 2.2 Bedding
5ee691b5-5c65-58f6-a2c4-53d268e0a2fb | note | Type of inspect / Test and Frequency - Prep and bedding, installed, levelled,
f4cf58b2-eee5-58e4-a151-cd15c1024d5b | note | Acceptance Criteria - Bedding levelled to avoid uneven loading on the ducts
a357e57b-415d-5bcc-a742-d40b73d21383 | note | Inspection Responsibility: BCL - V
600396aa-dd31-5625-8d3a-f424cde6e7a6 | note | Inspection Responsibility: Client - I
ef5336ae-809c-5426-8dad-c63b3961d614 | note | Verification Records of Inspection(s) / Test(s) - Photo of works
| checkpoint | 2.3 Duct Install
e3d63912-7e62-5ab7-9530-8a102db3cf16 | note | Type of inspect / Test and Frequency - Ducts installed and locked together, top level installed to string line to avoid any steps in top of channel
bbe4e5d4-581e-52b6-8ba0-5799eec21810 | note | Acceptance Criteria - No steps in top of channel
edec60de-f068-5e73-a764-c675fb011144 | note | Inspection Responsibility: BCL - V
6603963e-5e5c-560f-a371-bc516b5e3ad6 | note | Inspection Responsibility: Client - I
e5a0f863-cf9f-5350-be45-af3b6569e90f | note | Verification Records of Inspection(s) / Test(s) - Photo of works
| section | 3.0 As-builts
| checkpoint | 3.1 Redline Drawings
292b85fd-c003-5877-868a-fae388680632 | note | Type of inspect / Test and Frequency - Redline drawings of install
4154a47e-0118-5e72-84e9-3302b287f8aa | note | Acceptance Criteria - N/A
830966bf-1f79-596e-a375-4da2c10d332b | note | Inspection Responsibility: BCL - S
e56b8b52-3441-5445-a973-e66cffed3586 | note | Inspection Responsibility: Client - A
f144d053-2257-5ca3-9dc6-36fa866a122c | note | Verification Records of Inspection(s) / Test(s) - Redline Drawings Issued
| checkpoint | 3.2 Survey
da604390-1211-5971-bd05-fbe3f390fc7d | note | Type of inspect / Test and Frequency - GPS coordinates of duct install
f90e9f29-e79c-52a2-96d0-f07dc1aac3f1 | note | Acceptance Criteria - N/A
f6feab7f-c142-5388-bd4f-7cc39e5e55c4 | note | Inspection Responsibility: BCL - S
5dec842d-02a6-5123-b02b-cfa2c7307de0 | note | Inspection Responsibility: Client - A
099fdb21-3cc1-5159-9888-28119d00a04e | note | Verification Records of Inspection(s) / Test(s) - GPS coordinates marked up on drawing
| checklist | ITP 007 - Kerb and Bund Works | itp | ITP 007 - Kerb and Bund Works | 7bc2f48b-be5f-4479-8d72-c98016c5828e
| section | 1.0 Documentation
| checkpoint | 1.1 IFC drawings
dc767edf-0b29-5f9c-8051-5272965c84ca | note | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
cc1681a0-a8ea-5dfe-995d-8292a712a9dd | note | Acceptance Criteria - Approved IFC/RFI responses
7c54ec8d-76b2-5cdc-92e9-c736526aa1e7 | note | Inspection Responsibility: BCL - D
d161aef2-361b-54e4-b1ee-eef0d9184403 | note | Inspection Responsibility: Client - A
ea0f1cc0-cbe4-5366-8180-020a33cd0ebd | note | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
| checkpoint | 1.2 Material compliance
c3864a5b-1449-5523-8349-57281ad812e7 | note | Type of inspect / Test and Frequency - Material compliance prior to works – GAP40, GAP20
7f8db901-1f7c-55de-83cb-2476faacdc0b | note | Acceptance Criteria - Quary test certificates
c7816fb6-0028-57f2-b948-a7afa5c91919 | note | Inspection Responsibility: BCL - D
6baa541e-bd0e-535c-9c9f-e60ce003d7d2 | note | Inspection Responsibility: Client - A
e238dede-61c3-5c3e-9d0c-8005521da9b3 | note | Verification Records of Inspection(s) / Test(s) - Quary test certificates
| checkpoint | 1.3 Reinforcing
38ec6aee-cc45-5bae-bc19-de3befa0edf5 | note | Type of inspect / Test and Frequency - Documentation review
53d39489-efa8-5250-8109-7728b614f8e4 | note | Acceptance Criteria - Mill Certs
a9809306-8638-56fb-9894-99f7f1c71c3e | note | Inspection Responsibility: BCL - D
1abcd14c-b39f-5bdd-b8e0-740bc9525c67 | note | Inspection Responsibility: Client - A
c51b5aca-546d-53b0-923e-38b7a1b516fa | note | Verification Records of Inspection(s) / Test(s) - Mill certs
| section | 2.0 Construction - Kerb
| checkpoint | 2.1 Excavation
c1caf4bc-9301-5dec-ac9a-6aa46cca9b51 | note | Type of inspect / Test and Frequency - Subgrade checked and uniform
3e6abb60-ee1f-55e4-a57f-091b855c9dc2 | note | Acceptance Criteria - Subgrade uniform
dc50862d-df82-54b3-b40d-e7573ebd4a23 | note | Inspection Responsibility: BCL - V
1f0bc053-d97a-54a0-a4ba-11bcbcd43f08 | note | Inspection Responsibility: Client - I
a1f53241-50e0-5b29-aad2-de6b747d462f | note | Verification Records of Inspection(s) / Test(s) - Photos
| checkpoint | 2.2 Bedding
3d571bcf-c042-5b66-9632-6a63e13ad8b5 | note | Type of inspect / Test and Frequency - Prep and bedding, installed, levelled,
a8e989ba-55c2-5290-9210-3522e51c1ec1 | note | Acceptance Criteria - Level 100mm of bedding under kerb
915a715b-faba-528b-b1cd-255c5ecafa98 | note | Inspection Responsibility: BCL - V
8014e555-e93a-58ab-a4f7-64b03de89a3e | note | Inspection Responsibility: Client - I
ed825f88-fad6-5130-bd18-961e7d44aa12 | note | Verification Records of Inspection(s) / Test(s) - Photos
| checkpoint | 2.3 Reinforcing
2956f5b2-f36b-52bc-8ed2-e6221b8ea612 | note | Type of inspect / Test and Frequency - Bars installed at 400mm centres, top of hook checked for cover to top of concrete
92e769ec-7401-5eb6-a0c5-adbc2dcdae86 | note | Acceptance Criteria - Visual inspection, String out the TOC
1f5e9db5-215f-5a0a-81a2-9c027391748b | note | Inspection Responsibility: BCL - V
438fef78-2e36-5826-8062-8d18c12ce2dc | note | Inspection Responsibility: Client - I
d8f83b56-1537-51dc-9cfb-1ac42ed6a130 | note | Verification Records of Inspection(s) / Test(s) - Photo
| checkpoint | 2.4 Concrete
7357f322-9869-5c1f-928a-6a53447fb98a | note | Type of inspect / Test and Frequency - Delivery docket checked, once per pour. Concrete strength verified.
5bbc344b-84e1-551d-b1a3-f2ac893b8b1c | note | Acceptance Criteria - 20MPA concrete installed, level checked
261cb615-ff25-5c34-846e-0567afd6d779 | note | Inspection Responsibility: BCL - D
875228cd-ed42-5394-a160-5e76d116cc99 | note | Inspection Responsibility: Client - I
31a26a7c-b8df-58e2-9e77-61aba32c102c | note | Verification Records of Inspection(s) / Test(s) - Delivery docket, Concrete crushing strength verified
| section | 3.0 As-builts
| checkpoint | 3.1 Excavation
96bf89a7-619b-5387-868c-829ea6694689 | note | Type of inspect / Test and Frequency - Subgrade checked and uniform
6ad59e59-b5be-5cad-b363-23425344e224 | note | Acceptance Criteria - Subgrade uniform
682e3c3d-db24-5ddf-b5d6-b7513b9cd414 | note | Inspection Responsibility: BCL - V
9530dac3-e5b1-581a-b6fb-9d9081628785 | note | Inspection Responsibility: Client - I
46a2f89f-94a3-5552-ba9b-69dae4718ff7 | note | Verification Records of Inspection(s) / Test(s) - Photos
| checkpoint | 3.2 Bedding
619b6d42-851f-52be-9094-7463c0d0adb4 | note | Type of inspect / Test and Frequency - Prep and bedding, installed, levelled,
947e8329-0708-5315-8c0b-983023fef3d5 | note | Acceptance Criteria - Level 100mm of bedding under kerb
888cf871-9f44-5a3c-bb14-c89259e4152b | note | Inspection Responsibility: BCL - V
5b22b2af-18d4-541c-a063-de57afcb6542 | note | Inspection Responsibility: Client - I
b9dd8e41-2aad-5656-b2ce-8f5de19d92ec | note | Verification Records of Inspection(s) / Test(s) - Photos
| checkpoint | 3.3 Reinforcing
cdab7cd3-1544-5445-a574-5e586b3ad65b | note | Type of inspect / Test and Frequency - Bars installed at 400mm centres, top of hook checked for cover to top of concrete
2a6f2f9e-9767-511a-97f6-98d0621f944e | note | Acceptance Criteria - Visual inspection, String out the TOC
cd2a51a3-f6ae-5efc-96c0-eaa7702b1322 | note | Inspection Responsibility: BCL - V
2d4e13cc-ed7f-5392-bcf6-2bc10941ecc8 | note | Inspection Responsibility: Client - I
90474fb7-83de-5e1b-b8ab-8922080a5bfb | note | Verification Records of Inspection(s) / Test(s) - Photo
| checkpoint | 3.4 Concrete
e0f7cb3c-83ad-5b3f-9057-16e810caad24 | note | Type of inspect / Test and Frequency - Delivery docket checked, once per pour. Concrete strength verified.
38b2ed43-66a9-5fd8-9e34-607dd1dacc24 | note | Acceptance Criteria - 20MPA concrete installed, level checked
14f550ff-05f6-5cc6-aad4-59a30d33eb03 | note | Inspection Responsibility: BCL - D
f19fbc5c-7bd2-55dd-be1f-3bd315b549bc | note | Inspection Responsibility: Client - I
06dc565f-3ca6-57f0-a036-c96843dbffe9 | note | Verification Records of Inspection(s) / Test(s) - Delivery docket, Concrete crushing strength verified
| section | 4.0 Asbuilt
| checkpoint | 4.1 Redline drawings
008980a4-db0e-59eb-a707-1c47d4c54c0d | note | Type of inspect / Test and Frequency - Complete as built redline drawings of works once complete
cc6ed880-0706-5b9d-ab25-293206960b82 | note | Acceptance Criteria - Redline drawings capturing changes
a450b0be-1804-590b-a0d9-f155977f29f6 | note | Inspection Responsibility: BCL - D
c558546a-bf1b-58ac-9b41-b48c515461db | note | Inspection Responsibility: Client - A
20206f0e-08c7-50f7-be78-e7d0d2c36181 | note | Verification Records of Inspection(s) / Test(s) - Redline drawings
| checklist | ITP 008 - Bund Liner Fabrication & Installation | itp | ITP 008 - Bund Liner Fabrication & Installation | b212975b-c921-4db8-8f14-ac5c58e331d4
| section | 1.0 Documentation
| checkpoint | 1.1 IFC drawings
fe759bbd-07cb-5d6d-aecc-0d5268004f8e | note | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
48771e88-e838-5eea-b7ae-6d14de56ad5f | note | Acceptance Criteria - Approved IFC/RFI responses
a3442b8c-52fa-594e-b8ad-f5bbeb58fb81 | note | Inspection Responsibility: BCL - D
5572a5c4-47c3-57ef-abcc-68f295f8b18e | note | Inspection Responsibility: Client - A
a07d4424-c280-5d7d-acfc-9ca794f92fc6 | note | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
| checkpoint | 1.2 Design Report complete
c4a0be49-c326-5608-bf08-ca8547888f9f | note | Type of inspect / Test and Frequency - Design report from fabricator
9d89aa88-148c-50d3-bfd3-7c2995991cf4 | note | Acceptance Criteria - Design report from fabricator
b5a23116-2480-5d40-ba88-45289fcdef69 | note | Inspection Responsibility: BCL - D
e52e93c2-a16b-53e9-ae40-e3b091fd3e72 | note | Verification Records of Inspection(s) / Test(s) - Upload design report
| section | 2.0 Construction
| checkpoint | 2.1 Tank Construction
14ce1e9d-881e-5784-9e14-89f389f952c0 | note | Type of inspect / Test and Frequency - PE Tank fabricated by approved/competent fabricator
1b581d6b-1f03-5120-9861-82f8bee386d4 | note | Acceptance Criteria - Visual inspection
de3994c8-ee3c-5a16-a41a-3a37f641fefd | note | Inspection Responsibility: BCL - D
9defb522-a70b-5786-90f4-7944e2cb5359 | note | Verification Records of Inspection(s) / Test(s) - Upload tank construction documentation from Placon. Photos.
| section | 3.0 Testing
| checkpoint | 3.1 Leak test tank
502cc4cc-e42c-5680-9da7-0be25ecb8317 | note | Type of inspect / Test and Frequency - Fill to overflow level, hold for 24 hours. No level change, no visual leaks
4c5f78cb-2545-5b25-b37f-0c9fa980ca3a | note | Acceptance Criteria - Leak Test passed
45e6bd43-46b4-5098-9bea-2e09a8b623ad | note | Inspection Responsibility: BCL - T
4a11fb9a-10ee-5713-afd0-131f1a9daa4a | note | Verification Records of Inspection(s) / Test(s) - Upload Leak Test report
| checkpoint | 3.2 Spark test tank
b09c4916-0eeb-5e53-91a0-72cba9e6d6c1 | note | Type of inspect / Test and Frequency - Spark test all welds
5b1e7e74-c98d-5661-9d6f-c3c94f08abae | note | Acceptance Criteria - Spark Test passed
60a1c245-fcb4-5c88-953a-e0beb7b7b42e | note | Inspection Responsibility: BCL - T
2cb775fa-dded-5058-841e-7663eeebca47 | note | Verification Records of Inspection(s) / Test(s) - Upload Spark test report
| section | 4.0 Certification
| checkpoint | 4.1 Stationary Container Tank Compliance Certificate
bc858bef-701a-56b3-9736-fffdb6d6f1c8 | note | Type of inspect / Test and Frequency - Worksafe authorised certifier to provide compliance certificate
a29913dc-b606-536d-875e-70120a78c5d8 | note | Acceptance Criteria - Compliance certificate
46ac0504-df0f-55fe-ab82-037f5a1ce473 | note | Inspection Responsibility: BCL - D
cdc163ce-f8c4-5b30-a936-53ca1cd235bd | note | Verification Records of Inspection(s) / Test(s) - Upload certificate
| checklist | ITP 009 - PE Tank Fabrication | itp | ITP 009 - PE Tank Fabrication | 87f8aac4-81a5-463f-bd10-ecc2ad035cd3
| section | 1.0 Documentation
| checkpoint | 1.1 IFC drawings
8fe94dec-60b8-533d-a7e9-de23524e8c4f | note | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
984a34d7-8a17-546c-aeba-8124718012b3 | note | Acceptance Criteria - Approved IFC/RFI responses
7006edd7-a6ff-5cab-9629-a566914c5f49 | note | Inspection Responsibility: BCL - D
3cf41d9c-e36e-5471-b44a-1771582ea35d | note | Inspection Responsibility: Client - A
4d82abf5-b91b-5b73-9fb2-49b92ecb26b8 | note | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
| checkpoint | 1.2 Design Report complete
35fbd46f-2967-5a31-bcdf-4fefe471e828 | note | Type of inspect / Test and Frequency - Design report from fabricator
2eebf8ec-a9a8-5d85-94bc-f4020b07c051 | note | Acceptance Criteria - Design report from fabricator
0fd266ea-0fd5-52d8-b345-b298cef44dd0 | note | Inspection Responsibility: BCL - D
87961a81-4520-539c-ba6b-1b9e3d27cb14 | note | Verification Records of Inspection(s) / Test(s) - Upload design report
| section | 2.0 Construction
| checkpoint | 2.1 Tank Construction
7f89eb46-487f-5765-986b-faf04a52ab00 | note | Type of inspect / Test and Frequency - PE Tank fabricated by approved/competent fabricator
6c772e7c-a2a1-5327-a5b9-4e0898e4b0ff | note | Acceptance Criteria - Visual inspection
645e6cd9-0e2a-5b48-bcca-e3dcfa85aab3 | note | Inspection Responsibility: BCL - D
17be818c-4d05-5721-9044-9f656b4a83b7 | note | Verification Records of Inspection(s) / Test(s) - Upload tank construction documentation from Placon. Photos.
| section | 3.0 Testing
| checkpoint | 3.1 Leak test tank
1a1264bb-d23a-560e-ac2b-5a5a41339fb9 | note | Type of inspect / Test and Frequency - Fill to overflow level, hold for 24 hours. No level change, no visual leaks
d28869f8-31b5-5111-bacf-3ec3cacd7dca | note | Acceptance Criteria - Leak Test passed
f0cb5fe2-42c0-5ec2-9f65-368676d77c42 | note | Inspection Responsibility: BCL - T
6341f43c-e5ea-5e97-9083-cde478958f07 | note | Verification Records of Inspection(s) / Test(s) - Upload Leak Test report
| checkpoint | 3.2 Spark test tank
11abdca4-f04f-5205-9eee-e679da022506 | note | Type of inspect / Test and Frequency - Spark test all welds
28d702cd-a276-5580-8af0-c85ef6bc2eb0 | note | Acceptance Criteria - Spark Test passed
15d00d9a-ba6e-5323-9bae-a03749639255 | note | Inspection Responsibility: BCL - T
1386baf2-ec67-5527-ab25-1597b83c2fce | note | Verification Records of Inspection(s) / Test(s) - Upload Spark test report
| section | 4.0 Certification
| checkpoint | 4.1 Stationary Container Tank Compliance Certificate
d94cc94f-93ed-5ef8-a7a9-2d13e5126b28 | note | Type of inspect / Test and Frequency - Worksafe authorised certifier to provide compliance certificate
3f3b8525-611e-59a8-888b-60156683c67b | note | Acceptance Criteria - Compliance certificate
b08c3399-2d8c-5629-a77c-29ba16d926e9 | note | Inspection Responsibility: BCL - D
dc1f53fc-96c3-5de4-83e7-5fc14ee6987e | note | Verification Records of Inspection(s) / Test(s) - Upload certificate
| checklist | ITP 010 - O&M Manuals | itp | ITP 010 - O&M Manuals | 24060272-c948-4316-ba88-9cda93456ebc
| section | 1.0 Asset Lists
| checkpoint | 1.1 Equipment List
4e0b2ca6-fbb7-5801-88d8-478b679aad58 | note | Acceptance Criteria - List with equipment no., make & model
b98f4e29-a95c-5b42-a9e7-d3b56a3c91e5 | note | Inspection Responsibility: BCL - D
034e2cf2-ed11-5e9e-92d3-4cc8996bb7de | note | Verification Records of Inspection(s) / Test(s) - n/a
| checkpoint | 1.2 Instrument List
f2bae882-7863-5fe2-ab40-c268372b8e69 | note | Acceptance Criteria - List with equipment no., make & model
6b81eb17-f4f2-5546-8486-bdad4f6fe4d9 | note | Inspection Responsibility: BCL - D
2ab412e1-6657-50fe-8e43-aeffba6f6634 | note | Verification Records of Inspection(s) / Test(s) - n/a
| checkpoint | 1.3 Valve List
2fd80f22-fb88-5138-8cdd-1577b0a3d759 | note | Acceptance Criteria - List with equipment no., make & model
70269d9b-48aa-5d7e-82f3-b4ce9c4ef84f | note | Inspection Responsibility: BCL - D
1f3c15d2-be0b-54e6-9403-ed5489db6f2f | note | Verification Records of Inspection(s) / Test(s) -
| section | 2.0 Equipment O&M Manuals
| checkpoint | 2.1 Grundfos Pumps
517a0112-86eb-511c-905e-f9d4cd6f11fd | note | Acceptance Criteria - Vendor O&M Manual
8f42df51-97c0-580d-83e7-77575558480c | note | Inspection Responsibility: BCL - D
79c31471-fab6-5bec-801a-42ed95ea4380 | note | Verification Records of Inspection(s) / Test(s) - n/a
| checkpoint | 2.2 GF Water Jet Suction Pump
c5538733-475f-544f-b9c6-eeb2f3843430 | note | Acceptance Criteria - Vendor O&M Manual
| checkpoint | 2.3 Seat 15 Fan
04a6c37a-b3c7-51d7-9d88-baecd098feef | note | Acceptance Criteria - Vendor O&M Manual
| checkpoint | 2.4 GF Strainers
| section | 3.0 Instrument O&M Manuals
| checkpoint | 3.1 Endress & Hauser Flow Transmitters
| checkpoint | 3.2 Endress & Hauser Level Transmitters
| checkpoint | 3.3 Endress & Hauser Level Switches
| checkpoint | 3.4 Prominent Fluoride Analysers
| checkpoint | 3.5 Vega Level Transmitters
| checkpoint | 3.6 Weber Flow Switches
| checkpoint | 3.7 Wika Pressure Gauges
| section | 4.0 Valve O&M Manuals
| checkpoint | 4.1 Emerson Backflow Preventors
| checkpoint | 4.2 GF Actuators
| checkpoint | 4.3 GF Valves
| checkpoint | 4.4 K-Ball Valves
| checklist | ITP 011 - Bund Construction - Concrete Works | itp | ITP 011 - Bund Construction - Concrete Works | a2ed573d-818b-4ec0-aa9b-61fadcf4989f
| section | 1.0 Documentation
| checkpoint | 1.1 Construction Drawings
d9c213d6-00ed-58bb-af59-14b9e7dacd17 | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
11d61450-548a-5947-8209-0860af167e12 | note | Acceptance Criteria - Latest IFC Drawings
37bd8f8f-d5e6-50b6-bc8b-7596167e3e69 | note | Inspection Responsibility: BCL - I
2be51d90-85d9-5756-8172-2d57fdcf3e1d | note | Inspection Responsibility: Client - S
3beebdb3-a0fe-5719-bd27-dd2347e0e8f3 | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
| checkpoint | 1.2 Concrete mix design
b370a5f1-d26f-523d-adeb-99d9d0ff6a5a | note | Type of inspect / Test and Frequency - Submitted to Beca for approval
a76b9cc6-d5a9-5923-bad7-e7c4b38e6ff4 | note | Acceptance Criteria - Approved RFI
9bab5376-6c39-5923-83f2-d9dac3ba8611 | note | Inspection Responsibility: BCL - H
02ccac48-126a-54bf-81ee-4ff797526675 | note | Inspection Responsibility: Client - A
d65dd31f-313a-54e3-9806-34003c6eec8a | note | Verification Records of Inspection(s) / Test(s) - RFI
| signoff | HOLD POINT
| section | 2.0 Excavation
| checkpoint | 2.1 Set Out, as per latest “For Construction” revision
edf17451-6352-5ec2-895d-98c8a50bb1f9 | note | Type of inspect / Test and Frequency - Survey and mark the bund location
f04b410e-f2e4-5dae-8f62-bc2d6190d837 | note | Acceptance Criteria - IFC Drawings, Survey data check by PM
4045c36e-8af3-517c-9c0f-5565921f6d58 | note | Inspection Responsibility: BCL - T
b5ecb1f3-320d-5be7-8d82-4a1a1db242ea | note | Inspection Responsibility: Client - I
8a73b7dc-8706-538a-aee1-6b9ed506e596 | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings
| checkpoint | 2.2 Subgrade inspection
7e677914-2eeb-5f67-b46b-81764fd286ad | note | Type of inspect / Test and Frequency - Scala testing to confirm subgrade is of sufficient strength
e5e24da2-ec9d-5d64-a7ee-18d65b4f75a6 | note | ○ Witness by engineer
dbed8772-4e70-56a9-b7f3-2f95c3ee2ba7 | note | ○ Minimum of 2 tests per bund pour
425e7593-2a67-556d-9f01-19e80d292903 | note | Acceptance Criteria - Minimum of 5 blows per 150mm
bc4e936f-a937-5e96-adc1-455db24a56e5 | note | Inspection Responsibility: BCL - H
07851317-2d7a-5b28-8081-501aee5f2cf1 | note | Inspection Responsibility: Client - A
973f8618-dfbb-5acf-9828-2b26b6c4f692 | note | Verification Records of Inspection(s) / Test(s) - Scala Test Results
| signoff | HOLD POINT
| section | 3.0 Post Excavation
| checkpoint | 3.1 >150mm compacted hard fill under bund (GAP20)
0da27dd9-21e7-56d0-81c1-f61e680550d0 | note | Type of inspect / Test and Frequency - Clegg hammer testing, 5x5 grid, minimum of 4no per bund pour
2d9c4761-13fa-59d7-8f01-534aaf6a5183 | note | Acceptance Criteria - Clegg CIV>10
6f578dd3-d104-5269-837d-7796ab788246 | note | Inspection Responsibility: BCL - T
c7d8dbe3-4702-5672-bf0e-b76b3125f5e8 | note | Inspection Responsibility: Client - R
071771f5-b320-565b-83a8-c4dfb019fb43 | note | Verification Records of Inspection(s) / Test(s) - Clegg results
| section | 4.0 Concrete works
| checkpoint | 4.1 Site concrete
cc8cda13-2056-5eac-ac3f-34fa07e31826 | note | Type of inspect / Test and Frequency - Visual inspection and record of site concrete install, completed for each slab pour
405cd2cf-2e22-5e9a-90bc-c52e58c38470 | note | Acceptance Criteria - 50mm site concrete poured to base level of foundation +0mm -10mm tolerance
1186a8d4-a4e3-52f5-9054-b5f9e7ca3704 | note | Inspection Responsibility: BCL - D
c7423153-5d7f-5c96-b6b4-df7a24228792 | note | Inspection Responsibility: Client - W
0d15e048-4153-5425-9882-fbc38ae213cb | note | Verification Records of Inspection(s) / Test(s) - Photos, Concrete pour record
| checkpoint | 4.2 DPM
dfcdb8cf-7d31-5158-b831-379ff1d05433 | note | Type of inspect / Test and Frequency - Visual inspection and record of DPM installed, completed prior to each pour
df06de46-6491-51d6-9289-1ddae7d2958d | note | Acceptance Criteria - Polythene laid on site concrete prior to reinforcing
f0e6d95e-d319-5ac2-a635-1bb63893cc9f | note | Inspection Responsibility: BCL - D
8e17f72c-8e95-5cb3-9ed8-97b3ab734b10 | note | Inspection Responsibility: Client - W
44b62a3f-8878-5ea9-b677-4bac84a9f1b8 | note | Verification Records of Inspection(s) / Test(s) - Photos, Concrete pour record
| checkpoint | 4.3 Reinforcing (material)
a0493348-6d89-5b67-9040-3389fdbc8ccb | note | Type of inspect / Test and Frequency - Review documentation for each pour
ab29a6b0-68b9-5980-a6a1-0a33bc45d248 | note | Acceptance Criteria - Reinforcing to be Grade 500E to ASS/NZS4671
47b0a240-dd63-5d0d-a9ca-ddc420b54f7e | note | Inspection Responsibility: BCL - D
63c241a2-e452-5abc-93c8-66951c0ed205 | note | Inspection Responsibility: Client - W
b5393979-a028-51a8-bfad-0cab5c625f72 | note | Verification Records of Inspection(s) / Test(s) - Mill certificates, Detail sheet
| checkpoint | 4.4 Sump Construction
d0a6ad3e-03ad-5c3d-bc2b-5057ec35c499 | note | Type of inspect / Test and Frequency - Reinforcing check, dimension check, Formwork check
ee731936-9464-5fde-8d92-8803e706344a | note | Acceptance Criteria - As per IFC drawings
850c7311-0853-5be2-aa27-f5f06f8decfb | note | Inspection Responsibility: BCL - D
79d86193-99ee-5da8-8415-3455e33078a4 | note | Inspection Responsibility: Client - W
57ef8387-746c-5e11-826e-cf8e08ccde7c | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 4.5 Reinforcing install
1f983773-e7e9-5339-b98a-53ff9b096cb7 | note | Type of inspect / Test and Frequency - Measure to check cover, bar size and arrangement, lap length and type. Complete prior to pouring concrete.
54f409c1-9214-5692-b14a-527e26663334 | note | Acceptance Criteria - Reinforcing matches IFC drawings, any deviations recorded and acceptance agreed with engineer prior to pour
36d7ecfa-689e-5161-88d1-92559917f6f0 | note | Inspection Responsibility: BCL - D
91a55721-b2bf-53dc-9b9c-6436472392ae | note | Inspection Responsibility: Client - W
2cd87564-c890-56d0-906b-996bf533b070 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
| checkpoint | 4.6 Reinforcing install
b422f494-3472-5129-ac8a-d6aff556f872 | note | Type of inspect / Test and Frequency - Starter bars for tank plinth, Starter bars for blockwork
6ad1b96a-5c5a-5004-aac8-c45f33c780df | note | Acceptance Criteria - Matches IFC drawing
0563b686-6a87-5b56-ab84-d8ad7dba9b04 | note | Inspection Responsibility: BCL - D
2cc9831f-aa64-5f02-830b-8c64e2daeb0c | note | Inspection Responsibility: Client - W
cbdb07d1-a58a-5604-98b5-90beaa298dbc | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
| checkpoint | 4.7 Tank plinth
4331114d-ad48-5a38-8608-1c8f72166641 | note | Type of inspect / Test and Frequency - Size of plinth, height of plinth, Reinforcing checked, Formwork checked
e9c837f0-b609-5ef2-894f-cb31772e1c48 | note | Acceptance Criteria - Matches IFC drawing and response of RFI017
abb3167b-5934-5c5f-8b84-269cc25aa73c | note | Inspection Responsibility: BCL - D
28cb511c-d306-5173-a653-c4f4ab065487 | note | Inspection Responsibility: Client - W
effc15e5-f329-5c23-9d77-2ace1ca20c57 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
| checkpoint | 4.8 Concrete pour
8fbf9313-5d49-56e4-9dd4-2fb22cf2a797 | note | Type of inspect / Test and Frequency - Embedded items located in slab
49224cef-44bb-59ad-8509-f20a68397b47 | note | ○ Ducting
63f6d757-c02c-5997-9460-a8c9687b98cb | note | ○ Pits
ed1280f6-38fc-5d9b-8e40-31b54a84496a | note | Acceptance Criteria - Matches IFC drawings
4a5556a3-b11d-5587-b63a-97cfb8ca634d | note | Inspection Responsibility: BCL - D
cd176b1e-1b40-514e-8e2c-370431dd3d45 | note | Inspection Responsibility: Client - W
a92a9df9-e484-51c4-ba35-b281402374b6 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, photos
| checkpoint | 4.9 Concrete pour
f8fcc818-9b6f-5fad-ad34-67eaac000e85 | note | Type of inspect / Test and Frequency - Level check, formwork check, cover check. Inspections prior to every pour.
58804c58-4fb0-5c6f-b5aa-fb2ab0bbd9d3 | note | Acceptance Criteria - Matches IFC drawing dimensions and notes
cbcfb7ac-4c7e-5826-8867-b55a4fa158c4 | note | Inspection Responsibility: BCL - D
86879baf-aec7-5430-aae5-2dbf224f5b61 | note | Inspection Responsibility: Client - W
2fc17cfa-f4cf-52fc-96b3-81c1cfbf0461 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 4.10 Pour inspection/Approval to pour
e68b317d-bd4c-565c-b150-85121cc3d9ce | note | Type of inspect / Test and Frequency - Pre pour inspection by Beca Engineer (hold Point)
e0dc5fdd-cb43-5981-9f57-65345b32ec6b | note | Acceptance Criteria - Approval from Engineer to pour
6108528b-5f49-56fe-8ffc-e59236a16f0f | note | Inspection Responsibility: BCL - H
960fdb93-85b6-5654-ac96-44d0142667ad | note | Inspection Responsibility: Client - A
| signoff | HOLD POINT
| checkpoint | 4.11 Concrete strength
8dce7574-2c2c-5c42-8dad-ff70de078b86 | note | Type of inspect / Test and Frequency - Test certificate 7 and 2no 28day tests required for each pour day or per 70m3
78568642-cec2-52db-8a84-e8ca410447e3 | note | Acceptance Criteria - 28 day compressive strength >40mPa
7d0b7de8-90ba-5ab3-b203-10139c492e96 | note | Inspection Responsibility: BCL - D
2920aad2-8d42-5298-bb5d-f757a3cda31d | note | Inspection Responsibility: Client - R
09cc468b-43c4-5837-aa2f-51223cf9abe5 | note | Verification Records of Inspection(s) / Test(s) - Test certificate
| section | 5.0 Blockwork
| checkpoint | 5.1 Blockwork (material)
426d445a-559a-5529-9571-cfaabcae8270 | note | Type of inspect / Test and Frequency - Manufacturer documentation. Required once prior to commencement of works.
2d307fa0-9959-5714-af5f-e6d9c8412d9a | note | Acceptance Criteria - Masonry units meet AS/NZS4455
da600c61-7e8e-563f-9219-57c20b02677b | note | Inspection Responsibility: BCL - D
49c5aad4-f012-5b57-bdb2-0e472293928f | note | Inspection Responsibility: Client - R
5e352824-3b4a-5a41-8218-def3d700ede9 | note | Verification Records of Inspection(s) / Test(s) - Supplier documentation
| checkpoint | 5.2 Blockwork (reinforcing)
577ee31c-c941-554a-9067-70695889eb77 | note | Type of inspect / Test and Frequency - Inspect bar size, placement, lap length and number (once per pour)
e2efdabd-3a5a-58f8-99a5-319bfe3ce46a | note | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
01dfa1d1-ae4e-5286-872f-0cd0e2934899 | note | Inspection Responsibility: BCL - D
9f2bdeef-ecf2-5737-a07b-24f7e40d53c4 | note | Inspection Responsibility: Client - R
4792b1c9-436c-5005-9018-861fc63d1ad4 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 5.3 Blockwork (pour)
c340b3f7-ad0e-5932-916d-bbcaa4b9f3eb | note | Type of inspect / Test and Frequency - Inspection prior to pour, check washout location, dimensions, line and level (once per pour)
bb892576-9b53-54c6-aeb6-c6ec08aa1006 | note | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
861e926c-739a-55a1-a673-0b7544336ced | note | Inspection Responsibility: BCL - W
c1b83ca0-7ddd-5d5c-9da0-d2076a770181 | note | Inspection Responsibility: Client - A
a8195794-9c24-5c8b-8d0b-2ef8ca71b635 | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
| checkpoint | 5.4 Concrete strength
2b13ae9f-0c36-5f93-9751-37fb0046296d | note | Type of inspect / Test and Frequency - Test certificate 7 and 2no 28day tests required for each pour day
985e47c0-8c4e-5f4c-a74b-3be85c23df8d | note | Acceptance Criteria - 28 day compressive strength >17.5mPa
c23f07bd-095a-5ecf-a2f6-dcc5c738d193 | note | Inspection Responsibility: BCL - R
2077de8a-0a64-567e-88d2-74c0f97ca7d8 | note | Inspection Responsibility: Client - R
b8270b6a-db88-5114-b6fe-41e7982b0d65 | note | Verification Records of Inspection(s) / Test(s) - Test certificate
| section | 6.0 As-builts
| checkpoint | 6.1 Redline Drawings
7350657c-4ecc-5bfc-bc01-4e2c52a7d4f3 | note | Type of inspect / Test and Frequency - Redline Civil Drawings Sets post construction
9e7ac24b-9630-509c-a0ce-5fc02a88df51 | note | Acceptance Criteria - N/A
91dc174a-fa6d-565c-bb66-b4510296b231 | note | Inspection Responsibility: BCL - D
85c872f4-06f7-5821-afd3-a13a7ecb0603 | note | Inspection Responsibility: Client - R
04ab2739-5c99-5cea-8588-75e89a33aa46 | note | Verification Records of Inspection(s) / Test(s) - As built drawings