## 045 Busduct Install Test
Busduct Installation and Testing
Nominate Equipment or Works associated with this ITC | [12 empty] | Page 1 of 1
ITP No : |  | 001 |  | ITP Item No: |  | 3.39 |  | Job No: |  | Area:
Dwg No:
Function | [10 empty] | OK | NA | NCR raised
No | Confirm following items comply with requirements | [11 empty] | Major | Minor
1 | Compare equipment nameplate data with drawings and specifications.
2 | Inspect physical, electrical, and mechanical condition. (Look for signs of moisture penetration)
3 | Inspect bus for physical damage and proper connection in accordance with single-line diagram
4 | Inspect for proper bracing, suspension alignment, and enclosure ground. (Verify that the bus duct is properly braced between floors and horizontal runs.)
5 | Verify tightness of accessible bolted electrical connections by calibrated torque wrench method in accordance with manufacturer’s published data.
6 | Mark the head of the bolt with a permanent marking pen. (Lose connections will cause heating and damage to connection.)
7 | Check for proper physical orientation per manufacturer’s labels to ensure proper cooling. (prevents bus duct from heat damage when at full load)
8 | Perform continuity tests on each conductor to verify a proper phase relationship exists. (This is especially important when transition sections are used.)
9 | Check outdoor busway for removal of “weep-hole” plugs, if applicable, and the proper installation of joint shield. (Failure to remove plugs will cause moisture build up and bus duct failure.)
10 | Check for proper fire blocking material and installation between floors.
Record Serial No and Calibration Date of all IMTE used :
Comments
Minor NCR's raised |  |  |  | YES | NO |  | N/A | Have all NCR's been finalised ?
[8 empty] | YES |  | NO |  |  | N/A
Major NCR's raised |  |  |  | YES | NO |  | N/A
Accepted By |  |  | Name (Print) |  | Signature |  |  |  | Position |  | Date
Q Electrical
PM Review
Client (If Applicable)