## 047 Elect Submetering
Electrical Sub Metering
Nominate Equipment or Works associated with this ITC | [12 empty] | Page 1 of 1
ITP No : |  | 001 |  | ITP Item No: |  | 3.41 |  | Job No: |  | Area:
Meter ID No:
Location:
Function | [10 empty] | OK | NA | NCR raised
Confirm following items comply with requirements | [12 empty] | Major | Minor
Meter Installation
Check that the meter is:
1 | Correct type
2 | Installed in correct location on switchboard in accordance with drawing
3 | Positioned squarely and correctly fitted
4 | Labelled correctly
5 | Has been terminated and termination is correct
Meter Checks
1 | Confirm that factory calibration certificate has been supplied (attach to ITP)
2 | Confirm CT type, size and direction are correct
3 | Connect load,apply clamp tester and confirm meter reading against clamp tester
4 | Confirm meter reading in location simultaneously with metering head end reading
5 | Confirm meter reading in location simultaneously with BMS head end reading
6 | Confirm meter reading from BMS independently. Result equals previous test
Record Serial No and Calibration Date of all IMTE used :
Comments
Minor NCR's raised |  |  |  | YES | NO |  | N/A | Have all NCR's been finalised ?
[8 empty] | YES |  | NO |  |  | N/A
Major NCR's raised |  |  |  | YES | NO |  | N/A
Accepted By |  |  | Name (Print) |  | Signature |  |  |  | Position |  | Date
Q Electrical
PM Review
Client (If Applicable)