## 060 ACB
LV ACB MAINTENANCE
Project Details:
Customer
Site
Project
Job Number
Switchroom ID
Switchboard ID
Circuit ID
Maintenance Level
Test Equipment Details:
Test Equipment 1
Asset ID: |  |  |  | Make and Model:
Test Equipment 2
Asset ID: |  |  |  | Make and Model:
Test Equipment 3
Asset ID: |  |  |  | Make and Model:
Circuit Breaker Details:
Make: |  |  |  | Type:
Serial Number: |  |  |  | Rated Current:
Rated Voltage: |  |  |  | Protection Type:
Close Coil Voltage: |  |  |  | Open Coil Voltage:
Spring Charge Volts: |  |  |  | Undervoltage Coil:
Op Counter as found: |  |  |  | Op Counter as left:
Section 1 - Energised Inspection
1.0 Visual Inspection
Checklist Item |  |  | Result | Checklist Item |  |  |  | Result
1.1 Condition of Exterior Components |  |  |  | 1.5 Infrared inspection
1.2 Control Cables and Connections |  |  |  | 1.6 Ultrasonic inspection
1.3 Indication Lights on Switchboard |  |  |  | 1.7 Circuit identification
1.4 Abnormal odours |  |  |  | 1.8 Protective covers
Section 1.0 Comments:
1
2
3
4
5
Section 2 - De-Energised Inspection
1.0 Visual Inspection
Checklist Item |  |  | Result | Checklist Item |  |  |  | Result
1.1 Main Bus Bar Connections |  |  |  | 1.4 Arc Control Devices
1.2 Earth Connection |  |  |  | 1.5 Insulation
1.3 Main Contact Assembly |  |  |  | 1.6 Operating Mechanism
Section 1.0 Comments:
1
2
3
4
2.0 Mechanical and Electrical Operation
Checklist Item |  |  | Result | Checklist Item |  |  |  | Result
2.1 Unit Racks into isolated position |  |  |  | 2.5 Operate Spring Charge Motor
2.2 Unit Racks into service position |  |  |  | 2.6 Operate Close Coil
2.3 Perform 5 manual open operations |  |  |  | 2.7 Operate Open Coil
2.4 Perform 5 manual close operations |  |  |  | 2.8 Operate Undervoltage Coil
Section 2.0 Comments:
1
2
3
4
5
3.0 General Items
Checklist Item |  |  | Result | Checklist Item |  |  |  | Result
3.1 Clean, Oil and Adjust Operating Mechanism |  |  |  | 3.3 Control Cables and Connections
3.2 Check Auxiliary Contacts |  |  |  | 3.4 Check Local and Remote Switches
Section 3.0 Comments:
1
2
3
4
5
4.0 Maintenance Tests
4.1 Main Current Path Low Resistance Test
Test Item |  | A Phase |  | B Phase |  | C Phase |  | Neutral
Main Current Path - Before Maintenance Pole 1 (µΩ)
Main Current Path - After Maintenance Pole 1 (µΩ)
Main Current Path - Before Maintenance Pole 2 (µΩ)
Main Current Path - After Maintenance Pole 2 (µΩ)
4.2 Insulation Resistance Test
Test Item |  | A - B+C+E |  | B - A+C+E |  | C - A+B+E |  | N-ABCE
Insulation Resistance Test - CB Open - Load Side (GΩ)
Test Item
Insulation Resistance Test - CB Open (GΩ)
4.3 Protection Relay Test
Protection Relay Details
Make: |  |  |  | Type:
Serial Number: |  |  |  | Rating:
Test Type: |  |  |  | Test Equipment:
Protection Relay Settings
Phase Overcurrent |  |  |  | Earth Fault
Pickup |  |  |  | Pickup
TMS |  |  |  | TMS
Curve |  |  |  | Curve
Instantaneous |  |  |  | Instantaneous
Phase Overcurrent
Test Item |  |  | A Phase Result |  | B Phase Result |  | C Phase Result
Pickup (A)
Injected Amps (2x)
Expected Time in Milliseconds (ms)
Actual Time in Milliseconds (ms)
Injected Amps (3x)
Expected Time in Milliseconds (ms)
Actual Time in Milliseconds (ms)
Injected Amps (5x)
Expected Time in Milliseconds (ms)
Actual Time in Milliseconds (ms)
Instantaneous Pickup (A)
Time in Milliseconds (ms)
Overall Result
Earth Fault
Test Item |  |  | Earth Fault Results
Pickup (A)
Injected Amps (2x)
Expected Time in Milliseconds (ms)
Actual Time in Milliseconds (ms)
Injected Amps (3x)
Expected Time in Milliseconds (ms)
Actual Time in Milliseconds (ms)
Injected Amps (5x)
Expected Time in Milliseconds (ms)
Actual Time in Milliseconds (ms)
Instantaneous Pickup (A)
Time in Milliseconds (ms)
Overall Result
Test Item |  |  | Result | Test Item |  |  |  | Result
4.1 Main current path low resistance test |  |  |  | 4.3 Protection relay test
4.2 Insulation resistance test |  |  |  | 4.4 Electrical Functionality
Section 4.0 Comments:
1
2
3
5.0 E-Check Safety Sign Off
All modifications to the installation during maintenance has been returned to as the originally found state
Date:
E-Check Technician:
Q Electrical Overall Condition Assessment
Rating:
Recommendation:
Overall Condition Assessment Comments:
1
2
3
4
5
Maintenance type completed:
Level 2 Examination Maintenance - Shutdown inspection - Complete all Sections
This statement is to certify the electrical equipment above, to extent it is affected by the electrical work performed, has been tested to ensure it is electrically safe and is in accordance with the requirements of the wiring rules and any other standard applying under this regulation to the electrical installation.
Accepted By | Name (Print) |  | Signature |  | Position |  | Date
Q Electrical
PM Review
Client (If Applicable)