## ITP Cover Page
Streetlighting Inspection and Test Plan
Project: SH1/29 Intersection Upgrade
Number and Revision: 1208 - 903 - Rev B
SECTION 1 – GENERAL DETAILS
Project Name: |  |  | SH1/29 Intersection Upgrade |  |  |  |  | ITP Number: |  |  | 903
Project Number: |  |  | 1208 |  |  |  |  | ITP Status: |  |  | IFC
ITP Description: |  |  | Streetlighting Inspection and Test Plan |  |  |  |  | Revision: | 1000 |  | B
Contract Number: |  |  | 7991 |  |  |  |  | Drawing Sets:
Customer: |  |  | Waka Kotahi |  |  |  |  | Specification: |  |  | Project Specification
Quality Specified: |  |  | Z8
Review / Update History | [9 empty] | Verification Activity
Rev: | Status: | Date: |  | Reviewed By: |  | Revision Details: |  |  |  | Activity Key |  |  | Responsibilities Key
A | Draft for Review | 2024-06-04 |  | Michael Randall |  | Streetlighting Inspection and Test Plan |  |  |  | A | Action |  | ENG | Engineer / Engineer's Rep
[10 empty] | B | Report by Breach |  | CR | Customer Rep
B | IFC | 2024-07-10 |  | Shaun Kay |  | Amendments/comments added |  |  |  | C | Check |  | PD | Project Director
[10 empty] | D | Dimension Inspection |  | PM | Project Manager
[10 empty] | E | Examine |  | OP | Operations Manager
[10 empty] | HP | Hold Point (Engineer) |  | HSE | HSE Manager / Rep
[10 empty] | H | Hold Point (Internal) |  | QM | QA Manager / Rep
[10 empty] | I | Inspection |  | PE | Project Engineer
[10 empty] | M | Monitor on Random Basis |  | SE | Site Engineer
[10 empty] | O | Operation |  | QE | Quality Engineer
[10 empty] | R | Review |  | SUP | Superintendent / Supervisor
[10 empty] | S | Subcontractor |  | SV | Surveyor
[10 empty] | V | Visual Verification |  | ITP | Third Party Inspector
[10 empty] | W | Witness Point |  | SPEC | Specialist
SECTION 2A – Master ITP Approval | [7 empty] | SECTION 2B – ITP CLOSEOUT
Position |  | Name: |  |  | Signature: |  | Date: | Position |  | Name: |  | Signature: |  |  | Date:
Downer PM | [7 empty] | Downer PM
Downer QM | [7 empty] | Downer QM
Client (If Applicable) | [7 empty] | Client (If Applicable)

## STREETLIGHTING
Streetlighting Inspection and Test Plan
Project: SH1/29 Intersection Upgrade
Number and Revision: 1208 - 903 - Rev A
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Testing Quantity Required | Verification Activity |  | Downer Conformance of Compliance Signoff
[7 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details | ENGINEERS COMMENTS - Date: | DOWNER RESPONSE - Date:
SECTION 3 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
Design | [11 empty] | Breaking into PS sub-element
Safety in Design Analysis
3.1.01 | Safety in Design Analysis | Conduct a detailed safety in design analysis. Ensure the installation is compliant with the Site’s safety in design proposal including all regulatory requirements. | PS 22.1.15& 22.3.2 | Design Analysis report | Prior to Construction |  | H | PE
Management Processes | [11 empty] | Breaking into PS sub-element
Streetlighting Quality Assurance plan
3.2.01 | Streetlighting Quality Assurance plan | Sub-Contractor to provide a Quality Assurance plan to propose, establish, maintain, monitor and document a quality assurance system covering all aspects of the procurement, fabrication, installation and completion of the works. | PS 22.4.6 | Streetlighting QA Plan | Prior to Construction |  | HP | ENG
Material and Installation Requirements | [11 empty] | Breaking into PS sub-element
Montrose Box (MSB-NMB)
3.3.01 | (MSB-NMB) | Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction. | PS 22.1.7 | Shop Drawings | Prior to Installation |  | HP | ENG
3.3.02 | Hasp and Staple | MSB-NMB shall be fitted with a Stainless-Steel hasp and staple to allow for Waka Kotahi to fit their own padlock onto it. MSB-NMB shall be sourced directly from Montrose Foundry, Mt. Wellington, Auckland. | PS 22.1.7 | Datasheet and dockets | Prior to Installation |  | I | PE
3.3.03 | Metering | Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box. | PS 22.1.9 | Comms | Prior to Installation |  | I | PE
3.3.04 | CCTV Compartment | Allow for a CCTV Compartment withing the Montrose Box. Provide a 10A double power outlet within this compartment for future use of CCTV equipment. CCTV Compartment to meet NZTA requirements. | PS 22.1.10 | Datasheet | Prior to Installation |  | I | PE
3.3.05 | Earthing, Bonding & Surge Protection | Install an earth electrode in accordance with the in AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link. | PS 22.1.11 & 22.6.10 | Site Record | Prior to Installation |  | I | PE
Lighting Equipment
3.4.01 | Design Drawings | Provide drawings of luminaire design and pole locations for review and approval by the Engineer prior to construction. | PS 22.1.14 | Drawings | Prior to Construction |  | HP | ENG
Welding
3.5.01 | Welding | All welding shall be performed by qualified and experienced tradesmen in accordance with relevant New Zealand or Australian Standards, with the engineer having the right to request certification and welding experience, and, if concerns arise about welding quality, to request at no additional cost X-ray and/or ultrasonic testing of up to 10% of all welds selected by the engineer, with any failures potentially requiring additional testing. All welding is to be completed before any corrosion protection treatment is applied. | PS 22.6.6 & 22.7.1 | Welding Certificates | Prior to Construction |  | R | PE |  |  |  | added"All welding is to be completed before any corrosion protection treatment is applied."
Corrosion Protection
3.6.01 | General | Notwithstanding anything to the contrary in this specification, where possible all items of plant, equipment and materials shall be manufactured or supplied in materials that will not suffer corrosion. Appropriate materials include galvanised steel, aluminium, fibreglass, stainless steel, etc. All support steelwork, fixings and other galvanised steel shall be hot dip galvanised. The use of electro plated fastenings for external works is not acceptable. All welding is to be completed before any corrosion protection treatment is applied. | PS 22.7.1 | Datasheet | Prior to Construction |  | I | PE
Painting, Protection and Identification
3.7.01 | Environmental | Select painting and finishes in accordance with the area environmental conditions. | PS 22.8.1 | Datasheet | Prior to Painting |  | I | PE
3.7.02 | Compliance Review | Review the risk assessment and statutory and authority requirements completed as part of the system testing, commissioning and handover requirements and provide labelling and signage as determined. | PS 22.8.1 | Datasheet | Prior to Painting |  | R | PE
3.7.03 | Colours | Paint colours nominated are to be in accordance with NZS 5807 | PS 22.8.6 NZS 5807 | Datasheet | Prior to Painting |  | I | PE
Underground Services
3.8.01 | Ducting | Unless shown otherwise all buried ducts shall be the sizes and quantities as indicated on the layout plan. (DIA. 50mm) (DIA. 100mm) a) Use heavy duty HD PVC conduit for underground services. Use best practice PVC where possible. b) Colour: Orange for all conduits containing consumer mains, sub-mains or final sub-circuits cabling. | Road Lighting Ducting Layout PS 22.12.8 | Datasheet | Prior to Installation |  | I | PE
3.8.02 | Warning Tape | Provide orange marker tape complying with AS/NZS 2648.1 | PS 22.12.9 AS/NZS 2648.1 | Datasheet | Prior to Installation |  | I | PE
SECTION 4 – CONSTRUCTION ACTIVITY
Existing Underground Services
4.1.01 | Existing Underground Services | The contractor shall undertake a comprehensive services identification program prior to beginning site works. This would include as a minimum, review of all service providers maps and drawings, a site scan, and if necessary, a scan using GPR (ground penetrating radar). | PS 22.6.4 | Site Record/Survey Record | Prior to Construction |  | R | PE
Survey
4.2.01 | Set-out | Light columns set out as per design locations. | IBEX Lighting Plan | Survey Record | Prior to Construction |  | R | SV
Underground Services
4.3.01 | Trench Excavation | Excavate trench and lay 50mm sand bedding and free from obstraction | PS 22.12.8 | Site Record | Where Required |  | I | SE
4.3.02 | Ducting/Conduit | (a)Separation from LV conduits: Minimum separation between conduits shall be no less than 50mm from other conduits and no less than 100mm from boundary of the trench. Sandy loam is required for building and separation. b) Depth: Conduits shall be buried in trench at a depth no less than that nominated in AS 3000 for the method of installation, with all bends being slow radius bends. c) Separation from other services: Maintain separation from other services running in parallel and crossing electrical installation as nominated by relevant standard (e.g. AS/NZS 3500 for water services, AS/ACIF S009 for telecommunications, AS 5061 for gas services, etc.). | Road Lighting Ducting Layout PS 22.12.8 | Site Record | Where Required |  | I | SE |  |  |  | amended to align with PS
4.3.03 | Survey As-Built | Accurately record the routes of underground cables before backfilling | PS 22.12.9 | Survey Record | After ducts are Installed |  | H | PE |  |  |  | changing this to Project engineers hold point
4.3.04 | Backfill | Backfill trenches with sand as soon as possible after approval of laid and bedded service to a height of 300mm. Place the sand in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement, | PS 22.12.8 | Site Record | Where Required |  | I | SE |  |  |  | added "compact to the density which applies to the location of the trenches to minimize settlement," to reflect PS
4.3.05 | Warning Tape | Install orange marker tape complying to AS/NZS 2648.1. Install marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level. | PS 22.12.9 | Site Record | Where Required |  | I | SE |  |  |  | amended to align with PS
Lighting
4.4.01 | Shear Base | Ensure the shear base is installed as per the NZTA M26 specification and in the correct location as per the latest IFC drawing. | NZTA M26 IBEX Lighting Plan | Site Record | Where Required |  | I | SE
4.4.02 | Column Installation | Columns shall be positioned 1.0m behind the kerb unless stated otherwise or advised. Allowable tolerances of the column location are: A) 0.5m Parrallel to the carriageway B) 0.2m Perpendicular to the carriageway C) 0.2m Vertically Ensure columns are oriented correctly and have the correct outreach arm lengths. | IBEX Lighting Plan | Site Record | Each Column |  | I | SE |  |  |  | Added 'Ensure columns are oriented correctly and have the correct outreach arm lengths'
4.4.03 | Luminaire | Ensure the correct luminaire type and tilt angle is installed as per the latest IFC drawings | IBEX Lighting Plan | Site Record | Each Luminaire |  | I | SE
Montrose Box (MSB-NMB)
4.5.01 | Montrose Box (MSB-NMB) | Install MSB-NMB as per project specification, Installation and commisioning ITP and the Electrical Services drawings. | PS 22.1.7 | Site Record | Once |  | I | SE
Painting and Protection
4.6.01 | Preparation of Surfaces | Preparation: all surfaces shall be prepared by thorough cleaning of all dirt, grease, scale, welding flux and corrosion in accordance with AS/NZS 2312.1. For galvanised surfaces that have been subsequently cut or welded, prime the affected area with organic zinc rich coating for protection of steel to AS/NZS2312.1, two pack or accepted alternative Prime/undercoat all surfaces. Galvanised and non-ferrous surfaces must be etch primed. | PS 22.8.3 | Datasheet | Prior to Painting |  | I | PE |  |  |  | added to reflect PS requirements
4.6.02 | Application | Apply the first coat immediately after substrate preparation and before contamination, and follow all paint system applications strictly according to the manufacturer's recommendations. | PS 22.8.4 | Site Record | After surface preparation |  | I | SE
4.6.03 | Finishing | Concrete Bases: 2 coats synthetic emulsion paint Equipment Panels/Switchboards: 2 final coats full gloss enamel (c) Equipment: Factory spray application Other surfaces: 2 final coats full gloss enamel. | PS 22.8.5 | Streetlighting QA Plan | Prior to Construction |  | I | PE |  |  |  | added to reflect PS requirements
SECTION 5 – POST CONSTRUCTION ACTIVITY
Survey
5.1.01 | As-Built Drawings | As-builts reviewed and submitted showing final location of all poles. | PS 22.9.4 | Survey Record | Post Works Completion |  | R | SV
Testing
5.2.01 | Electrical Certificate of Compliance (CoC) | The contractor shall provide a CoC for the electrical installation. The certificate shall record all test results including insulation resistances, earth continuity and earth resistance. Detail to be included on the CoC is the measured prospective short circuit current for each outlet, switchboards and termination point, | PS 22.6.11 | CoC | Post Works Completion |  | R | PE
5.2.02 | Twelve-month warranty period | Provide twelve (12) months statutory testing, servicing, maintenance, remediation of defects and warranty of all services systems and equipment installed under this contract from the date of Practical Completion | PS 22.1.15 | Warranty | Datasheets |  | R | PE
Certification
5.3.01 | Final Certification | Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board. | PS 22.1.15 | Final Certificate | Post Works Completion |  | R | PE
Guarantee
5.4.01 | Guarantee | Provide guarantees for all equipment including 10-year minimum guarantees for external luminaires and poles. | PS 22.1.15 IBEX Lighting Plan | Guarantee | Post Works Completion |  | R | PE
Spare Parts Schedule
5.5.01 | Spare Parts Schedule | Provide a comprehensive schedule of maintenance spare parts, detailing recommended quantities, manufacturer prices including packaging and delivery to site, marking and numbering procedures, referencing equipment schedules, and preventive measures such as painting and greasing to avoid deterioration during storage. | PS 22.9.7 | Spare Parts Schedule | At least 8 weeks prior to Practical Completion |  | R | PE
Required Operating Instructions
5.6.01 | Required Operating Instructions | Provide operating instructions and schematic diagrams mounted alongside equipment to meet statutory requirements, e.g., Fire Brigade. Diagrams to be colour-coded, colour-fast, laminated and mounted. | PS 22.9.7 | Site Records | Post Works Completion |  | R | PE
Operating and Maintenance Manuals
5.7.01 | Operating and Maintenance Manuals | Provide a comprehensive Operating and Maintenance documentation to cover all installations to provide a detailed understanding of the plant and its operation, an aid for training of operators, a reference for fault diagnosis and a framework for preventative and breakdown maintenance. Submit manuals in two stages. Stage 1 include all the sections (generally sections 1-5) of manuals excluding final testing and commissioning records and As Built drawings. This manual shall be submitted well in advance of the Practical Completion and should be signed off by the Engineer at least 4-6 weeks before programme Practical Completion Date. A first draft manual should be submitted 8-10 weeks before the practical completion date for review. Subsequently, submit a completed second draft incorporating comments for further review. Finally, include all remaining sections, incorporate all changes and resubmit until all comments are addressed to the satisfaction of the Engineer | PS 22.9.6 | O&MM | 4-6 weeks before programme Practical Completion Date |  | HP | ENG
5.7.02 | Inspection and Test Plan | Installation and commisioning Inspection and Testing Plans to be provided to the satisfaction of the Engineer | PS 22.9.6 PS 22.9.4 | ITP | Prior to Installation |  | HP | ENG
5.7.03 | Final Copies Stage 1 & 2 | Submit 3 sets of final volumes within 2 weeks after practical completion. Incorporate feedback from review and from training of Principal’s staff, including preparation and insertion of additional data. Include a section containing commissioning test reports. | PS 22.9.6 | O&MM | Within 2 weeks after practical completion |  | R | PE
Final Contract and Hand-Over Documentation
5.8.01 | Final Hand-Over | Documentation is required in electronic and hard copy format. Electronic documentation shall be supplied on the latest Microsoft and Autodesk Software versions at the time of Practical Completion. Operating and Maintenance Manuals (including Final Commissioning Data): Electronic format installed on BMS File Server: 1 set PDF format on USB storage device: 3 sets Hardcopy: 3 sets As-Built Drawings: AutoCAD format on USB storage device: 3 sets Hardcopy full-size with hanging strips: 1 set A3 size (included in O&M Manual): 2 sets Revit Model: Refer to the requirements set out in the project BEP (BIM Execution Plan) Control Software: USB storage device: 1 set OH&S Safety Signage: Permanent: 1 set | PS 22.9.7 | Site Records | Post Works Completion |  | R | PE

## Sheet1
22.1 Scope of Works
22.2 Design and performance Requirements
22.3 Health and Safety .................................................................................................................... 176
22.4 Management Processes .......................................................................................................... 176
22.5 Standards, Codes and Regulations......................................................................................... 181
22.6 Material and Installation Requirements ................................................................................... 183
22.7 Corrosion Protection ................................................................................................................ 192
22.8 Painting, Protection and Identification ..................................................................................... 194
22.9 Inspection, Testing, commissioning, Handover and Defects Notification Period .................... 196
22.10 Supply and Metering ............................................................................................................... 208
22.11 Earthing ................................................................................................................................... 209
22.12 Wiring System ......................................................................................................................... 210