## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | ITP - Streetlighting - 903 - Rev B | itp | ITP - Streetlighting - 903 - Rev B |  | fa70d108-a7a9-46fe-b4a6-1ac377b01c2f
| section | 3.1. - Safety in Design Analysis
| checkpoint | 3.1.01 - Safety in Design Analysis
8b89d99c-65eb-56a3-ae8c-dd7d2113a126 | note | Acceptance / Conformance Criteria - Conduct a detailed safety in design analysis. Ensure the installation is compliant with the Site’s safety in design proposal including all regulatory requirements.
74abf515-409a-507e-bb6b-3d83c3de6f06 | note | Standard / Specification - PS 22.1.15& 22.3.2
feab34c1-79a0-5eda-a842-91be5a1cff09 | note | Verifying Document - Design Analysis report
5d37eb63-cd7e-546b-a5e3-c87a365f2db5 | note | Frequency - Prior to Construction
a4cc6791-5c49-5fc8-aa05-9ac4d234f3a2 | note | Verification Activity: Activity - H
88026bdb-a71f-571f-bb40-fc89771884af | note | Verification Activity: By - PE
| section | 3.2. - Streetlighting Quality Assurance plan
| checkpoint | 3.2.01 - Streetlighting Quality Assurance plan
95105840-acfb-5454-b42b-7f314ff7e234 | note | Acceptance / Conformance Criteria - Sub-Contractor to provide a Quality Assurance plan to propose, establish, maintain, monitor and document a quality assurance system covering all aspects of the procurement, fabrication, installation and completion of the works.
2d0fafc2-db04-587f-a9b0-a6a5bad9a1b3 | note | Standard / Specification - PS 22.4.6
cbd8e3eb-c76c-525e-96cc-1f405289bc11 | note | Verifying Document - Streetlighting QA Plan
88d22070-e1ff-575d-88cd-35fdec5d7756 | note | Frequency - Prior to Construction
79829e46-2208-5ad4-ac69-8bdc57f1d9de | note | Verification Activity: Activity - HP
165400ce-66b7-5e8e-a48e-d2d3c54bfcdb | note | Verification Activity: By - ENG
| signoff | AUTHORITY HOLDPOINT
| section | 3.3. - Montrose Box (MSB-NMB)
| checkpoint | 3.3.01 - (MSB-NMB)
dad3b660-68ad-51f0-ab2d-622c09a61c51 | note | Acceptance / Conformance Criteria - Provide MSB-NMB shop drawings complete with wiring schematics for review and approval by the Engineer prior to construction.
56a8bfa7-e110-5742-96e8-d706d02ea192 | note | Standard / Specification - PS 22.1.7
e467846b-f967-5fe1-a3b1-5dc91020491e | note | Verifying Document - Shop Drawings
d040bd67-b35a-5a8c-9c9f-40d686400b56 | note | Frequency - Prior to Installation
15eb5684-5e83-5394-b8ab-8ad2f9cc0771 | note | Verification Activity: Activity - HP
65243919-c5a3-593e-a71e-036c2f54b416 | note | Verification Activity: By - ENG
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3.02 - Hasp and Staple
09babadd-dc07-5e97-91e3-568b857a3fc8 | note | Acceptance / Conformance Criteria - MSB-NMB shall be fitted with a Stainless-Steel hasp and staple to allow for Waka Kotahi to fit their own padlock onto it. MSB-NMB shall be sourced directly from Montrose Foundry, Mt. Wellington, Auckland.
18689d8d-40a1-5e2b-adb5-9907c34bd143 | note | Standard / Specification - PS 22.1.7
44bec1af-e465-5b85-92d9-1df473571878 | note | Verifying Document - Datasheet and dockets
9ffabcbe-7bf3-5a19-9f60-16398967f671 | note | Frequency - Prior to Installation
7c05d107-ee0f-5ff6-a94c-707f01302685 | note | Verification Activity: Activity - I
336a4ef6-cb42-5800-87b3-36687b3577a3 | note | Verification Activity: By - PE
| checkpoint | 3.3.03 - Metering
23991eb9-362e-5044-a726-eb24d236c4a7 | note | Acceptance / Conformance Criteria - Liaise with the client’s electricity retailer for the installation of their three-phase meter within the metering compartment of the new Montrose Box.
ac3bb863-f70c-52f5-8e26-0e3372e7de53 | note | Standard / Specification - PS 22.1.9
179ba631-9cf1-5b01-8c15-0cc3916d9138 | note | Verifying Document - Comms
b8df60e9-ecef-5471-9e73-54232fe06c6e | note | Frequency - Prior to Installation
1141fecb-b923-577e-81a5-29b07fccc368 | note | Verification Activity: Activity - I
0bfd854f-cb3b-5356-9435-6d7aebaf1c70 | note | Verification Activity: By - PE
| checkpoint | 3.3.04 - CCTV Compartment
47635e1a-b0fa-5532-b6b9-774e55e28ccf | note | Acceptance / Conformance Criteria - Allow for a CCTV Compartment withing the Montrose Box. Provide a 10A double power outlet within this compartment for future use of CCTV equipment. CCTV Compartment to meet NZTA requirements.
2a7ed634-183d-5033-a7bb-9817fa2bca1d | note | Standard / Specification - PS 22.1.10
d3b0839c-cdce-53aa-9a5c-51dfe6e692ff | note | Verifying Document - Datasheet
25f74cf7-3f05-50e4-8264-713bbd8be4b4 | note | Frequency - Prior to Installation
651ea506-19f8-5613-a655-839d293bef5c | note | Verification Activity: Activity - I
1b7ab34b-9e25-52ce-a64a-22fc0b4ff6ec | note | Verification Activity: By - PE
| checkpoint | 3.3.05 - Earthing, Bonding & Surge Protection
832b3628-7d30-535c-bb7d-202622e9385d | note | Acceptance / Conformance Criteria - Install an earth electrode in accordance with the in AS/NZS 3000. Install new Earth Bar and Neutral Bar c/w MEN link.
735e8656-9d0c-5008-b0f7-166f3703b548 | note | Standard / Specification - PS 22.1.11 & 22.6.10
067c2fe0-3d3f-5636-a767-8d2832549f1e | note | Verifying Document - Site Record
e31e4f59-b8df-54e1-a7f7-d14ec10faa84 | note | Frequency - Prior to Installation
cf28b61d-da40-5ece-be49-cd236766e210 | note | Verification Activity: Activity - I
e46aba8c-ae47-5b57-9814-5d36eadc5bfd | note | Verification Activity: By - PE
| section | 3.4. - Lighting Equipment
| checkpoint | 3.4.01 - Design Drawings
095e00e4-0eb1-5e7b-a177-9638afe418b6 | note | Acceptance / Conformance Criteria - Provide drawings of luminaire design and pole locations for review and approval by the Engineer prior to construction.
f398f91f-dbaf-5661-aabf-6cff8e542511 | note | Standard / Specification - PS 22.1.14
8b2c29f6-e84c-501c-92d3-c872fb1de3a6 | note | Verifying Document - Drawings
a61d6787-3f16-51bf-84db-9d884c2b7887 | note | Frequency - Prior to Construction
205d27fa-40c3-576a-a33f-718c99148d12 | note | Verification Activity: Activity - HP
c517acb5-dd2e-5ded-aeac-5a674fd604f1 | note | Verification Activity: By - ENG
| signoff | AUTHORITY HOLDPOINT
| section | 3.5. - Welding
| checkpoint | 3.5.01 - Welding
6488d3db-9bca-5042-b6ea-4c74a26336a5 | note | Acceptance / Conformance Criteria - All welding shall be performed by qualified and experienced tradesmen in accordance with relevant New Zealand or Australian Standards, with the engineer having the right to request certification and welding experience, and, if concerns arise about welding quality, to request at no additional cost X-ray and/or ultrasonic testing of up to 10% of all welds selected by the engineer, with any failures potentially requiring additional testing.
5362db31-ed7e-516c-beb7-3034226d19a2 | note | ○ All welding is to be completed before any corrosion protection treatment is applied.
352072c9-ab26-5d7e-b336-910de2d37d23 | note | Standard / Specification - PS 22.6.6 & 22.7.1
d43a34cd-ac62-5681-a572-8b6bb6df11e2 | note | Verifying Document - Welding Certificates
e7dfff8d-662c-551c-bcc2-fee072282dd4 | note | Frequency - Prior to Construction
a9ff8a00-11fd-5b67-b12a-8ccc43aceb5c | note | Verification Activity: Activity - R
89f2fda0-5d9e-5b0a-92f6-205abd142839 | note | Verification Activity: By - PE
| section | 3.6. - Corrosion Protection
| checkpoint | 3.6.01 - General
72896e6b-1496-553e-9ca1-917c3faf53d3 | note | Acceptance / Conformance Criteria - Notwithstanding anything to the contrary in this specification, where possible all items of plant, equipment and materials shall be manufactured or supplied in materials that will not suffer corrosion. Appropriate materials include galvanised steel, aluminium, fibreglass, stainless steel, etc. All support steelwork, fixings and other galvanised steel shall be hot dip galvanised. The use of electro plated fastenings for external works is not acceptable. All welding is to be completed before any corrosion protection treatment is applied.
0bbb8b27-14a2-58b5-9f7e-d94f70b472bf | note | Standard / Specification - PS 22.7.1
9e754e4f-a430-568c-b84e-ae36fffee793 | note | Verifying Document - Datasheet
1d04f223-a0c0-5ea1-946b-11b1600982f9 | note | Frequency - Prior to Construction
ae758830-b599-51f1-a8fa-fa2ab6e7b087 | note | Verification Activity: Activity - I
08f19036-1e09-59d1-aeea-66a8e3d5f8bf | note | Verification Activity: By - PE
| section | 3.7. - Painting, Protection and Identification
| checkpoint | 3.7.01 - Environmental
3c158550-9ad7-5f9d-8e25-b380eb9b22c0 | note | Acceptance / Conformance Criteria - Select painting and finishes in accordance with the area environmental conditions.
344b6e04-c920-51bd-89db-e058b62aa80e | note | Standard / Specification - PS 22.8.1
c6f21874-db27-55a8-91ce-42db563646ce | note | Verifying Document - Datasheet
335abc26-4098-5add-887e-77be938380ac | note | Frequency - Prior to Painting
900e38da-f633-5753-9305-815674e43b71 | note | Verification Activity: Activity - I
93e7e26b-d80c-5d7b-8e5f-f0d91f2b146c | note | Verification Activity: By - PE
| checkpoint | 3.7.02 - Compliance Review
14f5f3a9-967f-5cff-b65b-7e3e7797ea9f | note | Acceptance / Conformance Criteria - Review the risk assessment and statutory and authority requirements completed as part of the system testing, commissioning and handover requirements and provide labelling and signage as determined.
38c3bcd1-1973-574e-b073-b2bee52972d9 | note | Standard / Specification - PS 22.8.1
f604e0d0-097a-5f09-866c-71863841e911 | note | Verifying Document - Datasheet
8b57db79-c936-55b6-8d02-940c3da87244 | note | Frequency - Prior to Painting
1bbcc248-a321-5d14-92ce-3e6402bc7068 | note | Verification Activity: Activity - R
dfca0a15-69c6-5c6c-9ed8-eb6f30f51a40 | note | Verification Activity: By - PE
| checkpoint | 3.7.03 - Colours
b0f652aa-80be-5403-bfd1-7ff206147c07 | note | Acceptance / Conformance Criteria - Paint colours nominated are to be in accordance with NZS 5807
e32987fb-2ce5-52e1-887f-355eb36055e1 | note | Standard / Specification - PS 22.8.6 NZS 5807
34e93b68-df2b-572c-b599-d2067ad6d004 | note | Verifying Document - Datasheet
a2885161-7868-53bc-940e-7762d71df3de | note | Frequency - Prior to Painting
f2bad3a8-dbf0-5bfd-af8a-75c8df9c4b78 | note | Verification Activity: Activity - I
c8bf7c47-493b-5bb1-a6f6-f57f73ee30cf | note | Verification Activity: By - PE
| section | 3.8. - Underground Services
| checkpoint | 3.8.01 - Ducting
7bb32db7-84db-5798-9076-3512d047123d | note | Acceptance / Conformance Criteria - Unless shown otherwise all buried ducts shall be the sizes and quantities as indicated on the layout plan. (DIA. 50mm) (DIA. 100mm)
8ca05f73-8158-513a-aeb1-f91c292975bf | note | a) Use heavy duty HD PVC conduit for underground services. Use best practice PVC where possible.
e8e28d47-5ffe-5004-8f3f-1873a43c3d96 | note | b) Colour: Orange for all conduits containing consumer mains, sub-mains or final sub-circuits cabling.
a4a30cf0-4308-5612-b766-267006f0bd61 | note | Standard / Specification - Road Lighting Ducting Layout, PS 22.12.8
2e0069fe-705d-5810-9009-da57592c3352 | note | Verifying Document - Datasheet
05311528-4b4d-5ee6-a869-84f005065342 | note | Frequency - Prior to Installation
4940d2af-8c84-554c-94b0-9640e9051461 | note | Verification Activity: Activity - I
d13afd3d-d64e-5504-a7c7-3f4217c34afa | note | Verification Activity: By - PE
| checkpoint | 3.8.02 - Warning Tape
a12b791c-4680-55d2-b61d-02e06d05db52 | note | Acceptance / Conformance Criteria - Provide orange marker tape complying with AS/NZS 2648.1
a2f457ae-2d1d-577d-a20d-604a11b626e6 | note | Standard / Specification - PS 22.12.9, AS/NZS 2648.1
5505f0cd-d55a-5e0e-bd9f-a6daca7cbd79 | note | Verifying Document - Datasheet
dec8fc02-4681-5363-97ea-f719ef27f005 | note | Frequency - Prior to Installation
f3997441-4a44-5eea-a073-19f4818cf4bf | note | Verification Activity: Activity - I
421c0cde-7ff5-56f7-b958-da2a98943d6d | note | Verification Activity: By - PE
| section | 4.1. - Existing Underground Services
| checkpoint | 4.1.01 - Existing Underground Services
edd9c07f-3d36-5ed0-955f-af4f58f6da74 | note | Acceptance / Conformance Criteria - The contractor shall undertake a comprehensive services identification program prior to beginning site works. This would include as a minimum, review of all service providers maps and drawings, a site scan, and if necessary, a scan using GPR (ground penetrating radar).
59fc6ca4-811f-5488-a610-668b9af5def4 | note | Standard / Specification - PS 22.6.4
99433fd1-5cf0-5acd-8c7d-1ac4008d80fa | note | Verifying Document - Site Record/Survey Record
237d1b1b-3e44-5718-a84a-f0859d4a676f | note | Frequency - Prior to Construction
f9d067a0-3bc8-599f-8116-7fd0112c18d5 | note | Verification Activity: Activity - R
9e4c2f51-5d9f-5c9e-be76-9207939bad99 | note | Verification Activity: By - PE
| section | 4.2. - Survey
| checkpoint | 4.2.01 - Set-out
5aff5e02-f558-5b34-a90a-a225c65e87ac | note | Acceptance / Conformance Criteria - Light columns set out as per design locations.
ccc35a7b-a2cc-5df1-93dd-d873f8104d81 | note | Standard / Specification - IBEX Lighting Plan
b1b39f66-5987-5a33-adc9-954b1eb0803b | note | Verifying Document - Survey Record
cc4863bc-f61c-57bc-b086-b9bf61de0023 | note | Frequency - Prior to Construction
f64f3fe5-743c-5f38-8de0-cce9f6649d27 | note | Verification Activity: Activity - R
eabbb61b-d648-58c1-9fa6-2362bc75440c | note | Verification Activity: By - SV
| section | 4.3. - Underground Services
| checkpoint | 4.3.01 - Trench Excavation
fa2d72e4-f435-54ba-bcbd-33a4eb03fb03 | note | Acceptance / Conformance Criteria - Excavate trench and lay 50mm sand bedding and free from obstraction
a945b395-ba89-58d0-bc26-1fc58dc00dd6 | note | Standard / Specification - PS 22.12.8
f235ea5d-218b-50a8-a812-69c441a64bd4 | note | Verifying Document - Site Record
78273b1c-af7d-5698-84e9-2e35b881121b | note | Frequency - Where Required
21d500ca-1cd4-5195-a8ae-4401a22dc4c1 | note | Verification Activity: Activity - I
00915434-e861-58ea-babe-7a039339a9cc | note | Verification Activity: By - SE
| checkpoint | 4.3.02 - Ducting/Conduit
095a241b-a557-5419-b8c0-7d5209354dfb | note | Acceptance / Conformance Criteria - (a)Separation from LV conduits: Minimum separation between conduits shall be no less than 50mm from other conduits and no less than 100mm from boundary of the trench. Sandy loam is required for building and separation.
508227a1-95e0-57f8-8d76-f8ea779a5133 | note | b) Depth: Conduits shall be buried in trench at a depth no less than that nominated in AS 3000 for the method of installation, with all bends being slow radius bends.
849a8ee7-d3cc-5d21-8d99-094fe1801138 | note | c) Separation from other services: Maintain separation from other services running in parallel and crossing electrical installation as nominated by relevant standard (e.g. AS/NZS 3500 for water services, AS/ACIF S009 for telecommunications, AS 5061 for gas services, etc.).
7248f09f-0ec9-5394-8fdc-64c759a604c0 | note | Standard / Specification - Road Lighting Ducting Layout, PS 22.12.8
e8f82c0b-fbab-535b-b022-15c13e38c55e | note | Verifying Document - Site Record
ef12903f-4a7c-5a08-bfc9-0f1e03ec81ef | note | Frequency - Where Required
29363c44-079e-542a-a3f4-54bce3a8b002 | note | Verification Activity: Activity - I
658f5fb9-e203-5723-9eca-ba0b277b03e0 | note | Verification Activity: By - SE
| checkpoint | 4.3.03 - Survey As-Built
fac666bb-03f2-5e18-be39-dd675b96135a | note | Acceptance / Conformance Criteria - Accurately record the routes of underground cables before backfilling
3554c3ac-5f6f-50d2-855a-8415e47095aa | note | Standard / Specification - PS 22.12.9
05b08c1f-dfb8-5aa8-8335-a9b47cda6d63 | note | Verifying Document - Survey Record
17da8a6a-715d-57d8-b7c1-166e7eb624d4 | note | Frequency - After ducts are Installed
553fbbe3-2a90-506e-b988-a0b755e92322 | note | Verification Activity: Activity - H
84a1197d-7118-5d7e-bc8b-475f5554d89b | note | Verification Activity: By - PE
| checkpoint | 4.3.04 - Backfill
14875e7d-acb8-5380-bf57-338109bdfdf4 | note | Acceptance / Conformance Criteria - Backfill trenches with sand as soon as possible after approval of laid and bedded service to a height of 300mm. Place the sand in layers < 150mm thick and compact to the density which applies to the location of the trenches to minimize settlement,
495c4aff-5d3b-5cbd-b525-981138171dd7 | note | Standard / Specification - PS 22.12.8
157b6ccd-1a65-50d3-836b-0178c3a1b2dd | note | Verifying Document - Site Record
f3f24ba3-0093-59a4-b1a3-dbc7cf2bfdb3 | note | Frequency - Where Required
31e820eb-44c3-5dee-9048-b850d0a70fab | note | Verification Activity: Activity - I
3061a857-32ff-58d6-be22-96049effd190 | note | Verification Activity: By - SE
| checkpoint | 4.3.05 - Warning Tape
28de7278-04f9-5ec2-b639-d02c5f1de581 | note | Acceptance / Conformance Criteria - Install orange marker tape complying to AS/NZS 2648.1. Install marker tape at 150mm or 50% of the depth of burial, whichever is greater, below finished ground level.
4dac0845-87a9-5445-91c5-0a8c322d0983 | note | Standard / Specification - PS 22.12.9
aba50031-fa91-5017-9ddd-1d5694a17664 | note | Verifying Document - Site Record
d9b12438-43e9-5e90-8eb0-ae6cc7282c59 | note | Frequency - Where Required
e154251a-fea2-5971-a19b-944b4f7c1879 | note | Verification Activity: Activity - I
3595378b-4d11-5ad8-a61d-2f59d160c405 | note | Verification Activity: By - SE
| section | 4.4. - Lighting
| checkpoint | 4.4.01 - Shear Base
5d00bfb7-19ca-5150-a5d3-a14e8860baa5 | note | Acceptance / Conformance Criteria - Ensure the shear base is installed as per the NZTA M26 specification and in the correct location as per the latest IFC drawing.
2d87b1dc-9215-5d99-aea6-ecc2b2032f30 | note | Standard / Specification - NZTA M26, IBEX Lighting Plan
54826512-bd73-5160-a0e0-065694be0604 | note | Verifying Document - Site Record
c9ca5705-7790-553d-8571-5fbfd5328f26 | note | Frequency - Where Required
057c784a-80a1-5198-9077-ce36c112f05c | note | Verification Activity: Activity - I
e818e6f6-b8d2-5855-a97a-a0de1bfc4118 | note | Verification Activity: By - SE
| checkpoint | 4.4.02 - Column Installation
193c0d7e-c568-50a0-82d9-e0d9d9172ef2 | note | Acceptance / Conformance Criteria - Columns shall be positioned 1.0m behind the kerb unless stated otherwise or advised.
4316c88e-7d07-5035-9acf-4a994f200894 | note | Allowable tolerances of the column location are:
c16acce1-868c-5200-b5b2-0a06d1094293 | note | A) 0.5m Parrallel to the carriageway
045be0c0-acd4-5d84-a08f-32a3a318571a | note | B) 0.2m Perpendicular to the carriageway
f1411082-f884-581b-918e-37c29ae9ee9c | note | C) 0.2m Vertically
ce3f2aff-7ca7-5d55-a9d7-bfdc13d3943b | note | ○ Ensure columns are oriented correctly and have the correct outreach arm lengths.
a1441cca-e6b5-5104-976c-89001fcf9a86 | note | Standard / Specification - IBEX Lighting Plan
f84550e6-30eb-5220-9ffa-cce115b8698a | note | Verifying Document - Site Record
7e90effe-782b-5e02-994c-c36246f87cf1 | note | Frequency - Each Column
dca78346-fe48-5162-90f2-dd66cc507d67 | note | Verification Activity: Activity - I
54d49b35-ca36-5663-aa6a-526ce413c8b4 | note | Verification Activity: By - SE
| checkpoint | 4.4.03 - Luminaire
54f9b4e3-11af-59b2-a6d7-ea9965ff3cfc | note | Acceptance / Conformance Criteria - Ensure the correct luminaire type and tilt angle is installed as per the latest IFC drawings
b13ab339-0818-5e70-9027-e718949dae57 | note | Standard / Specification - IBEX Lighting Plan
2858aa6f-de34-5b2a-91a3-a3bf268c7a4a | note | Verifying Document - Site Record
c536b2e2-e0d9-5479-9870-9a2b35d27892 | note | Frequency - Each Luminaire
56a70913-a79b-5bcf-951c-6c1a71c22887 | note | Verification Activity: Activity - I
d641e2ae-e550-5ed8-8757-7f100ca7eab6 | note | Verification Activity: By - SE
| section | 4.5. - Montrose Box (MSB-NMB)
| checkpoint | 4.5.01 - Montrose Box (MSB-NMB)
c2706842-0e75-53e6-8c40-9d0f5bc0bf52 | note | Acceptance / Conformance Criteria - Install MSB-NMB as per project specification, Installation and commisioning ITP and the Electrical Services drawings.
a6fe6af2-ce22-5d83-86dc-fdd328156983 | note | Standard / Specification - PS 22.1.7
13fc4f40-8de2-5b9d-b81e-db4612315488 | note | Verifying Document - Site Record
54fa19f6-c108-5ab9-9705-70c0a5216999 | note | Frequency - Once
4e83d3f9-3deb-5f20-9eb2-4127efdfcec7 | note | Verification Activity: Activity - I
94798367-0492-5851-b943-21cbc53f2585 | note | Verification Activity: By - SE
| section | 4.6. - Painting and Protection
| checkpoint | 4.6.01 - Preparation of Surfaces
70cb1f7c-c61e-5a09-b2d7-bd29f186da98 | note | Acceptance / Conformance Criteria - Preparation: all surfaces shall be prepared by thorough cleaning of all dirt, grease, scale, welding flux and corrosion in accordance with AS/NZS 2312.1. For galvanised surfaces that have been subsequently cut or welded, prime the affected area with organic zinc rich coating for protection of steel to AS/NZS2312.1, two pack or accepted alternative
c4bb5395-dd8e-5e31-a959-d414d675ed54 | note | ○ Prime/undercoat all surfaces. Galvanised and non-ferrous surfaces must be etch primed.
4726106a-445b-5c89-a4a8-9dba4f09b6b9 | note | Standard / Specification - PS 22.8.3
e7200ea7-cc4a-5493-ba4a-046fb798de7b | note | Verifying Document - Datasheet
252c1a8d-71ff-594b-a820-126fab373f83 | note | Frequency - Prior to Painting
257e4b5e-df81-5c90-b9ca-6f29692d4fdf | note | Verification Activity: Activity - I
c7fc7563-697f-5876-a29a-59496277e2d8 | note | Verification Activity: By - PE
| checkpoint | 4.6.02 - Application
60572689-2d18-50a3-8026-e18e96b9a358 | note | Acceptance / Conformance Criteria - Apply the first coat immediately after substrate preparation and before contamination, and follow all paint system applications strictly according to the manufacturer's recommendations.
aa2b40a7-e392-5a72-bc2f-53c0e099f0b2 | note | Standard / Specification - PS 22.8.4
85d86c0c-8af6-5256-910f-aacdf412f059 | note | Verifying Document - Site Record
1adef6e9-b0f1-585c-9620-abef599a032e | note | Frequency - After surface preparation
66ff874a-c744-5df7-acae-353d07613d5a | note | Verification Activity: Activity - I
bc7cebc5-21b7-5ffc-9176-8d0c65ad4451 | note | Verification Activity: By - SE
| checkpoint | 4.6.03 - Finishing
314eaee6-88cf-5840-9235-844f22d958f4 | note | Acceptance / Conformance Criteria - Concrete Bases: 2 coats synthetic emulsion paint
8c561367-1880-582e-b2b8-ad1ffb0df841 | note | ○ Equipment Panels/Switchboards: 2 final coats full gloss enamel (c) Equipment: Factory spray application
a928d6c3-0200-5619-973c-00f1c7e1fde3 | note | ○ Other surfaces: 2 final coats full gloss enamel.
26580671-2fe3-5e00-b4d3-49806eb65dc4 | note | Standard / Specification - PS 22.8.5
bce47e6d-0566-52b4-ba30-1527cdf1ecfa | note | Verifying Document - Streetlighting QA Plan
03699c68-2e94-54e7-8050-d6bfe978e37f | note | Frequency - Prior to Construction
6787d926-bc45-5eb1-89e0-11af8a1cbc18 | note | Verification Activity: Activity - I
1b1c35a1-cd49-5aad-b152-1a4ae4035b50 | note | Verification Activity: By - PE
| section | 5.1. - Survey
| checkpoint | 5.1.01 - As-Built Drawings
ae8cc8bd-75f3-50da-8234-fa89d15a911f | note | Acceptance / Conformance Criteria - As-builts reviewed and submitted showing final location of all poles.
e3c43e59-b183-57ef-bd57-a1eccce2898b | note | Standard / Specification - PS 22.9.4
d5f9104a-c07f-5aa7-be60-a1c7547f0390 | note | Verifying Document - Survey Record
1ff52c34-db84-5c78-ad06-f5dd381f1eb4 | note | Frequency - Post Works Completion
15fd6dec-fb47-53c9-99f8-cdaef6fc1074 | note | Verification Activity: Activity - R
dc106640-fa84-577c-b007-a1964dd24ed8 | note | Verification Activity: By - SV
| section | 5.2. - Testing
| checkpoint | 5.2.01 - Electrical Certificate of Compliance (CoC)
7dbd875c-2acc-56d4-be23-5b8c8ea7edcc | note | Acceptance / Conformance Criteria - The contractor shall provide a CoC for the electrical installation. The certificate shall record all test results including insulation resistances, earth continuity and earth resistance. Detail to be included on the CoC is the measured prospective short circuit current for each outlet, switchboards and termination point,
696ba1e3-9362-595f-8255-b73939a9de9f | note | Standard / Specification - PS 22.6.11
0a540a84-1c2e-5c17-ae14-23c57f1d342b | note | Verifying Document - CoC
ad1e12f4-c781-5c3c-afdf-d39130486bba | note | Frequency - Post Works Completion
34d603a5-a2a5-5499-b192-c8f04b247c42 | note | Verification Activity: Activity - R
68684866-1bbe-5786-9d3e-bdef99319628 | note | Verification Activity: By - PE
| checkpoint | 5.2.02 - Twelve-month warranty period
8582cfcd-cab4-570c-9c30-7614cb62d4fd | note | Acceptance / Conformance Criteria - Provide twelve (12) months statutory testing, servicing, maintenance, remediation of defects and warranty of all services systems and equipment installed under this contract from the date of Practical Completion
76f97a3e-ef81-5eb5-8659-4316ed86934a | note | Standard / Specification - PS 22.1.15
691f161c-5e5f-50d6-907d-f4b1a252f2c7 | note | Verifying Document - Warranty
aa762e9d-b73f-53a6-8122-b0f666842e14 | note | Frequency - Datasheets
fa0f5cde-154e-5288-9c78-56b2c4b6b7b9 | note | Verification Activity: Activity - R
0ae7b1f2-9990-592e-8756-d3acb81ffc57 | note | Verification Activity: By - PE
| section | 5.3. - Certification
| checkpoint | 5.3.01 - Final Certification
ec4fbb18-4044-5a09-8f6d-a756fea8ec45 | note | Acceptance / Conformance Criteria - Obtain final certification of the installed systems by an independent electrical inspector approved by the Electricity Workers Registration Board.
9484c330-8fc5-5e0a-8040-d338120737d8 | note | Standard / Specification - PS 22.1.15
48666ff7-66f1-5159-8dbb-1804d6025159 | note | Verifying Document - Final Certificate
ec5e90a4-e3da-5ee5-94c3-f804d568ac19 | note | Frequency - Post Works Completion
e78dd76b-18aa-5142-b968-b51c64ca2967 | note | Verification Activity: Activity - R
7fd320d7-a1b0-5bb2-8e3b-889ea404cd35 | note | Verification Activity: By - PE
| section | 5.4. - Guarantee
| checkpoint | 5.4.01 - Guarantee
a200de05-2cfa-5ed2-9d76-3fa634872f64 | note | Acceptance / Conformance Criteria - Provide guarantees for all equipment including 10-year minimum guarantees for external luminaires and poles.
671c744a-9171-5e3d-9905-a7cfd293a34b | note | Standard / Specification - PS 22.1.15, IBEX Lighting Plan
9b9f8758-4daa-5091-86fc-2835f5eb6832 | note | Verifying Document - Guarantee
f2be27fc-36f5-5208-b732-7010f873cb63 | note | Frequency - Post Works Completion
1247f784-f112-58a0-b204-8165f32d4be7 | note | Verification Activity: Activity - R
38cd6709-c4cd-5392-93d7-9c72dcc65780 | note | Verification Activity: By - PE
| section | 5.5. - Spare Parts Schedule
| checkpoint | 5.5.01 - Spare Parts Schedule
2cc937e0-2c01-57bd-8bba-88fbc0b2e6f5 | note | Acceptance / Conformance Criteria - Provide a comprehensive schedule of maintenance spare parts, detailing recommended quantities, manufacturer prices including packaging and delivery to site, marking and numbering procedures, referencing equipment schedules, and preventive measures such as painting and greasing to avoid deterioration during storage.
3b63edda-6e26-520b-808e-a6c8ac9dd4ba | note | Standard / Specification - PS 22.9.7
8fd5f8af-a6ae-5f20-a250-15dc125447ab | note | Verifying Document - Spare Parts Schedule
bfbd5332-d4ca-56f2-86ba-18f7d960246b | note | Frequency - At least 8 weeks prior to Practical Completion
9fb1f5fe-d0da-52f2-8acd-681efe4d50db | note | Verification Activity: Activity - R
50c1cd1f-4d75-54df-80ef-d1439d8dc1ef | note | Verification Activity: By - PE
| section | 5.6. - Required Operating Instructions
| checkpoint | 5.6.01 - Required Operating Instructions
6ada5fe4-e1f6-5c1c-97f4-d4f22fad9c4e | note | Acceptance / Conformance Criteria - Provide operating instructions and schematic diagrams mounted alongside equipment to meet statutory requirements, e.g., Fire Brigade. Diagrams to be colour-coded, colour-fast, laminated and mounted.
705527d4-8c71-5418-a690-7d30d9eef5a5 | note | Standard / Specification - PS 22.9.7
53cdf0a2-82a9-598d-885c-dd8d490bfeb5 | note | Verifying Document - Site Records
f0381975-1b90-5f26-a575-4df121cb99a2 | note | Frequency - Post Works Completion
2a197893-bf92-5cc9-a429-029a980ba90a | note | Verification Activity: Activity - R
29a98e64-baee-5847-beb4-4b60b492f514 | note | Verification Activity: By - PE
| section | 5.7. - Operating and Maintenance Manuals
| checkpoint | 5.7.01 - Operating and Maintenance Manuals
5bab8eaa-60db-5395-87f7-9ab853782e5f | note | Acceptance / Conformance Criteria - Provide a comprehensive Operating and Maintenance documentation to cover all installations to provide a detailed understanding of the plant and its operation, an aid for training of operators, a reference for fault diagnosis and a framework for preventative and breakdown maintenance.
2b7d29ee-7127-5a17-8b3e-18fc010b1e8d | note | ○ Submit manuals in two stages. Stage 1 include all the sections (generally sections 1-5) of manuals excluding final testing and commissioning records and As Built drawings. This manual shall be submitted well in advance of the Practical Completion and should be signed off by the Engineer at least 4-6 weeks before programme Practical Completion Date.
a7d74c87-a1e3-562c-bf7a-f7f76e035926 | note | ○ A first draft manual should be submitted 8-10 weeks before the practical completion date for review. Subsequently, submit a completed second draft incorporating comments for further review. Finally, include all remaining sections, incorporate all changes and resubmit until all comments are addressed to the satisfaction of the Engineer
780e0df4-63ee-50a7-8d62-529d86f68745 | note | Standard / Specification - PS 22.9.6
221c7536-aaf0-50d4-88d3-505a2fd5bf20 | note | Verifying Document - O&MM
53f3213c-ddf8-5a89-a3d5-f83be3cd0d72 | note | Frequency - 4-6 weeks before programme Practical Completion Date
5f9b7440-34bc-5845-abe6-6d1bfbab4ce2 | note | Verification Activity: Activity - HP
2e524ba2-c124-53ab-921f-77f1ca5bb0f0 | note | Verification Activity: By - ENG
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.7.02 - Inspection and Test Plan
853da2df-0652-5075-a812-639c9f427f12 | note | Acceptance / Conformance Criteria - Installation and commisioning Inspection and Testing Plans to be provided to the satisfaction of the Engineer
01978bc1-2425-5e30-ad75-d9998bcdce4d | note | Standard / Specification - PS 22.9.6, PS 22.9.4
3258e8e0-55f7-5e8f-8ad3-7f0c70ceda7e | note | Verifying Document - ITP
a6f48de1-3d0d-5ab7-a12e-eaff9bae67f3 | note | Frequency - Prior to Installation
44337a02-7d42-5d89-9247-2c4843e9911d | note | Verification Activity: Activity - HP
36ae7990-ff08-5ec4-bbb6-2db4d40aeffe | note | Verification Activity: By - ENG
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 5.7.03 - Final Copies Stage 1 & 2
9457221a-8975-54ea-8d84-f14d02122f86 | note | Acceptance / Conformance Criteria - Submit 3 sets of final volumes within 2 weeks after practical completion. Incorporate feedback from review and from training of Principal’s staff, including preparation and insertion of additional data. Include a section containing commissioning test reports.
68d56e7d-bc36-57db-b057-e3679c0c6686 | note | Standard / Specification - PS 22.9.6
471dd93d-4fd6-5669-9d3e-182432289634 | note | Verifying Document - O&MM
2b81b194-386c-565a-b8c9-b940762ebad5 | note | Frequency - Within 2 weeks after practical completion
bc001c2d-e93d-501b-a1df-42a6dd0964d6 | note | Verification Activity: Activity - R
596f928f-81c0-55cf-b72f-ec8b0a9f0305 | note | Verification Activity: By - PE
| section | 5.8. - Final Contract and Hand-Over Documentation
| checkpoint | 5.8.01 - Final Hand-Over
e299142d-642f-5081-9944-206253217d2e | note | Acceptance / Conformance Criteria - Documentation is required in electronic and hard copy format. Electronic documentation shall be supplied on the latest Microsoft and Autodesk Software versions at the time of Practical Completion.
c6b12f70-7f8a-5031-b25b-62e21a4904f2 | note | Operating and Maintenance Manuals (including Final Commissioning Data):
c9149671-11a3-5142-907f-f18e1f2102f8 | note | ○ Electronic format installed on BMS File Server: 1 set
0e0b32cb-2710-5335-950e-51c4bcf28753 | note | ○ PDF format on USB storage device: 3 sets
0d712266-7649-515e-8d67-ab969d71db3e | note | ○ Hardcopy: 3 sets
c6e4110a-e6c8-539e-a65e-fc98e49f65a6 | note | As-Built Drawings:
6326ea8c-4c44-5dba-9e99-e328af8ecdc9 | note | ○ AutoCAD format on USB storage device: 3 sets
25361ced-8e9f-56c5-932d-6693336b557f | note | ○ Hardcopy full-size with hanging strips: 1 set
0e43eae1-0405-5898-be31-9e312c374ce2 | note | ○ A3 size (included in O&M Manual): 2 sets
d982cc7e-8656-53b3-8696-8ad2fe6b7f34 | note | Revit Model:
b456118c-daba-50e4-b589-e9a3c12e9f75 | note | ○ Refer to the requirements set out in the project BEP (BIM Execution Plan)
dff34ba4-293a-5efe-81a5-b9729e4e94d9 | note | Control Software:
81e063a3-db7f-5d5d-88bc-6648f09157e4 | note | ○ USB storage device: 1 set
2e280229-6736-5169-a58e-2ac2df02d613 | note | OH&S Safety Signage:
783ecc73-8424-537f-8dcf-30d4f548a776 | note | ○ Permanent: 1 set
f212cc3e-f056-56ab-9102-db2258ed9cbb | note | Standard / Specification - PS 22.9.7
42e83937-3bd2-54b2-bce8-8571dae2a67e | note | Verifying Document - Site Records
a1b54ee0-a17d-5191-80a7-f462a0afb6ad | note | Frequency - Post Works Completion
621a68ee-6c39-5710-895d-66f78f03c39e | note | Verification Activity: Activity - R
1a27656e-0961-5097-a305-1f064117de50 | note | Verification Activity: By - PE