## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | CTN-ITP-001 - Removal of Existing Structures | itp | CTN-ITP-001 - Removal of Existing Structures | 1aba3ce5-a4e5-4f7e-994f-ff7bbf9f55c7
| section | 1 - Design and Planning
| checkpoint | 1.1 - Check for correct documentation
817b18bb-702e-5e18-a1b2-284c8e1bb768 | note | Frequency: Prior to commencing any activity
a9e6268b-330f-55ec-b634-a1c3b849f4c0 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
8c4bf775-7159-55c5-9f4e-b9ccfb16c948 | note | – using the correct and complete set of drawings
607d6183-556e-5220-af7d-a20ab900896a | note | – all drawings are the latest revision
109cd616-6f80-5638-973e-1ff2c261ba1c | note | Reference Documents: Drawings and drawing registers
a84443f5-8667-56f4-b49d-d96cd94fd804 | note | Inspection / Test Method: Visual inspection
9c8bb4d0-5825-535b-8171-a1a3ffe4a8ea | note | Record of conformity: This ITP signed
75050a48-30bc-5b66-9292-c23a7b27e986 | note | HP*
46e26e3a-5ca4-5cb4-9423-d1c99317d3e6 | note | Responsibility: Fulton Hogan Engineer
38537439-82c0-5913-b243-715bbe60759b | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
00566a89-788b-5881-be7b-4fdfb71441c3 | note | Frequency: Prior to commencing any activity
afc19906-a0e3-5976-a966-a66be289d429 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
ed2dbe6a-8a98-5635-90e0-731fd7a9c94f | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
36ad26c6-db02-5298-a8bf-4e267b878369 | note | Inspection / Test Method: Visual Inspection
1d1729d0-ed80-5bdf-bb6e-7a06a6599384 | note | Record of conformity: This ITP signed
9fb9aaa3-9d2e-5999-b909-2d5d080de7f8 | note | HP*
df058994-288f-514e-883e-1805df3f7234 | note | Responsibility: Fulton Hogan Engineer
fd635579-5f26-5491-bd55-2c71400fd3bf | date | Date Completed:
| checkpoint | 1.3 - Lift Planning
29dfcb17-1b03-58b5-a80f-634239147555 | note | Frequency: Prior to commencing any activity
f1b731ed-5c52-522a-a881-6ca6ce215877 | note | Acceptance Criteria: Lift plan review compelted
8c237f9f-3a0e-561c-ae09-a99ce1c795d2 | note | Reference Documents: Work Procedure, Lift Plan, HSMP
0c5a7ed6-7a90-5079-b8ab-c6db6784e95d | note | Inspection / Test Method: Verify
c24c45fc-ccae-5e6f-ba0d-c6898b0b5fec | note | Record of conformity: This ITP signed, Lift Plan
200891cd-e46c-5032-9e78-6b0d453488f4 | note | HP*
95046906-a598-5da7-a033-14557266725c | note | Responsibility: Fulton Hogan
bb4c45c1-bd2e-5a8f-a372-f17dc93467ff | date | Date Completed:
| checkpoint | 1.4 - Permiting
bec4c968-be4b-58a8-8a7e-9ad5b470be45 | note | Frequency: Prior to commencing any activity
c3c46484-0e1c-5de4-8cc3-376a84d06d44 | note | Acceptance Criteria: Verify approval of all permits and approval processes for removal of structure
52ef8e3c-1d0d-50be-982a-47849bb49a91 | note | Reference Documents: Work Procedure, HSMP
9c5a331f-03d7-5f58-af78-93b63840b74f | note | Inspection / Test Method: Verify
5db321ad-849f-5522-ab01-9a3078ae934b | note | Record of conformity: This ITP signed
9ffd4e6d-b2b0-5106-8a99-a1abd4d9f673 | note | HP*
de3bba13-3671-57d6-8c66-6ac0721ddd4d | note | Responsibility: Fulton Hogan Engineer
18211a0e-589b-5830-9ff1-3a6b6cd63c45 | date | Date Completed:
| checkpoint | 1.5 - Transport Plan
e7bfc773-8f9a-518d-9a4d-6d67f5b6fb4c | note | Frequency: Prior to commencing any activity
9114c291-fc85-5efc-8000-63f3f1c615ef | note | Acceptance Criteria: Transport route and plan complete, sight and review any transport documentaion
d7f67e9b-a5e9-560f-b25c-655b2df5246b | note | Reference Documents: Work Procedure
ada3b08f-2260-5654-ad6a-a53acd675498 | note | Inspection / Test Method: Verify
97f8cd31-71bf-5cde-86fc-c771c891ab41 | note | Record of conformity: This ITP signed, Route Map
a3aafef6-65dd-58f9-a878-1b9978bfaaf2 | note | HP*
b21d2842-f472-5211-8993-72d52b2c5778 | note | Responsibility: Fulton Hogan Engineer
57d9f657-ab8b-550a-8444-f9c27f59d896 | date | Date Completed:
| checkpoint | 1.6 - Asbestos
3f232614-6821-53f6-b3fc-719ba5f83ea9 | note | Frequency: Prior to commencing any activity
c5a2b937-2024-5932-83ea-4c34a30baa81 | note | Acceptance Criteria: Identify and verify removal of any asbestos material
ad5526a3-900b-541b-93f8-81fe0493ab2f | note | Reference Documents: Work Procedure
8a1c7cc4-b1d5-5fa7-912e-f8a82dba0cca | note | Inspection / Test Method: Verify
44eb7fa0-dfb4-51f1-af1e-69117c57eb42 | note | Record of conformity: This ITP signed
7bf95f35-5196-5976-887f-011979a59c3a | note | HP*
d52a15bc-5477-55e4-bc3a-85e53193f691 | note | Responsibility: Fulton Hogan Engineer
3dd83419-4914-5081-838d-a03412ec3199 | date | Date Completed:
| checkpoint | 1.7 - Exisiting Services
839cb016-6b8d-54e6-beb1-adb4afbc2541 | note | Frequency: Prior to commencing any activity
bb924931-bfe4-520e-92a6-669f3ffab0e7 | note | Acceptance Criteria: Verify the disconnection of any existing services to structure
9f951521-2699-5b1d-8331-8234df9f2233 | note | Reference Documents: Work Procedure
2e5d9da0-2fd9-5318-a9ad-51a90df3e5bf | note | Inspection / Test Method: Verify
00c5e5b0-b8ab-5c5b-9953-58b90242e159 | note | Record of conformity: This ITP signed
46ebe4a1-b75b-595c-9931-7158a8b987a8 | note | HP*
96d088a3-d162-5d2b-b479-165608b95417 | note | Responsibility: Fulton Hogan Engineer
56b19786-8ae3-507f-9778-cc066d0c8da4 | date | Date Completed:
| section | 2 - Structure Removal
| checkpoint | 2.1 - Exclusion Zones
5db35ba3-1e09-58f2-9ac9-df9fc4206478 | note | Frequency: Prior to demolition
e28d4e4e-0116-5d52-bcb7-2dd533546e4d | note | Acceptance Criteria: Identify and establish any no go and exclusion zones required for demolition
edf8650a-5a16-5fa2-af40-7b1ad1c92917 | note | Reference Documents: Work Procedure
3c0c4fbc-c58a-5681-88ed-fafd9f35426e | note | Inspection / Test Method: Inspect
fe1c09aa-6535-52b1-b418-efe449724129 | note | Record of conformity: This ITP signed
16123fa8-f713-5350-9b49-238f6f05620b | note | HP*
d2768fe1-03d9-58c2-81c1-9321d04ef647 | note | Responsibility: Fulton Hogan Engineer
46381fc8-344c-59ed-bfdb-0866015365ec | date | Date Completed:
| checkpoint | 2.2 - Demolition of Incidental Strutures
428c1495-994f-5e4e-8b64-a2f44b1ebe05 | note | Frequency: Prior to concrete pour
41524d0e-b47c-5f90-8299-38d88f024203 | note | Acceptance Criteria: Identify and remove any incidental structures relating to the main structure
607c8df9-e046-58e6-8e00-1fec565cd3a8 | note | Reference Documents: Work Procedure Drawings
23183848-36fb-589b-a525-5a824da599f8 | note | Inspection / Test Method: Inspect
8d5302af-ef46-5dea-8fd4-aab87fbfb192 | note | Record of conformity: This ITP signed
2216c056-dd8c-537e-8a94-f7b83f9e45c9 | note | HP*
77a70266-0100-537f-a03e-f17e1acede07 | note | Responsibility: Fulton Hogan Engineer
18e9a6fe-d2af-509e-9211-9d80281d42b0 | date | Date Completed:
| checkpoint | 2.3 - Relocation Route
d9a8a110-a1c6-501a-817f-7cdb5534698a | note | Frequency: Prior to Removal
3210e208-06f4-5db2-9cd0-8b8bf39267ac | note | Acceptance Criteria: Ensure relocation route is prepped and clear for relocation
93b60acd-747d-5d2e-979d-d32ffa010e57 | note | Reference Documents: Work Procedure
f6c23272-afa0-54a5-9d68-c79ba45e2ceb | note | Inspection / Test Method: Inspect
0a12dee8-0e1c-55c6-906c-38b5134f5291 | note | Record of conformity: This ITP signed, Route Map
5f716c1e-6214-568b-8994-efe3caaefc33 | note | HP*
2f23b183-a364-5192-aca8-5e22bd5efb1e | note | Responsibility: Fulton Hogan Engineer
41aa9b4e-b852-5d10-ad00-f66337c3d25b | date | Date Completed:
| checkpoint | 2.4 - Removal of Structure
de4a5e26-d5ab-5565-9b62-ade1497a86c2 | note | Frequency: Prior to Removal
e2fec0f0-c495-5b75-bdff-87ac1ea0ddc8 | note | Acceptance Criteria: Ensure removal of structure is undertaken per approved documentation
e6f89419-d112-54a0-a261-db01bad88707 | note | Reference Documents: Work Procedure
f1018777-5902-5e83-b376-947e8a7ff9ce | note | Inspection / Test Method: Verify
07083b1d-5006-52f4-936a-1ef9e53dd8b4 | note | Record of conformity: This ITP signed, Lift Plan
d127c9cd-8949-5153-b500-b90d16d9d566 | note | HP*
05ec88c2-6411-5b58-b8ab-8a1675bab1a2 | note | Responsibility: Fulton Hogan Engineer
5899864a-5b7d-57fd-bb28-a1a35754bb81 | date | Date Completed:
| section | 3 - Structure Laydown
| checkpoint | 3.1 - Laydown Area
400df3fb-9600-5f45-98f6-acbe341d7b02 | note | Frequency: Prior to Removal
4a590cd4-98d9-52f9-a073-6ddbd51d9959 | note | Acceptance Criteria: Verify laydown area is ready to receive structure
d1bff902-8945-581c-8bbd-4255c603f370 | note | Reference Documents: Work Procedure
f4579d08-009c-57d8-acc2-0108c96cb117 | note | Inspection / Test Method: Verify
8154b46b-2731-5aef-8557-35a25691cdb8 | note | Record of conformity: This ITP signed
a7899a9a-5ea2-5fc2-8915-b006d2ee36a1 | note | HP*
6a3c4b43-c1c1-5ca5-b3ef-5530303aaa3f | note | Responsibility: Fulton Hogan Engineer
a075f219-18c0-55e8-9321-057a3b35c19c | date | Date Completed:
| checkpoint | 3.2 - Storage
09543e02-b2c2-53ed-b6bd-5d86476c1afb | note | Frequency: Prior to Removal
d2b306e9-f378-52b7-803f-393df581c757 | note | Acceptance Criteria: Structures are stored in such a way as to prevent damage if required
7ba802d7-e36b-5bcd-8e5b-0ec8986a755d | note | Reference Documents: Work Procedure
78f469f6-11f8-5565-a224-6ea0b621cc12 | note | Inspection / Test Method: Verify
9d9163df-e41b-548f-8b59-2cbcda9c5d63 | note | Record of conformity: This ITP signed
d489aa33-a9d2-5ca6-813f-ca40b8cb17bc | note | HP*
4cefbda3-65c0-5a80-aa91-522b98219ee5 | note | Responsibility: Fulton Hogan Engineer
bd18d30c-af8c-5724-a67e-cb444e643db4 | date | Date Completed:
| checkpoint | 3.3 - Photos
4215aa14-3b23-5824-b251-9a909d9d940f | note | Frequency: Prior to Removal
9c352a00-c8a7-5b9f-9f65-7761b76f67dc | note | Acceptance Criteria: Photos of stored materials
79bac840-6d64-5880-9d2b-774148cf0365 | note | Reference Documents: Work Procedure
69303c3d-88d5-5197-9aa6-6b0879e1cbb7 | note | Inspection / Test Method: Verify
126eb712-6582-5738-854a-57c281491f24 | note | Record of conformity: Photos
26d1fe8b-dcdf-5f79-a057-bdd8605e8852 | note | HP*
f9136fc9-784c-51ec-ac6f-36c286e3611c | note | Responsibility: Fulton Hogan Engineer
017f885a-ea90-5c05-ae30-831eb18113a2 | date | Date Completed:
| section | 4 - Closeout
| checkpoint | 4.1 - NCR
f067902f-1607-561d-998d-182ca64ab090 | note | Frequency: Prior to lot closure
9e33086e-8824-53f1-94d6-99dd0ebd1114 | note | Acceptance Criteria: Details of any NCRs to be recorded in CL01E (if applicable)
c2514d4f-1ebe-56da-b455-43f3e8de4200 | note | Reference Documents: CL 01E
e83734ba-d903-5178-bb6f-2701eca58fe8 | note | Inspection / Test Method: Verify
47a09f95-8691-5651-b9c5-a8257d06f7b3 | note | Record of conformity: This ITP signed
d0da66fc-ed83-559c-9b7d-e577062815d9 | note | HP*
66f6000c-6915-540d-876e-d21221fd2614 | note | Responsibility: Fulton Hogan Engineer
1aeffe23-bbee-518c-a61f-a4dea0df3080 | date | Date Completed:
| checkpoint | 4.2 - Permits
306194c8-223d-501d-8a43-a6bd622bd182 | note | Frequency: Prior to lot closure
8ecc36b1-1eda-5da6-a7e6-006124f36362 | note | Acceptance Criteria: Close out applicable permits
203ebe11-f315-54c4-9963-8be44f41e101 | note | Reference Documents: Work Procedure
66804ae2-14db-5c3a-affa-dc7d168da0eb | note | Inspection / Test Method: Verify
cbf2c34a-8b51-5c62-b10c-0152432e94a0 | note | Record of conformity: This ITP signed
9789f563-9fdb-5bbc-844b-a61c432c2cc2 | note | HP*
8242a904-e71d-5d78-bc61-060b0ab88911 | note | Responsibility: Fulton Hogan Engineer
25fb153a-9cba-5cda-8c02-d6bfe15f1c46 | date | Date Completed:
| checkpoint | Final Inspection
6aacb68c-77d4-5b2e-868a-a69ac7db723a | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
d0407496-5f56-5026-9969-d36cc2918732 | textbox | Print Name:
a97f2adc-ad57-50ab-819d-7a78a6c619b9 | textbox | Position:
92ffca2d-80c6-5fc8-a028-bed8e009fad9 | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-002 - Stormwater Drainage Rev2 | itp | CTN-ITP-002 - Stormwater Drainage | fac7423d-0df4-4bcd-857b-389bc7621734
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
6dab3b26-99db-572f-979d-63406946fd43 | note | Frequency: Prior to commencing any activity
22fa997d-079d-5a5d-8fe3-33671d402341 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
e7f67501-d056-5416-a39a-3b2500806bc9 | note | – using the correct and complete set of drawings
e79ee5db-69cd-5233-b254-e335db3bfc8b | note | – all drawings are the latest revision
34952ec4-41eb-553f-ac16-843983d1ef89 | note | – Conflicting documents: The project specific drawings to superceed the specification
fcee553b-5215-57a9-8310-f8c7d9fb20cc | note | Reference Documents: Drawings and drawing registers
6b3901dd-0f21-524e-875e-5d3502235b6c | note | Inspection / Test Method: Visual inspection
21fed605-0bea-555e-adc0-09016919bf89 | note | Record of conformity: This ITP Signed
7f5e0ffb-8aaa-5045-b085-8f164a26ad34 | note | HP*
5cadc6d8-a615-5745-919b-3eb9208d84ea | note | Responsibility: Site Engineer
8f5fbcae-037b-5fae-aef8-f1145ecea79b | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
2bd0cb53-3be3-54c2-b096-4c42a84d45f4 | note | Frequency: Prior to commencing any activity
28b5f892-53af-5f90-a4cc-caa7bd4fa3f3 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
5242e189-f739-58d1-af5d-da3762e1e075 | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
f6005bc6-a342-52fd-ac29-edcd99d03c5f | note | Inspection / Test Method: Visual Inspection
787d3172-a218-58ac-ac35-bfe896bce5e7 | note | Record of conformity: This ITP Signed
2e44080d-9265-5bce-aa0c-c987c9596a49 | note | HP*
c29fc1aa-1c86-5b23-8310-8f3923b3d4bd | note | Responsibility: Site Engineer
d9997bae-e6f2-57d1-958a-eba1c754e90f | date | Date Completed:
| section | 2 - Procurement of Materials
| checkpoint | 2.1 - Precast Reinforced Concrete Pipe Supply
45310c4b-cd1d-516b-bdcf-ed8f754cd19d | note | Frequency: Prior to works commencing, 1 per delivery
3fc29c85-717f-558c-b2e8-27cb68f69307 | note | Acceptance Criteria: Pipe class and size and endwall type as per stormwater drainage details and pit schedule
5f9306c5-428d-52ff-9408-461d27bc26d1 | note | • All concrete pipes shall conform to AS 4058 and subsequent amendments
1f302658-835d-5614-a5f5-d3350b33d269 | note | • All concrete pipes shall be spigot and socket rubber ring joint type
4848b494-3d47-5685-8a10-9cb35c708792 | note | Reference Documents: Drawings C.4.2
526a384b-cf9c-5b53-9d81-dd1b86b80b69 | note | Inspection / Test Method: Verify
eb59256a-1274-5f18-94fa-f4586e9cd066 | note | Record of conformity: This ITP Signed, Order acceptance certificate
36334f13-42eb-56ce-8c9e-26123d80be72 | note | HP*
ef3a3e28-d267-5cc5-a8ae-030fd7a117c8 | note | Responsibility: Site Engineer
d91310f9-5a6a-55bb-9ffd-6647c659cb2a | date | Date Completed:
| checkpoint | 2.2 - Precast Reinforced Concrete Inlet and Outlet Structures supply
54eb03ed-ceca-5afb-85a8-540e0872a2e2 | note | Frequency: Prior to works commencing
0b8ced43-f231-5395-9a4a-01fe9eded662 | note | Acceptance Criteria: The supply of precast inlet and outlet structures shall conform with stormwater drainage details and pit schedule
329effb5-e8c4-5760-9813-c25f63165658 | note | • Concrete shall conform to AS 3600 and shall be supplied by a concrete supplier conforming with AS 1379.
57148c15-f3be-53e3-a3d0-aca07d2aa229 | note | • Concrete shall have a characteristic strength of 32 MPa and maximum aggregate size of 20mm.
bc7b2f1f-321d-568b-b432-e37b8e8de95e | note | • Concrete strength shall be tested in accordance with Section 20.4 of AS 3600.
a83deab7-ceaf-5e84-84ee-51b6d30cd484 | note | • Steel reinforcing shall comply with AS4671:2001
3fc918c9-9aa3-57f2-b482-81565d7390e6 | note | • Structural steel shall comply with the requirements of AS 4100.
2450b7d3-9a83-56cc-8f00-76007c0ff4cd | note | Reference Documents: DWG EW-CE-DRW-526-001 C.4.6a C.4.6e
043e1c90-6d7d-5fb2-b382-d29ffdd3c414 | note | Inspection / Test Method: Verify
8b2f842d-7982-5532-9fb1-a758477f32f2 | note | Record of conformity: This ITP Signed, Recievable Inspection Checklist
662b85b6-2035-5cd6-b5e1-09d4f74d5eaf | note | HP*
a911915e-e856-5934-b561-beed3bbdaebd | note | Responsibility: Site Engineer
62b92bbf-eccd-5a02-8933-83ffaf749ca7 | date | Date Completed:
| checkpoint | 2.3 - Bedding and Backfill Material Specification
16b03644-ebae-5063-98c0-faefed6ae3b1 | note | Frequency: 1 per drain line
c98b4ecd-de77-5751-915b-afb24c6f94e0 | note | Acceptance Criteria: Bedding and Backfilling of trench to be in accordance with drawing EW-CE-DRW-526-001
620f8440-30e1-57ae-a3cb-c75e27a6d694 | note | • Bedding shall be 75mm Class 3 FCR compacted to refusal using hand held mechanical equipment.
c6dfcce5-42b9-5707-b800-ce9a04f07ee3 | note | • See section 4.3 for details
6df43e6f-de22-505c-979a-707dd79a609e | note | Reference Documents: 'DWG EW-CE-DRW-526-001 C.5.4 C.5.20
8c1881c3-0d14-504d-80e6-b172d70d2281 | note | Inspection / Test Method: Verify
460143c2-02c2-5d9b-99fc-c88f141a0a27 | note | Record of conformity: This ITP Signed, Quarry test report
96932845-8c6a-58dc-b7e1-a69c3d1ac530 | note | TP
6b28fef1-55ee-560d-a7f9-f78600e63bad | note | Responsibility: Site Engineer
3e2f910e-c1a7-52b3-b9d0-4e17d51e65e0 | date | Date Completed:
| checkpoint | 2.4 - Setout of Works
a6a23b2f-9bfe-5b06-8a44-ec98125f1051 | note | Frequency: 1 per drain line
2a0b9af4-de72-5c18-94af-83bbb93705ec | note | Acceptance Criteria: Position of culverts confirmed with the superintendent prior to commencement of excavation
541f7c15-ab48-5af3-8d2b-3e685cb588b8 | note | • Minimum 3 profiles access and headwall/endwall
aee9c528-0b67-53cd-a942-cc406dd29e5f | note | Reference Documents: Drawings
b92c5c5f-ff1c-528d-af05-7c29a48f26ea | note | Inspection / Test Method: Visual inspection
494eded2-c9f6-5050-9736-2f768931c62d | note | Record of conformity: Survey records, pegs on ground & this ITP Signed
438a35fc-ec03-50d4-91e0-8367a7ba57fa | note | HP*
5df24450-b0fa-589e-b3c5-be24793110e0 | note | Responsibility: Site Engineer
9a882aa8-6dee-5c7f-96b4-73ed6dc76226 | date | Date Completed:
| section | 3 - Installation of Underground Stormwater Drainage
| checkpoint | 3.1 - Excavation for pipe
a18a35ee-1c00-5a2f-88eb-d9da29ef9d7b | note | Frequency: Each Lot
cdf9b7bc-ee94-5e88-b695-29a7a2cc565f | note | Acceptance Criteria: The line of cut for each side of the trench shall be marked out on the surface before excavation commences.
40c0b681-046a-5dea-aa6a-65638dfe098a | note | • Trenches shall be kept free from water, debris and falling earth.
567e1d65-b5e2-58d9-9fdf-1426cc9320d9 | note | • The final trimming of the bottom 150mm of trench excavation must not be carried out until immediately prior to concreting or placing of pipe bedding. Excavation must be completed for a minimum of 10 metres length ahead of pipe laying.
4fd4a38a-846d-5cf3-baaf-bbafe8aa0fd5 | note | Reference Documents: Drawings C.4.8b
e6adfe58-588e-5c1a-937b-4f55b5e61b18 | note | Inspection / Test Method: Visual Inspection
290d76ff-5c14-50aa-b4a4-11d73018cbe7 | note | Record of conformity: This ITP Signed
bce85242-dee6-5ca4-af9f-ef66e0df2da1 | note | IP
6d0a1678-8fea-5664-ab83-264e7b75ff3d | note | Responsibility: Site Engineer
51f4550d-e32f-55ca-8853-4b5cdff8b1d0 | date | Date Completed:
| checkpoint | 3.2 - Trench Inspection
3b3ce360-549c-5c60-a216-5e089a4d0a20 | note | Frequency: Each Lot
152ce3fb-8317-5480-8b45-427499f23bfd | note | Acceptance Criteria: Superintendent shall Witness excavation prior to bedding or laying pipes, confirm pipe is placed at correct alignment
d8a8e3fa-1c04-5643-a862-080bcc9de5d9 | note | Reference Documents: C.5.20
b46400ae-5ad5-5d17-9933-998c680e7a2c | note | Inspection / Test Method: Visual Inspection
2f0a143a-6168-5b7c-8198-deeaa66f8a4b | note | Record of conformity: This ITP Signed
ec856e1e-8272-5f83-89b7-badac082e1fa | note | WP
9cacfe14-88b5-5600-8133-48a7d43a2314 | note | Responsibility: Site Engineer
61ee8cf9-f8e8-5936-9abd-a20e82bf019e | date | Date Completed:
| checkpoint | 3.3 - Trench Base Preparation / Bedding
f877edc8-1aef-56a6-b9af-bcc19dd2af6e | note | Frequency: Each Lot
66c0e54a-af0f-5360-ad69-a2c7ccb2a35e | note | Acceptance Criteria: Trench bedding shall be 75mm Class 3 FCR compacted to refusal using hand held mechanical equipment for all plavement types.
6e200539-7095-5fc0-90dd-d5b0b1ced77c | note | Reference Documents: DWG EW-CE-DRW-526-001 C.5.4
f66ab937-b4da-58f9-9bcf-024eb358538a | note | Inspection / Test Method: Visual inspection / Measure
3ff6836c-7784-5ca1-8f96-040678918e90 | note | Record of conformity: This ITP Signed
24d308f2-ad7a-59c2-8969-fe00ec29a8df | note | IP
69994507-61cc-5ea3-ad8f-411f4185d53c | note | Responsibility: Site Engineer
9f1bd57c-5728-5512-87f3-c0364b672d69 | date | Date Completed:
| checkpoint | 3.4 - Haunching
cef2d575-8e51-50a8-a989-e96048efe533 | note | Frequency: Each Lot
e8325800-95f0-5b48-a069-b06535464b7b | note | Acceptance Criteria: Huanching layer to be placed reaching a height equal to 30% of nominal pipe diameter
d9026870-e386-5b24-91d8-6299c8f96d14 | note | • Haunch Zone to be compacted to refusal using hand held mechanical equipment
c7a77029-2878-59dd-8cf5-f255eaa56ae4 | note | Reference Documents: DWG EW-CE-DRW-526-001
edb5d190-d673-55cd-9311-ffea709594ea | note | Inspection / Test Method: Visual Inspection
2934b60f-ff12-5bbb-825d-21b3dd3f72bf | note | Record of conformity: This ITP Signed
5476e40b-9e14-5749-bf2e-b815de765521 | note | IP
374598a0-9cd3-5a59-b81c-a4dbe0c51af2 | note | Responsibility: Site Engineer
1fb37e64-44ad-515e-90af-d67814278608 | date | Date Completed:
| checkpoint | 3.5 - Laying of pipes
0190c18d-3c22-5bdd-aea0-873ff0f97327 | note | Frequency: Each Lot
0acadd22-802d-524e-bbfe-eb177f9b34d1 | note | Acceptance Criteria: All pipes shall be set in a straight line between access chambers or between access chambers and headwalls.
512a1cef-0844-50a7-94fe-1193ae0cfe6b | note | • On inspection by the Superintendant, any pipe not placed in a straight line shall be replaced at the cost of the Contractor.
68809eab-f711-50ea-86b4-000be27e12ce | note | • Pipes shall be set in an upstream direction unless otherwise approved by the uperintendent.
5ca5a711-f535-5eab-b5ee-6ff0965f4d98 | note | • When laying rubber ring jointed pipes the first pipe in every run of drain shall be firmly staked in position before the remainder of the line is laid. At periods of delay in laying the ends of the pipe shall be adequately fixed to prevent joint creep.
46e67c17-7372-5c0c-b734-dbeebbc71360 | note | Reference Documents: Drawings C.5.1 C.5.5
fe2d0fb5-095c-59b7-b513-f67d523ede9f | note | Inspection / Test Method: Visual Inspection
75a6871f-ae6d-5c10-833f-b822c4076505 | note | Record of conformity: This ITP Signed
dbd20ccf-4dcb-51ab-8f55-f149bd3da1f8 | note | IP
c1e46e21-8511-5c4b-a7de-4a98c6b94304 | note | Responsibility: Site Engineer
7a980c96-d938-586e-a016-894d4a149d07 | date | Date Completed:
| checkpoint | 3.6 - Jointing
fb675360-9ad9-5f5b-ab48-170ae7a36868 | note | Frequency: Each Lot
39f9b538-519d-5b02-a3eb-8b98a180fe29 | note | Acceptance Criteria: Pipes shall be jointed with rubber rings.
bfacb6e7-5b32-575a-aa43-bc56a7c43f34 | note | • Both spigot and socket shall be carefully cleaned of all dirt and foreign material. A clean rubber ring shall be used, accurately guided and centred on the socket and forced into place using appropriate lever tools where necessary.
9e1f0948-1c8e-560e-a07a-c8e9a5122f49 | note | • The joint shall be checked with a gauge to ensure that the rubber ring has travelled uniformly home. Defective joints shall be immediately remade.
1d7f62c1-21be-5f54-abdc-61aafd82e290 | note | Reference Documents: C.5.6 C.5.7
f6d1e92b-1f94-5153-ae54-8e462860cd84 | note | Inspection / Test Method: Visual Inspection
ddb1ed73-bef2-5428-9b8c-c40ff6f6e0c7 | note | Record of conformity: This ITP Signed
48879e23-1974-51c1-a36e-44be189f3601 | note | IP
72589baf-714e-5628-aa53-acfcd871d700 | note | Responsibility: Site Engineer
c5302075-fa13-5e23-b498-a3f8d7c072da | date | Date Completed:
| checkpoint | 3.7 - Drainage Pits
4cacea9d-7c8f-5a13-8cf2-b78fad982415 | note | Frequency: Each Lot
c03d4d31-e754-581f-aacb-1a087ee1118f | note | Acceptance Criteria: Drainage pits shall be in accordance with the stormwater drainage details and pit schedule.
69cb7191-9557-546d-a7bb-e7744b871099 | note | Reference Documents: DWG EW-CE-DRW-526-001 C.5.15
9caacee1-1fc8-533a-8f1e-742064cce534 | note | Inspection / Test Method: Visual Inspection
e9831100-905f-5f73-b327-674b64fd8258 | note | Record of conformity: This ITP Signed
24f67e78-b951-5bad-92bc-e49d4849886d | note | IP
d159f8ca-68a8-547d-a97d-39e792a0ed31 | note | Responsibility: Superintendant, Site Engineer
e927428b-116a-53d7-a462-a739dcea1d8a | date | Date Completed:
| checkpoint | 3.8 - Tolerance
6cb9e26e-d734-5c22-96d5-7dcfd62c0a71 | note | Frequency: Each Lot
98e50bfd-f053-5b2a-ad3f-38226c241ae4 | note | Acceptance Criteria: The horizontal deviation of any piped or box culverted drain shall not exceed 25mm from the true alignment. There shall be no obvious sharp changes of direction.
a58c1c28-1f0b-5921-98f2-09898f18d615 | note | • The maximum deviation from grade shall not exceed + or - 10mm for grades flatter than 1 in 500 and + or - 20mm for grades steeper than 1 in 500.
5436ea0c-d297-5dff-bbe3-1028e5b069b7 | note | • The grade of any piped, box culverted, or open drain shall not exceed + or - 5% for grades flatter than 1 in 500 and + or - 10% for grades steeper than 1 in 500.
5c9e4d31-b208-500f-92b6-75d00d453950 | note | • Invert levels at structures shall not exceed + or - 10mm from the design invert.
6ee7ac2e-4883-502d-b174-367fd3c19c18 | note | Reference Documents: DWG EW-CE-DRW-526-001 C.5.21
4fadc63b-f800-5a89-a756-cbfb5c9ca552 | note | Inspection / Test Method: Verify
a6d1d835-baa1-5d82-8ee5-3012ed861470 | note | Record of conformity: This ITP Signed
c75eaadb-e039-5e06-add9-4c827572b1ce | note | SCP
e1349975-f51b-52cf-a9cd-6290424979c4 | note | Responsibility: Surveyor, Site Engineer
c3a016ca-0bb2-50ec-948a-c99f60e38728 | date | Date Completed:
| section | 4 - Backfilling of Stormwater
| checkpoint | 4.1 - Inspection Prior to Backfilling
428e2b20-7b81-58f9-9a29-a1ec94ca1e29 | note | Frequency: Each Lot
b9e538a0-23e8-5933-9ca6-5e64bf60b83a | note | Acceptance Criteria: Inspection by Superintendant of installed pipes prior to backfilling.
17bb23cb-b30a-5946-8d21-f64738fb6bc6 | note | Reference Documents: C.5.20
c2c93aca-2b8c-5800-8b58-261d70192145 | note | Inspection / Test Method: Visual Inspection
7c303d3f-4187-5a94-bcec-59b21c6c0346 | note | Record of conformity: This ITP Signed
11130f9f-de1d-5fdb-8c50-5e4ea383b009 | note | HP
30772680-efd7-59e7-bb3c-ddeefddad23e | note | Responsibility: Superintendant
f48d209a-0196-5764-b3ee-2674851f1f3b | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 4.2 - Filling
82680afc-e8a2-597a-a53f-b51add2c2374 | note | Frequency: Each Lot
a64cc744-a59b-5991-b70b-34107ccf872a | note | Acceptance Criteria: (i) Under Landscaped Areas
b7b683b9-2455-5a7c-a466-71b1b50d3e43 | note | • Excavated backfill to be 200mm above top of pipe
92a22720-769b-50cd-92eb-76f67047cee5 | note | • From 200mm above pipe to 150mm below surface - Excavated material compacted in 150mm layers to the density of the adjacent soil.
261deb6a-21df-5159-8276-908106eaf570 | note | • Final 150mm - Topsoil
62467eac-cc79-59fd-a5ea-8636c33472e0 | note | (ii) Under Any Pavement
5586684f-a707-5691-af85-0ef721f80658 | note | • Haunching to 30% of pipe nominal diameter
4f7368f6-f737-5789-8a27-a04361fd5ecf | note | • Backfill material to the base of the pavement
13379fdf-8454-5b18-b5fa-c6f86f7c24b8 | note | Reference Documents: DWG EW-CE-DRW-526-001
42a9f3f4-3da7-5d0c-803f-c5f3ad4ec81b | note | Inspection / Test Method: Visual Inspection
7b2dded2-8e8c-5678-9db7-60953a98bc58 | note | Record of conformity: This ITP Signed
1e0d372b-07ff-5f4a-a1db-158539064f51 | note | IP
7a9f5725-ad62-584f-b57d-b5f556d1ec7e | note | Responsibility: Site Engineer
b6c0475d-a2e5-50f7-bd91-09a78d42346c | date | Date Completed:
| checkpoint | 4.3 - Testing and Acceptance of Fill Materials
839eaa79-d0a4-5c71-a390-8249879d6e36 | note | Frequency: 1 per layer per drain line. Test at each layer, near access chambers and along line.
17b5c274-580e-5c4a-960d-26177f88de60 | note | Acceptance Criteria: Bedding and backfill materials shall be placed and compacted in layers not exceeding 150mm loose thickness and shall be assessed for compaction and moisture content.
1c6590d1-a8c0-5af2-a671-c9fa8daefa1e | note | • Bedding shall be compacted to refusal using hand held mechanical equipment.
ac8aa0ed-85aa-59b0-97ad-8b91a84e4a48 | note | • Backfill material with nominal size < 40mm after compaction shall be compacted to a mean density ratio of not less than 97% CDR.
fe7cf077-c588-58ee-9254-e3eaf6ac0a42 | note | • Backfill material with a swell equal to or greater than 2.5% shall be maintained at a mean moisture ratio of 92% between the completion of rolling and the placement of the overlying layer.
e91c6bcf-b9dd-5a43-9f25-15e2ba17527a | note | Reference Documents: DWG EW-CE-DRW-526-001
b92d8a68-ca21-510c-b47c-ed49e8a3a4c5 | note | Inspection / Test Method: Verify
10af9105-de28-5933-a026-8c7755a5e213 | note | Record of conformity: Compaction Test Result OR This ITP Signed
1248edf6-02e7-5e35-afd6-6083121f8fd4 | note | TP
b1c4e032-f594-5ba3-9dc4-ff2bfcca3e2c | note | Responsibility: Site Engineer
31198d0f-c691-54c9-b59a-1ee2ccf5ecfa | date | Date Completed:
| section | 5 - Finishing and Commissioning
| checkpoint | 5.1 - Finishing and Rendering Pipes
3a3cfbf2-42f5-5214-bece-9fb1313396bc | note | Frequency: Each Lot
0c5d1670-51d7-5c32-ac78-c5d51cfd0674 | note | Acceptance Criteria: All stormwater inlet and outlet connections shall be cut trimmed neat and finished with cementitious mortar.
8cfd4156-9557-5f4b-b3c9-116e5e805efd | note | Reference Documents: Work Procedure
7e8903a4-9893-5265-934e-62ffb571488b | note | Inspection / Test Method: Verify
9a833394-20f0-5ac1-830c-dbb1b3254a86 | note | Record of conformity: This ITP Signed
24364968-127b-5e2a-b297-762cd920baa2 | note | IP
ff694b32-7b02-5e34-8880-ce31a8cd63f8 | note | Responsibility: Site Engineer
1d4dc3ff-87f4-53b7-877b-e357c751d4d4 | date | Date Completed:
| checkpoint | 5.2 - As-Constructed survey and documentation
bbc3e1ed-78dd-5b93-9782-f268c824ebbe | note | Frequency: Each Lot
3dd0b7a4-0277-597c-a03e-a908f411f4ca | note | Acceptance Criteria: The survey shall include all invert levels at access chambers, entry pits, headwalls and endwalls, centre to centre distance of pits, distances from centre of pits to headwalls or endwalls, size of pipes, types of pipes and bedding, location of pits in relation to adjacent boundaries, reduced levels of access chamber and entry pit covers.
f8435ac8-4ed7-540d-a7e1-2b05800bdaf0 | note | • Lot Maps shall be completed to show the extent of works for each lot.
24e84b7a-c86b-53ad-8ee9-23ce43bf2e2f | note | Reference Documents: C.5.21
3650747f-f64a-57ab-9cb4-90d4ffc96244 | note | Inspection / Test Method: Review
fca47132-3529-57f3-95fd-59602f6f24a7 | note | Record of conformity: This ITP Signed
37eec2b4-bac9-59a5-8bb2-9b1b52a9ff87 | note | HP*
9696be4c-6863-5ab9-b1ea-12f5a7c49dca | note | Responsibility: Site Engineer / Superintendent
2d73915a-0e31-57a3-87ff-91bfdcb49186 | date | Date Completed:
| checkpoint | Final Inspection
2582c3d1-e318-5f0c-8cb6-02d0c3ad9447 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
576e7a40-60cc-51ea-b563-ce945e365a0e | textbox | Print Name:
a6e488e5-3434-599a-a2d0-17d39784da42 | textbox | Position:
a963f957-654f-55b9-bc48-912667ce3e6b | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-003 - Service Trenching & Install | itp | CTN-ITP-003 - Service Trenching & Install | 5692b6bd-2570-4ca8-9480-0d71affdca35
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
98395e3b-5752-5346-97ab-cc8b46b51337 | note | Frequency: Prior to commencing any activity
1cfeb314-6757-5c92-9386-4f55ac3c06f9 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
e9b7c459-9a19-51bb-a840-073b722d46dc | note | – using the correct and complete set of drawings
c609d7a8-5cfd-54f4-a281-e36b3d923575 | note | – all drawings are the latest revision
13b668d2-d344-5009-b9cc-1202b9356193 | note | Reference Documents: Drawings and drawing registers
4673e7cf-bdbd-5530-b5d0-5c801397662c | note | Inspection / Test Method: Visual inspection
e4106d42-5af9-5039-8b25-5632e7bfc3c8 | note | Record of conformity: This ITP signed off
5e1fd4c6-11f2-531b-b509-a7aa5c2b5ead | note | IP
514600f1-bf8e-5502-ae0b-12c435fb2049 | note | Responsibility: Site Engineer
297f9b90-2e37-545e-9a00-03c7413d4f7a | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
71ecd841-f4e9-57f9-b4cf-60d9af851dbb | note | Frequency: Prior to commencing any activity
c624d405-6cb0-5c81-9193-02306d8cab9d | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
27391a8b-71f0-5a8d-ad60-a506dcdbc3df | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
78443518-6dc6-58e9-90aa-65aea594c56f | note | Inspection / Test Method: Visual Inspection
0cf1820f-a1fd-558f-bbf4-356d42d0773c | note | Record of conformity: This ITP signed off
bd3716d9-fa44-534f-9ad8-14fd3137bbf5 | note | IP
9e343599-a312-580c-a136-4edea83fd1f9 | note | Responsibility: Site Engineer
e6aa4c5a-8c12-53dd-ab4f-cc2750aaf206 | date | Date Completed:
| checkpoint | 1.3 - Materials
d438faef-3cea-5e87-898f-819d14622e36 | note | Frequency: Per Lot
34383b21-74eb-5cd8-b4c3-91ea7ac13a60 | note | Acceptance Criteria: Bedding sand provided over rock and above conduit
90b49e8a-a542-540b-bdc4-49ff6dea13d9 | note | • 20mm Class 3 FCR for backfill
394034a4-bfdb-5a25-8088-0a8f8a36d770 | note | Reference Documents: C.19, Drawings
18eb9283-1e84-59dc-bf8a-9e51176a139b | note | Inspection / Test Method: Verify
37085c4f-52c1-5d98-b58f-eda05cde889b | note | Record of conformity: This ITP signed, Recievable Inspection checklist
0e906e1c-345b-5e5f-8ead-01dbc21083bb | note | IP
c6fd3ad2-1601-538d-a8a1-d946b846b5ed | note | Responsibility: Site Engineer
db5ebe70-6aed-5e48-be41-1b4c6c3638e4 | date | Date Completed:
| section | 2 - Construction Works
| checkpoint | 2.1 - Survey set-out
c538adf4-e1b6-52ff-9083-1a22584924e6 | note | Frequency: As required
8c4d0ae1-25f8-5b29-9c6c-6f6f15017c59 | note | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works will meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
0a2a5ead-2f76-5d52-889c-2cbc89c3e4d1 | note | Reference Documents: Drawings
5225c28d-8e9e-5eba-a675-e45b40f9bb81 | note | Inspection / Test Method: Verify
9a03e515-6094-508e-86f6-284bb3907662 | note | Record of conformity: This ITP signed
d6067c3b-3d13-57c4-bdbf-6529d4f8fe0f | note | HP*
ea4fd987-23e8-51b7-a06b-b91c2b08589c | note | Responsibility: Site Engineer
fcaf231c-538a-5e39-86c0-9740ed2791f4 | date | Date Completed:
| checkpoint | 2.2 - Excavation/Boring & Trenching
5672df9d-8058-572b-a55a-76e4cef8a8ca | note | Frequency: Prior to Backfill
be0d3fef-0049-5b12-8be9-cdf62da2481e | note | Acceptance Criteria: Superintendent to inspect completed tench
d13d6708-30c7-5b4a-8606-2ac03a928397 | note | ○ Depth Requirements:
f37e45a6-6d07-5ef9-bd62-a32e28a2324d | note | • Where conduits are laid under carriageway pavements, the minimum cover from top of conduit to the pavement surface shall be 600 mm
f3599065-f450-580e-b446-49a54d4db2d3 | note | Reference Documents: C.19, Drawings
3cfa710c-e4b2-58af-870d-bbaf0ad5adfd | note | Inspection / Test Method: Measure
6ec625a3-49a2-5de6-af54-bfac892a98f8 | note | Record of conformity: This ITP signed
c543fb18-57ed-55c5-8393-4fd0545fac60 | note | HP
11132222-b1b0-5f67-b0b8-a14df50b87ae | note | Responsibility: Site Engineer
81e489b2-c3f9-56d3-98bd-7b91221a3926 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Installation of Conduits
44bebb22-2832-55cc-b9e2-71d5909b9c2e | note | Frequency: Prior to installation of conduits
b054629e-ae5f-5723-85c4-b9c5fb56ff30 | note | Acceptance Criteria: All conduit installation works for electrical wiring and communications cabling shall be carried out by, or under the direct supervision of, appropriately registered and licensed personnel
18ab69cd-5335-515a-94ab-895ac37cd9af | note | – 100mm bedding sand provided over rock
caa85590-0d84-5a9b-9f17-4a4f0dd79b10 | note | – 150mm bedding sand provided above conduit
39c545f2-9e41-528f-ab64-8637c33c0e4c | note | Reference Documents: C.18, Drawings
5e4d1fda-66cc-52a7-bf1c-b2b9e9df16e1 | note | Inspection / Test Method: Verify
d25bf0b7-c78a-507d-852a-be16ad6fd7f7 | note | Record of conformity: This ITP signed, Subcontractor competencies on salesforce
3964a5ef-6a2c-58a3-a805-680963a8949d | note | WP
a84879ec-6b17-5a00-9fae-26fdcfb0c6e1 | note | Responsibility: Site Engineer / QAV
21e481d2-a618-5a56-8841-de96d5f97f40 | date | Date Completed:
| checkpoint | 2.4 - Back Fill of Trenches
2dde1a81-e64c-5935-adc3-07e44625d88e | note | Frequency: Each Lot
94b92754-a9f6-5cb3-8497-e03ab7d8f795 | note | Acceptance Criteria: Place and Compact fill in no greater than 300mm layers
1324cf25-c413-5630-9ffe-91153ce06123 | note | – minimum 300mm 20mm Class 3 FCR below pavement/ground level
07ba2a96-5eff-5d68-8d46-3093e75fbb87 | note | – Where trench passes under load bearing zones maximum 200mm layers
13bb0ea3-96b8-58a1-b81d-7975f821a11c | note | – conduits under area to be paved backfilled with select back fill to subgrade level
b84b18a9-2295-5509-999c-e9e820baf318 | note | – conduits under area not to be paved backfilled with select fill to 0.4m above top of conduit and common back fill above that
d1405dfe-86c9-54a0-900b-5e18567c98a9 | note | Reference Documents: C.19, Drawings
b88a5bd4-65a7-5e7c-9a59-1c177a2241ca | note | Inspection / Test Method: Measure
e09b6482-29b0-594d-bfd2-5495b28d9e46 | note | Record of conformity: This ITP signed
93e8a315-f18e-502e-b992-00cf37e13770 | note | IP
03a8e810-ada2-5b3a-acb7-257aea7a18e6 | note | Responsibility: Site Engineer
d000c1b6-e57b-51a4-8855-b85038c2f637 | date | Date Completed:
| checkpoint | 2.6 - Compaction
066019e7-b05b-52ea-b026-17e953982a61 | note | Frequency: Each Lot
ec36d1bc-7ca6-5342-8edc-1d12a085a9a8 | note | Acceptance Criteria: Superintendent to inspect testing and compaction of subgrade
f8651d32-75b4-56ed-ab19-605d74c7c12a | note | • Post compaction falling cone penetrometer >7 blows per 300mm
22fa0e08-4671-54f7-ac9c-692fa784323d | note | Reference Documents: C.19, Drawings
94c988c9-1099-5bf8-ad55-3b01fb55fdba | note | Inspection / Test Method: Verify
7b5e9c73-92cf-5d25-a13d-0740c9de7cfb | note | Record of conformity: This ITP signed
447b1343-ab6b-5a9c-9183-46bd77119812 | note | HP
3e481716-5326-5159-a513-0f840067f074 | note | Responsibility: Site Engineer
b5e88053-ae6a-5504-b35a-a54f5de99aed | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.7 - Compaction
07cff7d5-6c1f-56ae-84a8-c97cb411666c | note | Frequency: Once, prior to use of backfill >40mm
ef556c82-f5c2-5cd1-a14c-bbd4ef538042 | note | Acceptance Criteria: Detailed proposals for the compaction of backfill materials of nominal size greater than 40 mm shall be submitted to the superintendent for review before commencing work.
9e91a89a-65b1-5798-9eee-3defae7d9777 | note | Reference Documents: C.19, Drawings
3ea95739-142c-5519-bdcd-a85632da1f15 | note | Inspection / Test Method: Verify
b32ee638-6efa-563c-be8d-93ccbdf74c72 | note | Record of conformity: Correspondence with superintendent
9ca8c0ce-d56d-581c-b97b-94102fa00ee3 | note | WP
6986eddf-9159-57cd-b917-5eaf079cdfdc | note | Responsibility: Site Engineer / QAV
96065705-b353-5dd3-9b05-94742e2f95b0 | date | Date Completed:
| checkpoint | 2.8 - Installation of marker tape
7fd6b6ca-e2a7-5b8f-8573-fd98d202a009 | note | Frequency: Each Lot
f287f513-fb54-56f9-a824-76aff61cf044 | note | Acceptance Criteria: Marker tape is to be installed above each line of conduits in all trenches where electrical and communications conduits are provided. When constructed in a shared trench, it must be ensured that the electrical warning tape is on top.
fd3dcdd6-f42d-5224-b215-9b653ce35e53 | note | Reference Documents: C.19 TC-2204
a6f6e20d-8148-5f02-b509-5b36f2d764d8 | note | Inspection / Test Method: Visual inspection
a32e9cbb-1b4b-5c55-bf33-3c858dcdd674 | note | Record of conformity: This ITP signed
4140dd07-076d-5aa8-896f-67bc1846f7b2 | note | IP
b7a34db8-2e21-5ec4-aabb-1c6b0f6ca668 | note | Responsibility: Site Engineer
e0d528d9-057f-59ba-b8bd-1bdb8b4e128b | date | Date Completed:
| checkpoint | 2.9 - Cable Pits & Pit Lids
5e8739d1-b8d7-54d8-bae8-36c01a53a691 | note | Frequency: Each Lot
849713c4-f8f0-5f27-873f-e265595c3c2c | note | Acceptance Criteria: Cable pits constructed and installed as per drawings
11928fa9-eee9-5f5e-8f1d-6e118a0cd1c9 | note | • Reinforced concrete apron installed around pits that are in an unsealed area
0f378afb-e330-5907-a86f-dbf6f7f04d4c | note | • Heavy pit lid provided where pit is located in a road pavement
d9f7ffd9-464d-5094-9edd-ade174ed555f | note | • All pits, junction boxes or terminal pits for electrical purposes shall be watertight
27d02435-44c8-5df1-a166-f15f052ca0ca | note | • Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
5f7a860e-e77f-567e-8da1-5a4cce9a0e4e | note | Reference Documents: C.19, Drawings
387176d3-1eee-5ede-8df9-aef44bca723c | note | Inspection / Test Method: Verify
ddbd0da3-984f-502d-b56f-9d57a4f3146d | note | Record of conformity: This ITP signed
ea29dcd7-f13f-5910-9e54-51b72bd5ee74 | note | IP
4b6c98de-c392-50d8-b5bc-6e79f75ffb1f | note | Responsibility: Site Engineer
70a9eebb-5e1b-52cb-8417-4345660fcfd8 | date | Date Completed:
| section | 3 - Completion
| checkpoint | 3.1 - Cleaning of Site
1798777f-b549-5f71-8771-ac3da583c161 | note | Frequency: Each Lot
c9ef86da-33c3-550e-9fe4-3aaa54b9680b | note | Acceptance Criteria: Surplus excavated material shall be removed from site. All affected areas shall be restored to similar conditions that existed prior to work.
3101d30b-a0e8-5251-bd86-16c5e2429cde | note | Reference Documents: C.19, Drawings
df974b32-fb73-53cb-b2a4-37248e5d7ad4 | note | Inspection / Test Method: Visual inspection
bc0f030d-3127-5e7b-bb22-d7a4af581d9d | note | Record of conformity: This ITP signed
baf36d74-6abd-51a1-b09e-47906bef383c | note | IP
5b6c54bb-f38b-5b88-b6f3-bd0527627e26 | note | Responsibility: Site Engineer
8fea8110-9cfc-5847-88fa-93ece98b85a4 | date | Date Completed:
| checkpoint | 3.2 - Recording/As Built
d6877817-692a-5189-a229-6f1190281e76 | note | Frequency: Each Lot
7deba905-8418-5f07-bb5a-1cf585fa043c | note | Acceptance Criteria: Installed location and depth of conduits, and location of pits and pedestals, shall be accurately recorded on as-constructed drawings.
e1b15500-3633-5021-af6d-df4f95e9a016 | note | • Lot Maps shall be completed to show the extent of works for each lot.
610ece33-e69f-56e5-90f6-3c4eefd00efc | note | Reference Documents: C.19, Drawings
4626fffa-d47f-56c1-8200-d7a4689f768a | note | Inspection / Test Method: Verify
3312e6ff-952b-5cb8-a193-4919bbe6ba24 | note | Record of conformity: As Built Drawing
e929ceb2-5189-5225-beb5-000c4d5b6f55 | note | SCP
73db3806-678a-5124-8832-dce1515dd1b2 | note | Responsibility: Site Engineer
a8512c67-2996-5e48-834c-6832e82f7fc4 | date | Date Completed:
| checkpoint | Final Inspection
f36cdcb6-a7fa-534e-b192-573a235bc8c8 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
ca918511-651e-5b12-973b-084cdc3f134f | textbox | Print Name:
e226e2c5-f172-5ad9-9cc4-38e88928cc41 | textbox | Position:
1a6cecce-190a-53e8-8fef-8b2932522f56 | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-004 - Subsurface drains Rev2 | itp | CTN-ITP-004 - Subsurface drains | c3fe24dd-2a8f-4cb2-84ed-ef0ce32fa027
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
066c1c66-527e-5edf-85db-b4fa3d129d67 | note | Frequency: Prior to commencing any activity
15294e71-81ba-5ec6-bd41-794da91f4ad4 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
836eacac-f35d-598d-8051-be285566b557 | note | – using the correct and complete set of drawings
5e86b593-c5a2-5b00-9823-e46a71d6206f | note | – all drawings are the latest revision
1ce295f7-92fb-5df3-8558-0c13e867b61a | note | Reference Documents: Drawings and drawing registers
7231819a-e7ab-5f44-8dfd-9868b1ac515a | note | Inspection / Test Method: Visual inspection
21a8c96d-5095-52bb-82c5-4034b0eea45d | note | Record of conformity: This ITP signed
9f92c5a6-adb4-57fc-aa27-58d311622011 | note | HP*
6ef9ea82-8d28-5828-a28d-693c2995d65a | note | Responsibility: Site Engineer
cb81760a-5d17-54e0-aeb7-90a4af7b75bd | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
b4b69718-0ada-5175-bf8e-195d76c0ab86 | note | Frequency: Prior to commencing any activity
64f982b5-547d-5b3f-89bf-042fafa0e0c2 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
cd8a8d99-c199-523b-ba1e-04f4f0f5d1bd | note | Reference Documents: PSP, EMP, TGS, SWMS, WP
b6698a67-4012-5785-83ec-7254f2a0c55f | note | Inspection / Test Method: Visual Inspection
31e4b749-8803-5ce5-b474-3956bb3661ba | note | Record of conformity: This ITP signed
b5e67521-d4f2-5244-9ec0-fb3734ee817d | note | HP*
2406c6f2-1f05-59bf-a570-6559757580d2 | note | Responsibility: Site Engineer
3bc32fbf-ed50-5aa3-8acb-ed6a1368be8a | date | Date Completed:
| checkpoint | 1.3 - Material Classification
6bb0979c-a500-5e4d-a787-81dade59b41f | note | Frequency: Each Lot
31205855-17c8-53d0-b487-0591fffbb542 | note | Acceptance Criteria: Pipes supplied shall be of the category and diameter shown on the drawings
8c278112-9fc3-556f-9648-afbea616fa34 | note | ○ Material shall be as indicated on the project drawings and / or shall conform to the following:-
6da18bd8-1a07-527f-88cd-db7036ce1528 | note | • uPVC slotted spigot and socket sub-soil drainage pipes.
10a172b1-69c0-5ef9-b464-e1fd6c4aa12c | note | • Fibre reinforced cement slotted spigot and socket sub-soil drainage pipes.
c5ff248f-b7f3-5192-b420-7e3b2fff5e39 | note | • Perforated corrugated polyethylene continuous tubes.
fb12a958-8449-55c8-9f28-b2dacedb74c3 | note | • Geo textile must be of A34
57824b9c-5ef5-555e-a7d2-da0f81b571c6 | note | Reference Documents: DWG EW-CE-DRW-526-001 C.6
6df6de4c-e44a-5338-bcd7-e47257668333 | note | Inspection / Test Method: Verify
38e7c521-3d9a-563c-b3c5-01f0038a8b6b | note | Record of conformity: This ITP signed off
63383860-ebed-5696-aabd-0e2e0e5ac0ae | note | IP
69594c20-b21d-5cdc-929e-fb7b227adb18 | note | Responsibility: Site Engineer
b4402950-949a-5fb5-b378-f752076667c1 | date | Date Completed:
| section | 2 - Construction Works
| checkpoint | 2.1 - Excavation Permit
ee206293-ff7b-53b4-bd93-9a5afe509338 | note | Frequency: Each lot
34626b58-ac0b-5242-bc16-84f659b1a819 | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing.
3f17533f-fe4f-55ff-944c-af14eb5bca07 | note | • Plant and equipment shall be appropriate for the task.
af0576a7-824f-5f19-9de1-0739ff79b5b2 | note | • Excavation operations shall not disturb areas outside the limit of excavation
e44d5cc5-62c0-5c31-b0bc-ddaa89f7399f | note | Reference Documents: Excavation permit
d938083f-d61a-591d-a0f7-f34372d42457 | note | Inspection / Test Method: Verify
6c7ec06e-5a6e-5b17-ac72-bdc19b0761d6 | note | Record of conformity: This ITP Signed
5048d548-5f16-5508-b9ba-28813e569702 | note | HP*
d531d991-8375-5407-98e6-0365f70c41db | note | Responsibility: Site Engineer
e182dd78-2243-5733-82d7-5331c3cc8730 | date | Date Completed:
| checkpoint | 2.2 - Outlets
db7cd0de-58ae-5b52-acbd-fbfd14f46adb | note | Frequency: Each lot
9fca74b7-50b5-59d3-84dc-e70309b239b1 | note | Acceptance Criteria: Superintendent inspection of proposed underground outlet location. Outlets shall be installed through walls of pits, provided inverts are not below the top level of the outfall drain.
039658fc-58e8-5256-953a-95e26b8ab753 | note | Reference Documents: C.6.2
082dd875-647b-5013-8b42-25ce739e1dc0 | note | Inspection / Test Method: Visual Inspection
00f8a321-ac06-5c91-a663-288052d39877 | note | Record of conformity: This ITP Signed
a274c574-5fe9-5f1d-b3ad-ecccaf1d5905 | note | HP
201fdf7f-45d1-55cf-b893-25041fd4b40c | note | Responsibility: QAV
9f04623b-9d0b-509e-bf37-d8b9e6635c21 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - Excavation of Trench
2f38a7e6-4789-53fa-a209-aff1ddd10aa2 | note | Frequency: Specification for trenching
11beb9f4-8441-5718-9775-828ca6758d35 | note | Acceptance Criteria: Excavations for sub-soil drains shall conform to the requirements specified for excavation for services subject to the following specific requirements and modifications:
1caf37e0-8d3a-5ec0-ad14-19f2e95fd0a8 | note | • Trench depth and width shall be as shown on the Drawings.
9d9604aa-91a7-5535-829b-5dc4b90f3f33 | note | • Trench bases shall be uniformly graded to an even fall as necessary to suit whichever of the following is applicable:
213bb479-554a-5941-93c9-b08b20700e56 | note | • Parallel with pavement or kerb and channel formation grade.
1f7af9b0-73a3-5052-a917-715666c5b79a | note | • Parallel with overall grade of stepped footings.
25d7b47d-c806-5b26-bdc4-263249c20061 | note | • Not less than 1:250.
2a22d377-d1aa-50dd-9c7c-d156fd4157b5 | note | ○ If it is not possible to conform to any of the above requirements, the Contractor shall notify the Superintendent and await direction before continuing with the affected part of the work.
fb954c4e-9791-50f0-8eac-e739362a4bee | note | Reference Documents: C.6.1
bd6239be-a2a5-5329-a081-9e3015306a4f | note | Inspection / Test Method: Visual Inspection
9699a788-de13-51f6-a4be-839088556fa0 | note | Record of conformity: This ITP signed
e30d51cc-9904-5da0-970f-d94093d61f13 | note | HP
b134ba3b-7e1c-5b41-a1d6-da1be3891e2e | note | Responsibility: QAV
b0779713-5ccc-5ffa-8d80-80b00811151f | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.4 - Bedding
45d32243-3869-5c32-a7e1-4d5c0aa75a7d | note | Frequency: Each Lot
810606ac-be84-5c0f-aa5f-de6019cbdee4 | note | Acceptance Criteria: The bottom of the trench shall be well compacted and evenly graded suitable material, 25mm minimum depth of 20mm Class 3 FCR
1eb95854-4a74-512b-acfb-9ae876c30cca | note | • If rock excavation was necessary and if the bottom of the trench is uneven, all low and rough areas shall be filled, and solid rock outcrops covered with bedding material to a compacted thickness of not less than 25 mm.
88f78ba3-46db-51bb-9e7a-ac8eba5beeca | note | Reference Documents: C.6.6
7f791891-931d-5f13-8fb8-130aea980ca0 | note | Inspection / Test Method: Visual Inspection
1943fd58-b7d6-5bec-8464-92ed18f1d9eb | note | Record of conformity: This ITP signed
6e90e220-3cf8-5e88-82a9-a88e694e0877 | note | IP
d7b59c46-dbcb-52ff-975e-7f1828b48309 | note | Responsibility: Site Engineer
7d734e67-2ae9-56f2-845a-c69cec12cd7f | date | Date Completed:
| checkpoint | 2.5 - Placing pipes
ceea5b4c-669d-544e-b84f-2be357aea98b | note | Frequency: Each Lot
5e2c6a3c-0073-54e5-a28b-eff2d78c3046 | note | Acceptance Criteria: Sub-Soil drain to be 100mm Dia. PVC Class 1000 Agricultural drain.
f2f2a9e6-199a-541e-8789-6192226975f2 | note | • The pipes shall be laid true to line and gradient on the graded compacted bedding.
176f374f-7d1b-507c-be2b-85c4841e5e21 | note | • Pipes shall be jointed to fit tightly by pushing the spigots firmly into the sockets. For pipes without sockets, special end jointing fittings shall be used.
57d10afe-3d32-5095-9962-8466b44d5b0c | note | • Fittings shall be compatible with pipe material.
9dae1d03-420a-50f1-abdc-1ab2cdd545cb | note | Reference Documents: DWG EW-CE-DRW-526-001 C.6.4
e523941d-d358-5177-9e96-6b22b32499c4 | note | Inspection / Test Method: Visual Inspection
ad7a8e2a-ca4b-5861-b0e0-1e99a367daca | note | Record of conformity: This ITP signed
34f4b0da-8c21-595e-ad5c-a726f429074c | note | IP
b403f513-7a49-5bcc-a9a6-e2ceddd3fba5 | note | Responsibility: Site Engineer
ed4d8c78-c283-5053-9305-b766fa00266e | date | Date Completed:
| checkpoint | 2.6 - Backfilling
12942b0b-54d8-576a-9eb8-d74ad450bc13 | note | Frequency: Each Lot
04022310-23a4-5f89-adb0-a9dc5156f7dc | note | Acceptance Criteria: Superintendant inspection of Subsoil drain backfill prior to covering
1d2fc924-48f4-54bd-8dab-f3954d8d74fd | note | • Backfill needs to to encase subsoil drain and cover upto 150mm over to allow for sediment collection.
858383f0-6745-5622-b743-f18625bf69a3 | note | • Backfill to be 14mm screenings to subgrade.
3c6dd8e1-4284-573a-b205-af1e3251e6f4 | note | Reference Documents: C.6.5
bed6fc06-2060-5093-b21f-9440f05f2899 | note | Inspection / Test Method: Visual Inspection
f9de70b7-2ca1-50dd-bf05-c5b6aeb6fd26 | note | Record of conformity: This ITP signed
3fb0279d-65a6-555e-bf95-eac73414bb9f | note | HP
d7eba938-5900-5b41-8dcb-1aa5acfaa01b | note | Responsibility: QAV
66ba9565-34ef-5420-b363-26fec86cda41 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.6 - Backfilling
26841da4-db9b-50af-b431-caad4730c580 | note | Frequency: Each Lot
bb2ffcc1-1543-5ad8-958e-6369c43e47b9 | note | Acceptance Criteria: At full depth pavement joints 100ø class 1000 pvc pipe sub-surface drain type 2 with filter fabric around trench (150mm Overlap) with "no fines" concrete filter
b621b5c6-d8a3-55ce-b483-91795b9d5370 | note | • Material (with 4% cement & compacted).
24e715df-e2e4-535d-8cb5-d62d4e03c37c | note | Reference Documents: DWG EW-CE-DRW-416-001 C.6.5
14900efa-e10d-5359-b287-2f1fde2b708a | note | Inspection / Test Method: Visual Inspection
59a3c80c-f157-53e9-a215-00b8e08488af | note | Record of conformity: This ITP signed
4c5e342c-b8c4-5ee2-b9f9-971e85a8b1b6 | note | HP
3b5e06e7-6434-5a0d-93df-9abb94e0f186 | note | Responsibility: QAV
f14b155d-fe58-5d9a-95b3-4e63700ecf84 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.8 - Access Points and Flushouts
f0ba6c71-ee8e-5e43-bd23-73909d0b668c | note | Frequency: Each Lot
04c1e4b3-1891-5aaa-829d-e2c6eb12be88 | note | Acceptance Criteria: A flush out riser is to be located at the Back of kerb (BOK), comprsing of 100mm UPVC PIPE, capped.
a76daed8-ac7a-52a6-a449-7f693bd8a212 | note | • Minimum 200m intervals along road alignments, a single flushout points at high point or at locations within WSUD/Raingardens.
c43ed8cb-e32d-5fb5-8400-258f3681c94e | note | Reference Documents: C.6.5
092e1d17-fa57-558c-a5e1-cfd09eb916ae | note | Inspection / Test Method: Verify
a54cceae-a483-5d49-bbfa-621f51593b20 | note | Record of conformity: This ITP signed
57a09e43-32f0-55fa-a96f-aab8ab896a82 | note | IP
fffda4ce-135c-51c0-9bc9-8ee79b1c7b1e | note | Responsibility: Site Engineer
040bf974-0cb5-5c9a-981a-e3602154a9c1 | date | Date Completed:
| section | 3 - Finishing and Commissioning
| checkpoint | 3.1 - As-Constructed survey and documentation
76652f08-9752-5e23-935c-12bc23450d03 | note | Frequency: Each Lot
0fb1a4d0-a2bc-5777-a2bb-257a72d586f3 | note | Acceptance Criteria: The survey shall include pickup of location and depth of installed sub-soil drainage and location of any inlet/outlet/flush out points.
e8da6498-b1dc-55b1-866a-9c4d7fdb5300 | note | • Lot Maps shall be completed to show the extent of works for each lot.
a430d98a-0dc5-5152-8b29-0cd77c9eb516 | note | Inspection / Test Method: Review
130b1101-761c-5a91-a2ef-6dadf861ff77 | note | Record of conformity: This ITP Signed
d11644e6-a9dd-569f-88eb-95d57ecdcdee | note | HP*
ac89ae7f-722e-5db6-8ac5-758c9c90fcb5 | note | Responsibility: Site Engineer / Superintendent
735e2674-34af-50ef-beea-5f280b3c95fa | date | Date Completed:
| checkpoint | Final Inspection
ab6d9a00-47ff-5710-96a9-f6c0cd0ef166 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
64d1a98d-a3bb-57f8-8193-f0b4befc4c7a | textbox | Print Name:
0992cef7-ff5e-5402-be02-22926f0fa2a4 | textbox | Position:
88ba982b-0bbd-5c6d-bca2-e223d216bbd5 | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-005 - Asphalt Placement | itp | CTN-ITP-005 - Asphalt Placement | 3acc7465-8e49-4478-898f-4c0baaf34ca4
| section | 1 - Construction Works
| checkpoint | 1.1 - Submission of Mix Design
a0c4232a-ada3-5e74-b342-e30d99b75dbf | note | Frequency: Prior to commencing paving
039bf732-3637-5948-a58e-f5f585d44cd7 | note | Acceptance Criteria: No Asphalt shall be supplied until the mix has been registered and the superintendant approves the mix for use. Only use mixes that are registered by State Growth as 'General Mixes'
592e43b5-e0c8-5600-8f84-c3d1c15fea48 | note | Reference Documents: Cl 407.06
1e0a6236-66a4-57db-95e5-ded34bdc813d | note | Inspection / Test Method: Verify
008bf1d9-4f2c-58f4-b7e1-cdf760a9c93c | note | Record of conformity: Mix registration & correspondence
a20d6b39-06d8-5b90-b516-f98ae9b356fd | note | HP
a16b556d-5203-596a-a55b-84077a1e5f1d | note | Responsibility: FH Engineer/ Asphalt Supervisor / QAV
ee4dff7a-cf09-51fa-9e8a-98941f7a730d | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 1.2 - Implementation of all measures and controls
7e4ba150-bd71-58e9-9c81-0a8b6e786b82 | note | Frequency: Prior to commencing any activity
ec5e58ad-b635-536c-be83-fefa5691c764 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
02c6e13d-34a7-57c3-9e8e-87003350eea2 | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
1a730786-c11c-5762-b16f-8db8b10353ad | note | Inspection / Test Method: Visual Inspection
0b27675e-1612-524a-bdff-1fc6a8b85d79 | note | Record of conformity: This ITP signed off
35b47ce5-2508-5e4a-84cc-83e2d0bf734d | note | HP*
bcc15dd8-fdb2-5102-b9c7-b0b8a4558062 | note | Responsibility: FH Engineer
ca58188e-afe5-5d27-800e-a799ebf15ba9 | date | Date Completed:
| checkpoint | 1.3 - Site Inspection and Base Condition
caca90a7-bbf1-5472-bc93-32e89c3c1f04 | note | Frequency: Prior to commencing paving
1420f621-67c1-56b3-9494-2dd50a8d4054 | note | Acceptance Criteria: Base condition is acceptable for placement of asphaltic concrete.
8b58e52a-e5b4-5ce4-a261-2eaaab92a9a0 | note | Reference Documents: Work Procedure
ed8ac413-475a-551d-b88f-299446545cc2 | note | Inspection / Test Method: Visual Inspection
f7d6b154-c7f7-578b-94d5-4c0ee0c96d62 | note | Record of conformity: This ITP signed off
34c3f1c2-4acc-573a-9a81-8784c944ee5e | note | IP
4aadfbdb-a094-5025-924a-bf67a30cf292 | note | Responsibility: FH Engineer / Asphalt Supervisor
f301b364-a24b-5c84-98e6-439a73695a15 | date | Date Completed:
| checkpoint | 1.4 - Ambient Conditions for Placing
dc2ddb79-97c2-5fa9-9acb-2c12629cf38a | note | Frequency: Prior to commencing paving
3e91aef1-c75b-5eda-8826-80abaa3f9dd0 | note | Acceptance Criteria: The temperature of the pavement to be surfaced shall have a temperature greater than 10 degrees and no rain shall fall during placement of the mix and the surface shall be dry.
96d75065-0d7d-5351-ab3a-386e5026271f | note | • Primer seal - no primer sealing shall be applied whilst the pavement surface temperature is less than 20 degrees or during wet, windy or rainy conditions, or when adverse weather conditions may prevail at any time during the work.
1b48850b-4e5c-59e0-9d52-637d425ce090 | note | Reference Documents: C.9.13
a06fae9a-8218-55e4-a0de-b76b0db150f1 | note | Inspection / Test Method: Verify
fe0819b4-2441-5270-9db3-a603cff25933 | note | Record of conformity: This ITP Signed off
3fc8b218-0cbc-591b-873b-aac91df1f976 | note | IP
02489932-5e76-5698-9d19-e47307565cd2 | note | Responsibility: FH Engineer / Asphalt Supervisor
60050fa6-0c5b-5c13-9ff6-5f140415ea9e | date | Date Completed:
| section | 2 - Asphalt Placement works
| checkpoint | 2.1 - Tack Coat
f60540c5-39ac-57f8-b9e6-46c6f2e5f59b | note | Frequency: Prior to commencing paving
b14f4600-30b1-5364-9299-18b39c8c3f8d | note | Acceptance Criteria: The tack coat shall consist of a diluted rapid-setting Anionic bitumen emulsion as specified. Application shall take place not less than 30 minutes nor more than 2 hours before placing asphaltic concrete.
027f8410-f578-5f01-adac-28f98fbae4e2 | note | • The tack coat application rate shall achieve a residual bitumen of 0.1 to 0.2 litres per square metre. The actual rate of application will be selected by the Superintendant to suit the class of material.
558d665b-2787-59c1-b381-e016ecc67b3d | note | • Any pools of tack coat which may have formed in surface depressions shall be brushed out
ef0e91c1-d730-5686-ae6e-80dfeef0ae25 | note | Reference Documents: EW-CE-DRW-406-001 EW-CE-DRW-416-001 C.9.12
01a2b96b-9c01-578e-99c2-8d58a020ee96 | note | Inspection / Test Method: Visual Inspection
de10909c-2d3d-5edc-8156-978fff9d44a5 | note | Record of conformity: This ITP Signed off
f3385766-5c5b-56fc-865d-c82e55203f33 | note | WP
52d68d31-bba3-57cf-a687-da8c721bdcd1 | note | Responsibility: FH Engineer/ Asphalt Supervisor
c9a64264-a75d-5875-9608-eb15945e205b | date | Date Completed:
| checkpoint | 2.2 - Prime Coat
b0d77d5a-829c-5342-899c-24b9d517225b | note | Frequency: Prior to commencing paving final layer
20fe6b5a-1df2-59a3-a957-fa834a2b8953 | note | Acceptance Criteria: Prime coat to be applied at 1.0L per square meter
6c0bb2ea-de52-54a1-85aa-d8a235ddd12d | note | • Primer sealing shall be carried out under favourable weather conditions and the prepared base course shall be sufficiently dry to permit adherence to and penetration of the base course by the bitumen.
c4c8e188-c6bb-5817-8e76-e902a67a9c09 | note | • Before primer sealing, the pavement shall be broomed free of all loose material and dust and any defects are to be made good. Should conditions require it, the surface shall be lightly watered immediately prior to the application of the primer.
c2920eec-20ea-555c-9fd0-891c1b91060d | note | • The primed surface shall be covered with 5mm diorite screenings at the rate of 80 square metres coverage to one cubic metre of screenings and rolled with a 6 - 8 tonne roller until screenings are firmly embedded in the primer.
b43a058f-388e-5466-9989-37845b3a007c | note | Reference Documents: EW-CE-DRW-406-001 EW-CE-DRW-416-001 C.9.12
1c0f0fc8-2cb5-5382-9b48-6f7067e64ac1 | note | Inspection / Test Method: Visual Inspection
c61e0906-7a2a-5bee-8d12-70295161a683 | note | Record of conformity: This ITP Signed off
d064df48-b2f0-592f-b183-4a29625ddd03 | note | WP
54e1c321-2653-5681-991b-39feb690bf20 | note | Responsibility: FH Engineer/ Asphalt Supervisor
c8f3e3bd-4b03-5290-b89c-ad302ce30189 | date | Date Completed:
| checkpoint | 2.3 - Commencement of Placing
34672287-245f-54f1-86c6-4ac804512f2c | note | Frequency: Prior to commencing Paving
30766ca9-7e97-530d-9310-2307fdcba81f | note | Acceptance Criteria: The placement of asphalt on the sub-base or granular base for a new pavement or for an overlay of an existing bituminous surfaced pavement shall not commence until the consent to proceed is obtained from the Superintendent
12adbdde-65f2-5e9a-9de6-3bf378313d8f | note | Reference Documents: Work Procedure
c4a70600-c5a3-5bd2-bb5b-cc61d7a64043 | note | Inspection / Test Method: Visual Inspection
43f2ed4e-6e81-542a-a9db-30f01cf26fd9 | note | Record of conformity: Hold Point Release
0cb4c4a6-2e4b-5aa4-85dc-f67f952e9d52 | note | HP*
6745b3d0-86a0-5651-8b33-8adaf13647fd | note | Responsibility: FH Engineer / QAV
3da91206-9630-54df-9096-2b51f69bc520 | date | Date Completed:
| checkpoint | 2.4 - Delivery of Mix
1489c6b8-fb14-51aa-b3a0-3f58afd2a085 | note | Frequency: Each load
7632929e-4d53-5a21-9ad9-d47b3c9060a3 | note | Acceptance Criteria: The asphaltic concrete mix shall be placed at a minimum temperature of 140 degrees Celsius immediately on delivery to the spreader
004e59dc-5e89-5e1e-b3af-3cd72da22201 | note | Reference Documents: C.9.13
452f200e-2b9a-55d2-9d02-2dd437fcf17e | note | Inspection / Test Method: Visual Inspection
ec16706a-723e-5c7f-85a3-82f1cd807022 | note | Record of conformity: Delivery Docket /Asphalt Traceability Sheet
883701c0-16d1-54c0-8a5b-f1c0bb335fc1 | note | IP
0d8626d8-5a76-541d-ab57-c4448665583f | note | Responsibility: FH Foreman / Asphalt Supervisor
9a5d3d94-1a47-5a18-87e1-882a81252348 | date | Date Completed:
| checkpoint | 2.5 - Layer Thickness and Level Control
70e86356-e0d1-55aa-b879-622e5072ac48 | note | Frequency: Regularly during paving
b4e53762-5e5d-5d8a-9659-41b9aadfb89b | note | Acceptance Criteria: Thickness of asphalt layer conforms to asphalt thickness on drawings.
9d8ee522-7a08-5a74-b5b4-f12a9c71093e | note | • The asphaltic concrete shall be placed in one layer by an approved self-propelled machine spreader, conforming to AS 2150, Section 12.
f27f7348-f0e1-51f8-a053-30ff0700e400 | note | Reference Documents: EW-CE-DRW-416-001, EW-CE-DRW-406-001
2aee9b27-e4be-5b48-a29d-f0b1f6e6feb9 | note | Inspection / Test Method: Verify
ce5b668a-7209-50cc-ade9-3128e10f759b | note | Record of conformity: Dips using ruler or dip stick
1b22a8f0-76f2-57d3-8312-6104efec471e | note | IP
7fa0941c-3b8a-5ff0-ade2-8b243d0b9b56 | note | Responsibility: FH Foreman / Asphalt Supervisor
80084584-c20a-519d-9d9a-62530071b46f | date | Date Completed:
| checkpoint | 2.6 - Asphalt Placement works
7873c2c6-d2b3-5417-821b-b12ac2c13ffe | note | Frequency: Each Load
9164be33-05fe-5fef-b50f-4bf7d3f23e08 | note | Acceptance Criteria: The temperature of the asphaltic concrete at the time of initial rolling must not fall below 120 degrees Celsius.
80d5013b-fc12-5a1c-b622-6774243b9eae | note | Reference Documents: C.9.13
8bca35d4-f7ae-5312-b7e0-e1687a4de3ae | note | Inspection / Test Method: Verify
ed23ecb4-8f7a-5eca-b5f6-62b04899cffc | note | Record of conformity: Thermometer
309f79cc-2872-5a3e-a85d-44ff51358da0 | note | TP
dff943ac-2907-51eb-a1ff-6bc4e2a537dd | note | Responsibility: FH Foreman / Asphalt Supervisor
ab8e77a8-a3d8-5dc7-a6ea-1ba65f296613 | date | Date Completed:
| checkpoint | 2.7 - Surface Finish of Wearing Course
040baf92-85c6-56c9-b66e-836be136ae12 | note | Frequency: During paving and after final roll
353ef873-82da-5f90-b1d8-57d25695370b | note | Acceptance Criteria: Joints shall be in accordance with AS 2150 Section 12.6.
69b2da6e-a357-5a4c-95ca-064faa6e6e49 | note | • Form any joints necessary and ensure that the finished profile is smooth and even over the joints without ridges or depressions.
29126ad0-edd5-5cbe-8fe9-0c7f9b4cecf8 | note | • Joints shall be waterproof.
6bbb5a2d-0043-5b7b-b5ff-74963a164b35 | note | • If the asphaltic concrete begins to shove or crack, in no circumstances continue with rolling until the cause has been determined and corrective measures taken. Keep drums and wheels of rollers wet with water and clean during all rolling operations.
4ea0daed-20d9-5042-865a-bcf3b523cc0d | note | Reference Documents: C.9.13
4ce6cecf-7975-5ecf-8449-fcfba045d7c0 | note | Inspection / Test Method: Visual Inspection
57e8cae9-e43e-5e35-ade6-c1da418dc02f | note | Record of conformity: This ITP signed off
5ac04877-9582-522b-aab1-b0e2d12e03ca | note | IP
6616363f-23e2-55aa-8c15-d58c33719487 | note | Responsibility: FH Foreman / Asphalt Supervisor
b2fa31a0-dbdd-57dc-92e7-fa7dca9c2018 | date | Date Completed:
| checkpoint | 2.8 - Kerb and Channel
6b7af1bd-4c87-5034-9fd2-2108a79ae24d | note | Frequency: During paving and after final roll
4681f754-7c29-5d6a-bb85-5bcce4103895 | note | Acceptance Criteria: Where asphalt is placed against kerb and channel, The edge of the wearing course shall be either flush with or not more than 5 mm above the lip of the channel
ba6c7653-bd24-5f81-973a-bedaaa3ba2fa | note | Reference Documents: Work Procedure
99ae73d5-ed7b-5964-9f9b-36738bfb9abf | note | Inspection / Test Method: Visual Inspection
54352bee-d2fb-59fd-8898-7204cac5e3a3 | note | Record of conformity: This ITP signed off
a2d996f2-cefc-55e8-bc27-ed08542ad005 | note | IP
a4dc18e1-638f-575f-b0df-1b4814123ff2 | note | Responsibility: FH Foreman / Asphalt Supervisor
25e8d7ad-02e6-5a8e-b755-66f439949829 | date | Date Completed:
| section | 3 - Testing and Conformance
| checkpoint | 3.1 - Compaction
4ddf6032-ede3-5448-8698-bd2e844fbe43 | note | Frequency: As Requested
958b05af-768b-54a2-8b97-ca4532c773c2 | note | Acceptance Criteria: The density of the compacted concrete shall be not less than 97% of the Marshall maximum density.
54255945-66b6-5da5-84cd-3670ea057bbe | note | Reference Documents: C.9.13
3bcfd0d3-666f-5aee-8114-e6a28cc22f1f | note | Inspection / Test Method: Verify
588331fe-b9e7-567d-bf60-356f92b38e79 | note | Record of conformity: Test Report
4a2cad92-7008-5e93-9d72-4309f0769216 | note | HP
04a618ae-51df-5d66-8099-dee73437f08b | note | Responsibility: FH Engineer/ Lab Technician
f6a566fd-7510-521c-88cc-8e7834f755f0 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - As-constructed survey and conformance documentation
118a200c-e7b2-526c-be89-a8f284375d18 | note | Frequency: Each Lot (1 per day)
d34c2a7e-11ff-5727-ae00-0acaf076131f | note | Acceptance Criteria: Lot Maps shall be completed to show the extent of works for each lot.
fde37f6d-a7da-5500-a9b1-df86166e1001 | note | • Lot Maps shall include layer depth and finished levels at 20m intervals and conformation of ponding checks per lot.
25411efc-ce31-5ec1-a1af-42cf1e9167b4 | note | ○ Tolerances
2a30dea5-70d6-596f-b54b-8a8c460aab98 | note | • Width of prime: + 150mm or - 0mm
a43d59b8-d3f0-5465-af54-fadfefbc8ef5 | note | • Width of primer seal: + 150mm or - 0mm
035b25c4-befd-5ee6-9e50-1aec883a24c3 | note | • Thickness: + 5mm or - 0mm
cd343bec-b79c-541a-9972-3c0ac4e7a6a2 | note | • Finished level: + 10mm or - 10mm
8e2a1303-a4cc-5d36-9314-fa40ee8bed74 | note | Reference Documents: C.7.2 (5.), C.7.4 (Table 6)
fab65828-b10f-5f33-99fe-3bc3165d4735 | note | Inspection / Test Method: Verify
d587e8fd-c864-5f63-a71b-7d5a3bc7ead6 | note | Record of conformity: Visual match existing / This ITP signed off
efd47ec5-5c09-5f46-a591-5df0fa4bb28c | note | SCP
e4d0b90a-33c1-51f2-ad92-843b41e4f901 | note | Responsibility: FH Engineer/ Surveyor
8f5678eb-2d81-5035-82ad-334603d72df1 | date | Date Completed:
| checkpoint | Final Inspection
cd63ed7b-6e61-56eb-8c86-73ce661165e0 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
6356b1fa-9e64-5050-b213-bc7aff4e6531 | textbox | Print Name:
e1e167e8-c176-5689-8a2e-d458c120c9fd | textbox | Position:
1d86e99b-a3d8-547c-ac72-ad044a5c9e23 | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-006 - Concrete - Kerbs | itp | CTN-ITP-006 - Concrete - Kerbs | e85f2eeb-47f5-48bc-a8dd-42bbe1c81c83
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
6bc2627d-b68a-51e5-9331-09568c1fcee1 | note | Frequency: Prior to commencing any activity
e68e70fd-c9f9-5f97-965e-b5c7f7d43539 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
592d64f8-da8a-56cf-93a9-29d276d11722 | note | – using the correct and complete set of drawings
fe1c427f-d980-5cc9-8a9a-3674a36ddcdc | note | – all drawings are the latest revision
dbe797c4-c4a9-5123-b62b-b23b3646ea80 | note | Reference Documents: Drawings and drawing registers
276c8c6e-56b5-5182-8762-705fad5b6df4 | note | Inspection / Test Method: Visual inspection
4cd24f43-70f0-587b-ba43-3afdb6a0515f | note | Record of conformity: ITP Signed
ce1a1e5d-f5d7-5c0d-bf01-0da4a2871b6c | note | HP*
7576be38-e928-57ce-8fc2-94fa0f45c5fe | note | Responsibility: Site Engineer/ Site Foreman
6b901fae-9703-5b92-83ff-b861bd15bbbe | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
f227fe21-cad2-5ea8-862d-3896e811f8a0 | note | Frequency: Prior to commencing any activity
36bb38cc-a950-58a2-b4a9-06b5ebb2c053 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
1d855601-1f3a-571f-95a8-502541529f29 | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
22240516-5b91-5c33-998f-3c9d45ca3626 | note | Inspection / Test Method: Visual Inspection
6f45956d-8c18-5d5f-ae99-2a3cf51ef81d | note | Record of conformity: ITP Signed
91196b51-1d20-5cb0-9cdc-0459d77852dd | note | HP*
fcf145e8-faf3-576c-80e2-75374e776380 | note | Responsibility: Site Engineer/ Site Foreman
5bae8926-4ff7-5ffe-b54b-cc20126b435f | date | Date Completed:
| checkpoint | 1.3 - Submission & Approval of Concrete Mix Design
8048a345-828f-5c3b-b2e2-cf8e8746992c | note | Frequency: Prior to first concrete pour
9f14af47-f1e7-5fde-ab1a-e5d327cfe82b | note | Acceptance Criteria: Supplied concrete pre-mixture for kerbs, needs to be in accordance with the supplied Early Works Civil Drawings.
dff6203a-ed6c-5f2e-9b79-37759e7b5e5f | note | • Unless specified, then concrete used in this construction shall conform to AS 3600 and be provided by an approved pre-mixed concrete supplier, conforming with AS 1379.
1316f3dd-d3a1-539a-82c8-d87cc71f6da2 | note | Reference Documents: Work Procedure
b1a174c9-e3eb-59b5-ae85-a10d9909e87d | note | Inspection / Test Method: Verify
86e5a73e-990d-5788-a769-6745c3d55ba2 | note | Record of conformity: ITP Signed, Mix design approval
7072a401-80e2-5edd-8011-ff68bc644edf | note | HP*
f78745ef-6ff9-544e-ab72-1d9b0e7a705a | note | Responsibility: Site Engineer
ee7c135c-4f37-5a43-aff5-e72183342674 | date | Date Completed:
| section | 2 - Construction Works
| checkpoint | 2.1 - Setting Out
54b8b1ea-b316-5b54-970e-f61c904d86ef | note | Frequency: Prior to start
478072df-c6e4-5cf1-abe9-1186e7de3fc9 | note | Acceptance Criteria: Set out work in accordance with drawings. The Engineer and Supervisor will review and confirm set out with surveyor.
1ed4587b-7f34-54e2-9720-d7d64b56eb95 | note | • No survey/level pegs to be removed by any persons until completion of works.
562de5d2-361d-536f-b1ba-8beb4f7b82c4 | note | Reference Documents: Work Procedure
7af114df-cd16-5dfc-8b3c-80b9fd7abb62 | note | Inspection / Test Method: Verify
d246376e-deba-5a99-a0ba-ecd797fbc190 | note | Record of conformity: This ITP Signed
a63b9227-b5db-528e-b51d-b772d98f6ea9 | note | HP*
72625d76-2192-54ff-9b66-27bd6f0ca9f4 | note | Responsibility: Site Engineer
0052341f-22c0-550a-b80c-925c46387563 | date | Date Completed:
| checkpoint | 2.2 - Excavation Permit
d1d25bd6-19d7-54a6-8f50-b8ce637bbaab | note | Frequency: Each lot
fcd2257b-1600-5727-9cd1-d840bd1c9389 | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing.
0e01218f-4aba-5f5e-b8a0-9b361a202c5b | note | • Plant and equipment shall be appropriate for the task.
69731834-fe31-5c4b-a306-73d1589b779a | note | • Excavation operations shall not disturb areas outside the limit of excavation
4d4bed5f-953a-526e-b80c-05de6848f366 | note | Reference Documents: Excavation permit
6c8ef806-b49e-527d-baf4-69567d6ba908 | note | Inspection / Test Method: Verify
96b129c0-1e40-5167-8d99-bd5be858980d | note | Record of conformity: ITP Signed
2f5c1060-10f7-5093-b413-4720650bbe69 | note | HP*
81eab740-5fab-5cf3-8b96-8a803df50fdf | note | Responsibility: Site Engineer
1b2a0207-1b40-5871-88ad-c80fb59b37c7 | date | Date Completed:
| checkpoint | 2.3 - Excavation
d069f4cd-9c3d-561e-93cc-a09c934d8a61 | note | Frequency: Each Lot
c48ca525-9511-5765-82d5-172ab018d139 | note | Acceptance Criteria: Excavation completed to required depth to allow placement of the bedding layer
8b403a4a-d38c-523b-a424-ba76f6bb58d6 | note | Reference Documents: Work Procedure
02c4ebbe-baca-5a49-881a-b2f9c4193732 | note | Inspection / Test Method: Verify
ad263e66-5dfd-51e8-9dff-27805dd08da2 | note | Record of conformity: ITP Signed
041da8b2-ffde-5dfe-bd49-3c1f26924130 | note | IP
02772cd6-474b-5f17-88e3-ecb6b2d9c9f3 | note | Responsibility: Site Engineer
04d503b3-c9f8-5d37-925a-d9098819c4b0 | date | Date Completed:
| checkpoint | 2.4 - Concrete Placement
c161e847-4e8e-5c5c-b7bc-72645c79a493 | note | Frequency: Each Lot
2ec29804-1b35-5273-8b9f-428e788c5712 | note | Acceptance Criteria: All kerbing shall be constructed from 32 MPa 28 day cylinder test compressive strength concrete manufactured in accordance with AS 3600 for 10mm aggregate. Slump tolernaces to be in accordance with a 50mm slump.
c9696e45-eef9-5b22-bc6e-7eb602a72801 | note | • Kerbs to roads shall be constructed of extruded concrete kerbing. Kerbing to smaller radii than can be placed with the extrusion machine used shall be cast insitu to the same cross section as that of the extruded kerbing, except that the cast insitu kerb shall be 100mm deeper than the extruded kerbing and shall be embedded firmly in the road surface to the extra depth. The outward appearance of the extruded and cast insitu kerbing shall be identical.
20debf66-34f7-575f-9d88-fa65de172f33 | note | • Where required match all new kerbs to existing level neatly, ensuring minimum 1 in 250 grade, saw cutting and reinstating pavement in front of kerb to fall to new kerb level.
9515d6a4-a67a-5aa3-a6c6-a234db0cba52 | note | Reference Documents: DWG EW-CE-DRW-406-001 C.10.15 C.10.16
adc7eed9-9dec-5052-a6d6-a0096ad281e1 | note | Inspection / Test Method: Visual Inspection
64643445-c15c-5081-b76d-c8db93a65688 | note | Record of conformity: ITP Signed
f522e62f-9063-569b-a249-9206fa3ff3e5 | note | IP
acfc8aa2-1242-5534-bdab-fed18dfec392 | note | Responsibility: Site Engineer/ Site Foreman
43b6c8a4-7eaf-5f50-af9a-d1eba100bdcc | date | Date Completed:
| checkpoint | 2.5 - Pram Crossings
6d788f4b-983c-5acd-b011-0188b063ed6d | note | Frequency: Each Lot
d2223f8a-c9b4-5d52-bd57-b05f479f1e3e | note | Acceptance Criteria: Ensure that pram crossings are constructed in accordance with requirements for access and mobility and with dimansions as specified on DWG-416-001.
22fec6a5-031a-5093-943e-21c0d36114c2 | note | • For pram crossings within concrete kerb refer to Figure 24A of AS 1428.1
0b579ea3-90fc-5d98-9f03-3022f8741565 | note | • Kerb ramp allignment in accordance with Clause 7.7.1 of AS1428.1
b0ccec83-ab12-5662-9101-b01e2550a757 | note | Reference Documents: Figure 24A AS1428.1 DWG-416-001 Clause 7.7.1 of AS1428.1
707db4a4-504e-5653-8fb8-e99e99f4c48e | note | Inspection / Test Method: Verify
ad5bc0b6-23d0-5c77-99f2-c850cbd57974 | note | Record of conformity: This ITP Signed
2eb700f6-ec50-561e-9535-9ee7caee6c82 | note | IP
fee18d8e-8c0f-5d37-a2aa-aecf55b45ae9 | note | Responsibility: Site Engineer/ Site Foreman
b35628aa-41e6-5eec-8f50-9758bc4ba9f9 | date | Date Completed:
| checkpoint | 2.6 - Joints
1216963f-f896-5d2b-8a27-40d003f5d067 | note | Frequency: Each Joint
aed659aa-5e84-50a2-befc-3389bd70e48e | note | Acceptance Criteria: Contraction joints shall be constructed at 2.0m intervals, at sides of entry pits and at tangent point of sweeps by complete separation of adjoining sections of the kerb immediately after extrusion.
d8740c1a-6c93-5591-af53-6627a5dac51d | note | • Joints shall be 3mm wide, clean cut and made vertically through the concrete at right-angles to the direction of the work.
f9a01c19-c8b6-5b57-a1de-084372f9dac2 | note | • Where kerbing is laid by machine, joints shall be formed in a manner which doe s not cause damage to the adjoining concrete during cutting and to a depth which will prevent cracking elsewhere. In general it can be expected that the cut should extend to at least one-quarter of the depth of the section.
92c67de2-a9c4-55ce-9b0f-812c25d2e18a | note | • Where kerbing is cast against fixed forms, contraction joints shall be formed by means of a 3mm thick steel plate cut to profile which shall be withdrawn before final finishing.
54178e08-f2ac-5ace-a5f0-0ea0a8b84fb1 | note | • Expansion Joints shall be constructed at every third contraction joint not less than 24 hours after placing. The expansion joints shall be formed by the sawing of a 10mm gap that completely severs the adjoining sections of the kerb. The gap shall be filled with approved joint filler after the Superintendant and the Local Authority have inspected and approved the cut joints.
960b2ced-4137-5c6b-9f58-ccc87622205b | note | • All existing pavement adjacent to proposed kerb or proposed joints shall be saw cut in a neat line to the satisfaction of the supervising engineer, and to have 300mm overlap.
c6e5f499-8174-55e3-ad20-c5b513d1cc45 | note | Reference Documents: EW-CE-DRW-007-001 C.10.17 C.10.18, EW-CE-DRW-406-001
1723d25e-ae08-5202-93e3-c7550f58d6fd | note | Inspection / Test Method: Visual Inspection
d4268ad1-7913-50dd-ac91-3af33952246e | note | Record of conformity: This ITP Signed
361ed21d-8842-5dbe-ac03-185e08ffd6e1 | note | IP
38e2594f-c555-59c9-a174-bd674186d3d6 | note | Responsibility: Site Engineer/ Site Foreman/Superintendant
57be2c84-46b6-5cb0-a069-3edd7300a89c | date | Date Completed:
| checkpoint | 2.7 - Protection of concrete
f5e0cae5-404b-5dcf-8587-7d9ffcdf1983 | note | Frequency: Each Lot
74846088-a6e6-53ad-b5ec-050aac32be9a | note | Acceptance Criteria: Kerbs shall be always protected from bitumen overspray by adequately covering the kerbs with polythene sheeting or similar approved material
762b2047-2082-5de4-8c5f-e9496a1a96ee | note | Reference Documents: C.10.20
8008ee3e-5f3c-569c-bcc3-f295ab765ffd | note | Inspection / Test Method: Verify
3600a1a9-b118-5ea0-877e-c0f8e6501fa3 | note | Record of conformity: This ITP Signed
6e31b5c7-ed5a-5f28-b16a-925633adb330 | note | IP
96dcff23-9b1b-5bcc-8510-7c3c8d8f5fdc | note | Responsibility: Site Foreman
6d4048b4-b789-515f-a146-59cdccd2149c | date | Date Completed:
| checkpoint | 2.8 - Curing - Kerb
781a0d91-6f89-5db4-9d1f-783ddba080c7 | note | Frequency: Each Lot
c7418c08-3d64-55e5-81e4-80501ae55dab | note | Acceptance Criteria: Within two hours of surface finishing, all exposed faces of the completed kerb shall be protected against loss of moisture for a period of not less than 96 hours after placing by shrouding with plastic sheeting or by spraying with a curing compound complying with AS 3799.
6fe9bc8c-7ec3-59c8-9299-a2fc5ab144f4 | note | Reference Documents: C.10.19
23afed14-a4eb-5426-9eaf-36e64b5e28dc | note | Inspection / Test Method: Verify
5934998e-d492-5d73-93fd-7a4b1dd53927 | note | Record of conformity: This ITP Signed
ea512a6c-b76a-54ec-97a0-70402ec1fefb | note | HP
1dbb753d-46eb-56a4-9b67-f9497620bac9 | note | Responsibility: Site Engineer/ Site Foreman
e943788e-142a-51d0-980a-5a1286dc7583 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 3 - Completion
| checkpoint | 3.1 - Carry out sampling of concrete - strength and consistency
89d55ccf-abb2-5040-8426-aff8c7f453bd | note | Frequency: Each 50m3
07c2ccc8-fc89-5609-8e13-26d1556f74ee | note | Acceptance Criteria: Sampling and testing of the strength of concrete shall be carried out in accordance with Clause 6.2 of AS 1379.
a4650249-ec8e-5e37-8ff8-d04116608d15 | note | Reference Documents: Work Procedure
a4fb7309-7518-5c5e-a306-f58a9976da82 | note | Inspection / Test Method: Checklist
d044aac1-cd60-5f39-bfb5-b2136c00947d | note | Record of conformity: ITP Signed/Test Records
52f89a72-15d7-5f5a-864b-e297c6eb1ed8 | note | TP
89aca801-4b49-5ffa-90ee-efd67be0ea53 | note | Responsibility: Site Engineer
1726d9e8-991c-5a12-824f-8ee25e370b35 | date | Date Completed:
| checkpoint | 3.2 - Tolerances
4d15bbb3-0892-5b71-8fef-24045c2dfb8e | note | Frequency: Each Lot
469d35bd-0af8-529f-b304-7f3ecbe742f1 | note | Acceptance Criteria: Tolerances
7fe01eb8-b8bf-5870-bea1-199d620d4794 | note | • Surface: + or - 5mm when tested with a 3m straight edge
92ee1ac6-1ed0-50d7-b614-2ea02ede4b40 | note | • Level: + or - 5mm
e0167938-5614-524a-ab01-ed3fcfeee838 | note | • Line: + or - 10mm
e275fc16-cdb5-5721-9a63-339a5942a47a | note | Reference Documents: C.7.4 Table 6 (9.)
f9128b71-fe7f-590c-802b-db35eb74fd54 | note | Inspection / Test Method: Visual Inspection
55d6eadb-12e7-5cfd-a323-8e72230e9322 | note | Record of conformity: This ITP Signed
37ff4087-53a6-5f04-82a9-76cec7cc80fc | note | IP
16d01c81-9890-5953-9b96-8516a1d6133b | note | Responsibility: Site Engineer/ Site Foreman
84faaa19-d3c1-5b0b-a84a-540098335703 | date | Date Completed:
| checkpoint | 3.3 - Backfilling
a6d9ecdf-8e30-547b-9845-85940b5bdd0a | note | Frequency: Each Lot
3e138461-7640-534a-bb54-70e8f45ea866 | note | Acceptance Criteria: The backfilling to kerbing shall be placed as shown on the drawings after the curing and acceptance of the kerbing. The backfill material to be a similar material to the locally occurring topsoil, free from debris and compacted adequately to accommodate the driving of rubber tyred domestic vehicles.
b008edc1-4db9-53b5-990e-2e0f912dec93 | note | • After curing, no earlier than 3 days, backfilling shall be completed as per the below:
e580f41a-953d-53e8-80e0-f80ebadf0fda | note | – Topsoil compacted in layers < 150mm
dfabbe1f-5acf-5c44-abf4-7393ef47b35a | note | – Width ≥ 300mm behind edging to top of edging
2ae84d6a-e57e-54e9-83a6-a7b833f97b58 | note | Reference Documents: C.10.21 Work Procedure
a2755bf7-a454-5a83-bafb-41421537cc65 | note | Inspection / Test Method: Verify
c0df8566-a597-5804-9537-691580eaff53 | note | Record of conformity: This ITP Signed
ba55f374-1b41-55b6-af5c-5bdc5fe51214 | note | IP
93b53a16-46a9-5205-a0d3-22a951471ed0 | note | Responsibility: Site Foreman
8ca3a5ae-46a7-565c-b4fe-ed4bafc4daf0 | date | Date Completed:
| checkpoint | 3.4 - As-constructed survey and conformance documentation
f6c33b34-7b46-5986-9d21-ebc64597a63f | note | Frequency: Each Lot (1 per day)
48eb2d8c-4a91-531f-9753-e240f5dc98a8 | note | Acceptance Criteria: Lot Maps shall be completed to show the extent of works for each lot.
597efca3-8985-5951-ad5c-70f9518a198e | note | • Lot Maps shall include Width between kerb at 20m intervals, contraction joints, expansion joints and Curing Certification per lot
19ccbdec-680b-5b59-bbcb-5aad5db26824 | note | Reference Documents: C.7.2 (7.)
85d93da7-5a9c-5555-b80b-ad199ee5e33a | note | Inspection / Test Method: Verify
4a920fbf-590e-50be-b359-e38ec9858886 | note | Record of conformity: Visual match existing / This ITP signed off
f17aad63-d817-54a4-b618-88c3a5ea2a35 | note | SCP
fba831f9-9187-5140-9f62-b006c5835a98 | note | Responsibility: FH Engineer/ Surveyor
479b487a-9990-54d0-ad02-7f501a5179a8 | date | Date Completed:
| checkpoint | Final Inspection
85a997b9-9b77-5a36-9a94-2597a01ecbd5 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
b0997bee-2b1f-5af0-9585-c1f73f2f43e5 | textbox | Print Name:
2e3d7c0a-9a95-5695-876e-6c85c74c3792 | textbox | Position:
a580c0b3-6171-565f-bfcd-ca590c23c585 | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-007 - Concrete - Footpaths & Islands | itp | CTN-ITP-007 - Concrete - Footpaths & Islands | ca39093c-3d83-462d-b913-15092ddde6e5
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
cbf56c66-69f8-53a6-b3ac-6cf5bb84bf1e | note | Frequency: Prior to commencing any activity
d7f2356d-b1bc-5d32-8c56-e39d5ec15a1c | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
605159ba-9af6-5fa1-965c-663efd9d1104 | note | – using the correct and complete set of drawings
87885be0-85d6-5adb-8e12-646a42452e12 | note | – all drawings are the latest revision
6674f5fb-050b-504b-a132-17f702e63926 | note | Reference Documents: Drawings and drawing registers
a2f7e8e7-d708-52f2-9d10-25671128fc14 | note | Inspection / Test Method: Visual inspection
64772304-fc46-5fe3-b7fc-2d5ca1b71975 | note | Record of conformity: ITP Signed
5b38a067-8b42-59a2-a99d-9fc476725eab | note | HP*
4de99b6f-41d8-5811-b784-c660f41ecbd6 | note | Responsibility: Site Engineer/ Site Foreman
571cc039-c01d-59da-be2c-f09cd342119b | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
9e4d7c0b-d7b0-5019-999a-3a99852e3e07 | note | Frequency: Prior to commencing any activity
f2c3d6e2-5653-58e6-b2b5-b13951ac7f50 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
d3dccbc5-e636-5cf6-b818-f6b55fc56415 | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
5bcf9ffa-e7d7-53c5-92be-46c84ff3f511 | note | Inspection / Test Method: Visual Inspection
988dd7b0-e766-5fa6-ab11-6360e427c1b4 | note | Record of conformity: ITP Signed
c8323074-83cc-5ffa-9a24-80f692c3f288 | note | HP*
5f8ace94-de04-54dd-9d57-8ab7ef68d2d7 | note | Responsibility: Site Engineer/ Site Foreman
88e9102f-85cb-5697-b901-e3370bea6d8b | date | Date Completed:
| checkpoint | 1.3 - Concrete Mix Design
b353f0a7-95e0-5d23-aaf5-233395b08da8 | note | Frequency: Prior to first concrete pour
492dc1a1-1817-5d27-8c6f-705945ca7a19 | note | Acceptance Criteria: Supplied concrete pre-mixture for footpaths, needs to be in accordance with the supplied Early Works Civil Drawings.
ca529f55-6c75-5302-87f1-7a6c5108c5f7 | note | • Unless specified, then concrete used in this construction shall conform to AS 3600 and be provided by an approved pre-mixed concrete supplier, conforming with AS 1379.
b47521a8-21d9-5845-9538-d48f3bbdb368 | note | Reference Documents: C.11.2 Work Procedure
6b081fa8-5389-52fa-a99e-fdd9c19178b6 | note | Inspection / Test Method: Verify
1e007936-0ed0-5143-978b-4e9048d5100f | note | Record of conformity: ITP Signed, Mix design approval
6f3218d9-7824-5201-9f1a-d5283fdab8f9 | note | HP*
e0beebe8-b3a5-5aee-afd4-05dcf2083d64 | note | Responsibility: Site Engineer/ Superintendent
f4529bec-267c-5064-a22e-a81d4a5a56b4 | date | Date Completed:
| section | 2 - Construction Works
| checkpoint | 2.1 - Setting Out
093475c1-86b0-51dd-b75b-16ec55d79d98 | note | Frequency: Prior to start
8874302d-535b-5090-8541-016b4ac5b67c | note | Acceptance Criteria: Set out work in accordance with drawings.
2a1b5ac1-e3ea-5c77-85c8-7d4d5815e746 | note | • The Engineer and Supervisor will review and confirm set out with the surveyor.
5b289606-8c18-5172-aab5-e94a75446068 | note | • No survey/level pegs to be removed by any persons until completion of works.
7f3dfcf7-2df8-53ea-b654-b719ade5598b | note | Reference Documents: Work Procedure
8d9d349b-df72-5d94-83c9-b6ef2ef63067 | note | Inspection / Test Method: Verify
e4dad96d-aee5-518e-b657-65e8188c648e | note | Record of conformity: This ITP Signed
c14aa65a-dee3-5359-bef6-4f812365b836 | note | HP*
e6919ece-ed60-507f-9b54-6b5117be48eb | note | Responsibility: Site Engineer/ Superintendent
66533def-ccb8-578e-b435-22268ce16ee3 | date | Date Completed:
| checkpoint | 2.2 - Excavation Permit
e4bb1142-0f2c-556b-8822-7e1fbe4e1b23 | note | Frequency: Each lot
2d2acf94-9bed-57a7-b5fd-3cff3ac7461f | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing.
fab75ccc-4e3d-55ed-935c-0e21d093ef66 | note | • Plant and equipment shall be appropriate for the task.
b161363e-8540-5f24-9d99-ab05c5822611 | note | • Excavation operations shall not disturb areas outside the limit of excavation
36553019-bc78-5bdb-af21-9377f59d4168 | note | Reference Documents: Excavation permit
ee923af1-091b-5289-aa78-cebbf18848c4 | note | Inspection / Test Method: Verify
0726336f-f2be-5d18-9913-4d5e77ca524f | note | Record of conformity: ITP Signed
ef31f98c-c440-576d-87ba-ea9ea87cda69 | note | HP*
5962ed19-991a-5423-a41b-a7a402ec614a | note | Responsibility: Site Engineer
3c2c0021-6b2e-5889-8a47-29a7e19b5fae | date | Date Completed:
| checkpoint | 2.3 - Excavation
683c0e84-36cc-5dae-8ede-76cd87bdb4d2 | note | Frequency: Each Lot
27faf44c-bbaa-57fd-9862-79e6f12c0721 | note | Acceptance Criteria: Excavation completed to required depth to allow placement of the bedding layer
db2dd32e-be7e-5165-9ac3-040286201b4b | note | Reference Documents: Work Procedure
c333110b-d6ca-5013-bba7-f74bfb380125 | note | Inspection / Test Method: Verify
02aaa8ff-c7fc-5ff9-8518-11e7469d9e4b | note | Record of conformity: ITP Signed
c65635ad-03ae-5e3a-8726-1c0548b4e84b | note | IP
e3457cdc-fa09-59da-b85a-dfefee17783b | note | Responsibility: Site Engineer
a842d2ea-96da-52ae-b233-a8c333c6d37c | date | Date Completed:
| checkpoint | 2.4 - Formwork
85b6f0c7-14a9-59d2-b9b2-1f1dea409f34 | note | Frequency: Each Lot
0b7b7b7b-40cb-5559-a956-df4d44e07184 | note | Acceptance Criteria: Formwork shall comply with the requirements of AS 3610
45491b1e-0524-56bd-8800-1293b9f7ed4c | note | Reference Documents: Work Procedure
148c49ef-37ea-57a4-8a77-d238b3b38f3e | note | Inspection / Test Method: Verify
b591da3f-f5a9-56eb-87d6-53a580ec1398 | note | Record of conformity: ITP Signed
b44446b6-383f-5240-aa26-1e96373f1934 | note | IP
f7fe8929-08e6-5964-bf90-ce10032d53af | note | Responsibility: Site Engineer
062dc9fd-c6bf-52ea-823e-af9694116aee | date | Date Completed:
| checkpoint | 2.5 - Reinforcement
dca09716-2dbf-580d-b897-5101716e5dae | note | Frequency: Each Lot
e8155fc8-babb-5d55-b2f9-ab24bb797632 | note | Acceptance Criteria: Reinforcement must comply with the requirements of AS/NZS 4671.
317a0b71-39a8-5c17-b6ea-d3652f00fef3 | note | • Concrete Infill pavement reinforcement to be SL82 mesh central.
dbccc8be-2797-5596-b8f9-e0c612669da8 | note | • Concrete Footpath Pavement reinforcement to be SL72 central reinforcement.If required to be stopped or cut either side of expansion joint (EJ)
b0a1f507-1c16-5dfc-b3ef-9b692ef97ffc | note | Reference Documents: DWG EW-CE-DRW-406-001, Work Procedure
392a3afd-2094-5769-b5b9-276462381e0c | note | Inspection / Test Method: Verify
bca98dfa-7bb6-5b41-8764-8a478504b254 | note | Record of conformity: ITP Signed
03b81ac0-e0c5-5131-9018-88561edc567e | note | IP
774c49d0-81fd-529b-842b-96dd007f60c4 | note | Responsibility: Site Engineer
70a23c65-6a24-59cb-ad2a-76df515a8804 | date | Date Completed:
| checkpoint | 2.6 - Concrete Placement
c5caf274-421c-529d-a558-924b23521690 | note | Frequency: Each Lot
ce3d417f-969f-5504-8cbd-957d8d2fe349 | note | Acceptance Criteria: The concrete, when placed, must be well tamped to remove all voids and to work fines to the surface for trowelling.
67b9c837-03c7-5cb1-9799-69d0f0481433 | note | • Concrete Infill pavement to be 150mm depth N25 concrete
9d3b7869-db60-5c73-8b02-8c68243f948e | note | • Concrete Footpath Pavement to be 100mm depth N25 concrete
28c9de28-7983-5d4f-879b-8da617d46c72 | note | • Concrete shall be of 25 MPa 28-day cylinder test compressive strength.
b4c7b3fc-5546-5192-8216-371769261b2a | note | • The maximum aggregate size shall be 20mm.
4ff95096-9ed9-5f5c-a218-067ae01e36ce | note | • The slump shall not exceed 65mm or be less than 25mm
690ab3c4-8009-5a88-8b94-0b2dafd2f6aa | note | Reference Documents: DWG EW-CE-DRW-406-001 C.11.2
f8e8b4d6-6df9-5b00-80a8-7c5455985f66 | note | Inspection / Test Method: Visual Inspection
89ec8d6b-5a68-5db1-a0de-f7172299afbd | note | Record of conformity: ITP Signed
c2ed0857-a2a1-509f-82f6-ad338b56351c | note | IP
b6c44129-66e8-5403-906b-6a6edcb8d332 | note | Responsibility: Site Engineer/ Site Foreman
1afa34c3-339d-560b-a8eb-1116e10eaab1 | date | Date Completed:
| checkpoint | 2.7 - Surface Finish
7aea4d90-78a1-5a12-ab56-e00ece3b228c | note | Frequency: Each Lot
e32c9a09-9b4d-5273-8d07-572f7855a8b7 | note | Acceptance Criteria: A brushed finish shall be provided to the surface of the slab with joints and edges polished smooth for 80mm width with jointing and edging tools.
0fb397be-28d6-5f38-b6c8-54b2b94ece93 | note | • The alignment of the edge of the path is to be straight and true to line.
2c7e1dce-4a19-587b-a7e2-a0d4de5b4146 | note | • Deviations from alignment or from specified width will not be accepted.
da098fdc-5f9b-5294-b8bc-9d5c6f71f91c | note | Reference Documents: C.11.5
56b865c3-627b-5a75-9eff-030fb15bb880 | note | Inspection / Test Method: Visual Inspection
c645414e-40a0-58c1-9302-eed1efb8f99d | note | Record of conformity: This ITP Signed
9187368c-aa47-579d-951e-b2199110438e | note | IP
2299c288-061e-54b5-a0ae-90da6bee08d7 | note | Responsibility: Fulton Hogan Engineer
823157be-5822-5e68-acfc-c853db04a052 | date | Date Completed:
| checkpoint | 2.8 - Joints
37b8a10c-55cd-550c-818d-4099316b9806 | note | Frequency: Each Joint
f37e0e3b-514d-52f3-b6bd-bd462ef88d75 | note | Acceptance Criteria: Expansion Joint
2c1d2e5c-501d-5f4b-98fd-41b52e617e75 | note | • A 19mm expansion joint shall be provided whenever rigid pavements abut fixed structures or at max. 15m centres to footpaths.
315904f9-97a6-54ac-8b0b-4d1f624a01a4 | note | • An approved joint sealer shall be inserted in the joint and finished flush with the surface of the path.
c24b3eb3-c877-591f-84c7-2d2ad2609c06 | note | • Contraction Joints in footpaths and cycleways shall be constructed at 2.0 metre centres for footpaths.
a71ec0be-dc08-5da2-a0ba-108879d8b30b | note | • Concrete Infill Pavements to have Sawcut/tool joint at every 1200mm (DWG 406)
aad7358b-5c4c-557f-bdae-27437cdaac58 | note | Reference Documents: EW-CE-DRW-007-001 C.11.3 C.11.4 EW-CE-DRW-406-001
02e10576-df21-59fb-9fa4-907ea1f3c9ea | note | Inspection / Test Method: Visual Inspection
1db73c21-6a7e-5031-889c-9361b5fd9a5e | note | Record of conformity: This ITP Signed
b6648129-ea73-59b4-b3ae-c6ba0621c3be | note | IP
3aa1cd31-bb42-5b3d-886c-804eea7f8794 | note | Responsibility: Site Engineer/ Site Foreman
a57edeb5-9ca9-5d79-a498-19615bb7e733 | date | Date Completed:
| checkpoint | 2.9 - Protection of concrete
03694459-ee8e-5409-8d15-0921cd9626c8 | note | Frequency: Each Lot
329f8b89-9bc5-5ecb-adc4-cdf72b59e7aa | note | Acceptance Criteria: The finished path shall be protected from damage by passers-by and with polythene film for 24 hours after completion if rainfall during this period is apparent.
168634f0-0b4e-5739-9fe3-998f4dd8428c | note | • Barricade, warning signs and lights shall be erected to prevent damage of the footpath from vehicles and pedestrians for not less than 24 hours after completion.
44267cf0-a3cd-563c-a4ec-8e36a981a51f | note | Reference Documents: C.11.5 C.11.7
91418a13-f5b1-5c63-aa49-56b2d2115456 | note | Inspection / Test Method: Verify
f8688878-92fb-5a44-8348-2ec2e827d08b | note | Record of conformity: This ITP Signed
5e15c259-861e-5f06-83c6-63f040f444bc | note | IP
90ad2dfd-f5d5-566a-807a-dca44f2eb6cc | note | Responsibility: Site Foreman
41f4c445-0625-505f-b5dc-fbae9be0cc44 | date | Date Completed:
| checkpoint | 2.10 - Curing - Pedestrian Footpaths
509699da-a5b3-59fc-855c-9aad8561080d | note | Frequency: Each Lot
0eadbc34-cb9a-571c-9736-98c541d5c214 | note | Acceptance Criteria: The entire footpath shall be protected against loss of moisture for a period of not less than 72 hours after placing by shrouding with polythene sheeting or by spraying with a curing compound complying with AS 3799.
26e63a23-3253-5350-bdb2-92b81b0cdf66 | note | Reference Documents: C.11.6
844d02e0-1825-527a-8d12-76cba04ebd68 | note | Inspection / Test Method: Verify
f42bd934-1bac-5a21-943a-6ec05fe739de | note | Record of conformity: This ITP Signed
f0f3ebed-5953-5eab-a4ae-5e0a2c23b6be | note | HP
592ac158-ad86-5f90-8721-31607197b967 | note | Responsibility: Site Engineer/ Site Foreman
eeb91fbf-8d60-5c6c-816b-53b1fb63dccf | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 3 - Completion
| checkpoint | 3.1 - Carry out sampling of concrete - strength and consistency
bfdb1e83-d344-5831-95c6-8f66b52764c5 | note | Frequency: Each 50m3
54817a57-a439-54a6-ac82-28f3f972c4e6 | note | Acceptance Criteria: Sampling and testing of the strength of concrete shall be carried out in accordance with Clause 6.2 of AS 1379.
4b97bc5b-6bf0-5727-afde-7ec142083864 | note | Reference Documents: Work Procedure
9c38001a-bab1-55ef-a85f-bd8dda2ea688 | note | Inspection / Test Method: Checklist
0b843da9-4761-5568-80cf-8bda57d63ac3 | note | Record of conformity: ITP Signed/Test Records
0bce7b53-001b-5971-a220-1c5379534c6f | note | TP
8dd2e373-d340-5af8-8184-c6ec481fe30d | note | Responsibility: Site Engineer
796400ab-0400-5f8c-9b11-f14894fbf647 | date | Date Completed:
| checkpoint | 3.2 - Backfilling
cebde716-1232-5d79-ba1d-6548375e5569 | note | Frequency: Each Lot
b9878b8c-3fff-59d7-a4b8-a03ddf8a36c8 | note | Acceptance Criteria: Contractor is reasonable to ensure the site is made safe and clean, this includes All cement droppings, slurry, etc. and surplus materials to be removed from site, cleaning of surrounding strcutres from conrere splats.
fdd2b651-98bc-5d0c-8190-faddbc8c9f26 | note | All formwork, pegs, stakes, etc. shall be removed after the curing of the path has been completed.
9b693dc5-68d4-564d-8f31-f04409fd6ffc | note | Reference Documents: C.11.8
ac9e8543-5fa1-542e-9a8e-ccb2f1c7c99f | note | Inspection / Test Method: Verify
5375f0b1-addb-5bd6-be49-2d0fbcc6e05a | note | Record of conformity: This ITP Signed
ab5e83b9-eed2-5927-9e28-f47e0cf6a5cb | note | IP
5f4cdb24-33e7-562a-ab87-4e13974700b8 | note | Responsibility: Site Foreman
0fa59125-dcf9-5713-9a78-1204b3100c44 | date | Date Completed:
| checkpoint | 3.3 - As-constructed survey and conformance documentation
8706a8f4-8585-5496-8513-e7a0af7e3747 | note | Frequency: Each Lot (1 per day)
a4a614e9-c267-5545-ad4f-0f93307e2aa7 | note | Acceptance Criteria: Lot Maps shall be completed to show the extent of works for each lot.
7cafc3ce-554f-5bf7-afc1-8de6d70841fc | note | Reference Documents: Work Procedure
2ac564aa-abd5-59ff-b89e-dd312d7304e6 | note | Inspection / Test Method: Verify
852e0a4b-7539-5837-992e-3bb645cbe769 | note | Record of conformity: Visual match existing / This ITP signed off
6752a650-068c-5516-bdcf-41bd86a8f42d | note | SCP
e0dbc542-c697-57b6-80d1-dfb2f4446ed5 | note | Responsibility: FH Engineer/ Surveyor
37299b6c-c0e0-5513-a0c7-59a862cb0cdf | date | Date Completed:
| checkpoint | Final Inspection
6073026a-d034-59f7-ba00-0b4340908cab | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
c8d40cce-4c4f-5f63-b2de-17869b0790b2 | textbox | Print Name:
a6bb869c-29ab-5f30-a0f0-7d869cf03550 | textbox | Position:
11d737bc-3af2-5a81-aa0f-11bb64ce8005 | date | Date:
| signoff | Sign ITP
| checklist | CTN-ITP-008 - Cast In-Situ Pits | itp | CTN-ITP-008 - Cast In-Situ Pits | 3d261362-b4fe-4108-af61-9a75f491599e
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check that current revision drawings are being used
0365b6a6-c037-57a2-be99-9c91bdfd519d | note | Frequency: Prior to Commencing Work
e89b58a7-2fa2-567d-a948-1b26a2bb4b9e | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
659bd08f-bf4b-5cb8-abcc-e957a8ab1fd4 | note | Reference Documents: IFC Project Drawings/ Drawing Register
564e2dec-07c8-5e06-a8d5-37f8d2a3595b | note | Inspection / Test Method: Document review
edd0e0d8-3e9a-579a-88eb-459772ff14fd | note | Record of conformity: Latest revision IFC drawings, ITP signed
3af84e3d-1142-51fd-957e-3a9b2628cbd9 | note | HP*
e483059b-35f6-5fdd-be37-e33fd920ed28 | note | Responsibility: Site Engineer
3d9cea91-ff3f-54d5-b2ec-406a8133c962 | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
34b600b6-c18a-5c25-9430-effbf71ef5b3 | note | Frequency: Prior to commencing any activity
445a49cc-28c5-548b-82cb-5278af8a7129 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
de0db7b2-5c0e-5402-9181-3108cb508237 | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
258a4831-adea-5763-93ea-2490c4901754 | note | Inspection / Test Method: Visual Inspection
76b52c25-cb6d-5570-8ba2-fafa120dee18 | note | Record of conformity: This ITP Signed
6fe92749-aa58-5985-8bbd-83f26c02a16b | note | HP*
9d5a8f96-7499-592e-bee6-819b15f1fff5 | note | Responsibility: Site Engineer
ae1a3bc9-47d5-5452-a218-a801090ae931 | date | Date Completed:
| section | 2 - Material Conformance
| checkpoint | 2.1 - Materials & source Approval - In-Situ Pits
78bc5660-0fdc-5809-836d-0bc5f0dada14 | note | Frequency: Prior to works commencing, 1 per delivery
8d657643-4c8b-5ed1-a6e5-eb67a8d788aa | note | Acceptance Criteria: In-situ Pit resources including bedding, reinforcing steel and formwork shall be as specified or as shown on the Drawings.
b2c5536c-b5a4-5d50-9fcc-a9bc9e80504e | note | Reference Documents: Work Procedure
e69b60fe-4d44-5c7e-b6b9-49aac3bc90df | note | Inspection / Test Method: Visual Inspection
d9cb0130-6391-5e80-a5fb-2a9b207edce2 | note | Record of conformity: Receival inspection checklist
60ec4265-af74-53f5-8191-17a47380d214 | note | IP
391ffe20-348d-511d-a7c3-4c89cae513ec | note | Responsibility: Site Engineer
18312801-92a2-5882-ba09-43c1a4c197fa | date | Date Completed:
| checkpoint | 2.2 - Materials & source Approval - Pit Covers
e305522b-c8a3-5927-ae7c-75369a39a1e0 | note | Frequency: Prior to works commencing, 1 per delivery
6a0f3106-68a3-53c5-81d4-787904036d92 | note | Acceptance Criteria: Pit covers shall be either cast iron, precast concrete covers or gratings as per drawings and shall be constructed and fixed to pits in accordance with relevant Tasmanian Standard Drawings
c5ead115-c7b3-5e87-a6c2-8aabdee0ff39 | note | Reference Documents: EW-CE-DRW-526-001 - Pit Schedule C.5.16
289e1789-c3c2-57f0-a6ca-6f23f60391b4 | note | Inspection / Test Method: Visual Inspection
2c2dce49-982a-54a4-a12c-ba71854786fa | note | Record of conformity: Receival inspection checklist
eaab9bf1-ae95-5e15-a67b-47da04235614 | note | IP
3fac8975-5487-5b4e-968f-73d69fc196bd | note | Responsibility: Site Engineer
515034ed-99d1-59d8-ab1f-c68a93f9bd89 | date | Date Completed:
| checkpoint | 2.3 - Materials & source Approval - Step Irons
65e96e82-0d24-5196-a92e-e16059a6c6f5 | note | Frequency: Prior to works commencing, 1 per delivery
3a62b53a-a48e-5136-bd26-7436e032b9b9 | note | Acceptance Criteria: For pit depths greater than 1200mm, provide 24mm galvanized hot dipped step irons or approved equivalent at 300mm centres measured from top of cover to invert level of the base as detailed on the drawings and in accordance with AS 1657-1992.
d5a967d2-7518-54e8-9275-a01dbb2c9cd5 | note | Reference Documents: EW-CE-DRW-526-001 C.5.17
fc69f96f-2253-5881-9183-1330edc5a7ed | note | Inspection / Test Method: Visual Inspection
c7075238-6ab8-598e-a25f-ffb4e674e301 | note | Record of conformity: Receival inspection checklist
a0ed7d01-4073-581d-a236-af5843744206 | note | IP
59c9ae3d-d853-54b8-be15-7c916649bc73 | note | Responsibility: Site Engineer
3c827b71-5c8e-5125-a31a-5714a6bcdca9 | date | Date Completed:
| checkpoint | 2.4 - Source In-situ Pit Material
4883883a-9faa-5b7f-84fc-e63292ae10a0 | note | Frequency: Each Lot
075b6b48-4865-5d90-95fe-d1d01a436e3b | note | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation.
3fb56b68-d59e-5bcc-aa1d-fd9257a9cbb1 | note | Reference Documents: C.5.15
83891436-6977-5602-aad7-758dd6536e82 | note | Inspection / Test Method: Verify
daaabeee-44e3-5f4d-b2f1-0bddf93f5134 | note | Record of conformity: Mix Design
38b9df4a-1575-5f01-ad5e-d75bb4e80740 | note | IP
b5077ca5-2cc2-5f0b-afc8-8eeda1c21504 | note | Responsibility: Site Engineer
7d74da3a-b778-599e-83b2-74949656aa59 | date | Date Completed:
| section | 3 - Construction \ Erection of Formwork
| checkpoint | 3.1 - Pouring Concrete
f7e59120-61dc-57a1-b5b6-bdad6c7dc312 | note | Frequency: Each Lot
1a14eec7-047e-5ef6-a41c-8f1c089d899a | note | Acceptance Criteria: Excavation depth shall be as per specified or as shown on Drawings to accommodate structure including blinding layer / bedding.
e06266d2-c00a-5beb-93f6-ad5bfb50e1f3 | note | • Excavations for pits shall be trimmed neatly to size so as to give the exact thickness of walls as required.
a5ea8aaa-fec0-5557-9d75-10285e191ed6 | note | Reference Documents: EW-CE-DRW-526-001 - Pit Schedule C.5.15
5a25f090-ad2f-5a0b-b45a-848d5c4a767a | note | Inspection / Test Method: Verify
c2462ab3-5b10-5e29-bb99-eeda63e53b13 | note | Record of conformity: This ITP signed
a6bb2625-c262-50d3-a4a8-993993250d63 | note | IP
e0451ab0-38e0-51d0-8ab9-6ab48c4378ad | note | Responsibility: Site Engineer
d61e690f-c5a4-50f0-a236-580732840987 | date | Date Completed:
| checkpoint | 3.2 - Bedding
15327582-5012-51ec-a0bc-12b3fb365f4d | note | Frequency: Each Lot
1300c008-15b4-53c6-b9f5-f077c5e0358d | note | Acceptance Criteria: Pit base to be poured on 75mm min. depth of 75mm Class 3 FCR.
81324bf5-d8b8-5fc9-8c1a-75bd526ec12a | note | Reference Documents: EW-CE-DRW-526-001 C.5.15
138a9d78-2827-5d62-94a8-09a7e66f0f9e | note | Inspection / Test Method: Inspection
427ed76f-6654-57c3-ba61-23107ed56a42 | note | Record of conformity: This ITP signed
0068725e-e32f-5648-819e-0626a549caa5 | note | HP
622cb62a-d361-50d4-a2d4-6d6c50ce3de3 | note | Responsibility: Site Engineer
49544b50-50a2-57c2-b50b-ac4d30a5f255 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.3 - Formwork
c657f43e-ddcf-5256-ac3a-082bc3c3c810 | note | Frequency: Each Lot
c8dda0be-9771-5b9a-97da-e5e16b0bc158 | note | Acceptance Criteria: Formwork shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
81b1dd80-4b77-5b72-b2a1-adc0538d80eb | note | Reference Documents: Work Procedure
993b7855-3fd3-510b-abb6-541e68739108 | note | Inspection / Test Method: Verify
97531949-31f9-502e-8789-c45f76534a3e | note | Record of conformity: This ITP signed
e7b0d00d-b1a3-53d3-a2d3-51444453332c | note | IP
95150586-97dd-58bb-b0e9-4527529be88c | note | Responsibility: Site Engineer
54145665-5e40-503e-8844-346910bae352 | date | Date Completed:
| checkpoint | 3.4 - Subsurface Drainage Accomodation
757bd975-c34b-5ad3-83bf-4f93ee72f47d | note | Frequency: Each Lot
68bad9af-0468-5d4c-924b-d6a65dbdebb6 | note | Acceptance Criteria: Form holes in walls to accommodate subsurface drains as directed.
887cd8ab-8329-5976-9c5c-e56ee11d3330 | note | Reference Documents: EW-CE-DRW-526-001
dc5e7794-3b27-596b-86b1-235333a3ef3a | note | Inspection / Test Method: Inspection
8c88fdee-edf8-5b99-91bd-4a61d5da686e | note | Record of conformity: This ITP signed
70a5d4b4-b735-5610-8319-8c41b4027a81 | note | IP
d01790a4-ab2c-5563-9153-e3a19d59439d | note | Responsibility: Site Engineer
9659077f-abc5-5e0b-b0eb-1cdd497846bf | date | Date Completed:
| section | 4 - Reinforcement
| checkpoint | 4.1 - Steel Fixing
eeee8823-9d67-5e9b-b073-b20ee38d4354 | note | Frequency: Each Lot
0b9a3a64-9ea4-5114-bfc0-5f946288601e | note | Acceptance Criteria: Reinforcement type and design to be in accordance with reinforcement schedule on DRW-526-001 with a 300 min. lap
635cf359-f8cd-5087-8dd3-58fe7e26e809 | note | • Reinforcing steel shall be bent and placed in accordance with AS 4671 and sufficient bar chairs shall be installed to ensure reinforcement is in the correct position.
8b02a1f5-def8-5582-8d3a-d8f6e4b739a4 | note | Reference Documents: EW-CE-DRW-526-001 Work Procedure
613798ce-33ea-5c8f-9e51-19988aa97019 | note | Inspection / Test Method: Verify
86edfd3e-0311-5cbd-aeb5-404b2a8fc6ed | note | Record of conformity: This ITP signed
7bfdfb93-83fc-5212-8148-d0bb0e88800b | note | IP
08b146db-10ca-55a4-8941-9373857e3289 | note | Responsibility: Site Engineer
8c07ca2b-aa42-548b-a6a1-ad6f483bf81f | date | Date Completed:
| checkpoint | 4.2 - Reinforcement Installation
9a7a144e-cfff-56f0-bdf1-856b22bb602b | note | Frequency: Each Lot
8068037c-eb2b-57ea-8c14-4b3eb384d7a0 | note | Acceptance Criteria: Pre-pour Checklist Completed:
60eb353f-2537-58a1-9365-8834bb8c4d04 | note | – Position and spacing check and recorded
cf7b997f-0901-5370-b566-f022475cb4d4 | note | – Cover checked and recorded
22ccfda4-0ce2-5ff0-af9a-b274498e00ac | note | – Reinforcing supports checked and recorded
06b7b196-5092-5e95-84ef-b8bc8885ab14 | note | – Laps at required length
c40bf909-026a-5d8c-b1c8-b812be8a5871 | note | Reference Documents: Work Procedure
b781bf42-a6c8-5c77-b39a-88e91a98b088 | note | Inspection / Test Method: Inspection
1c4ccef3-7ec3-59af-a434-b02afb138d04 | note | Record of conformity: This ITP signed
f0f17a7b-12d1-5ec9-8d33-1d25df694f45 | note | IP
d581b896-2e80-50b5-84ad-f2e5c5ed1cf4 | note | Responsibility: Site Engineer
f82a45ba-47da-543b-892d-01ab7876eb32 | date | Date Completed:
| section | 5 - Inspections
| checkpoint | 5.1 - Pre-pour Inspection - Pit Base and Pit Walls
ed9d8a6e-d8ab-5762-b2ec-0be0c339e6e7 | note | Frequency: Each Lot
2c842551-3836-5b1d-a64e-3f29062f9921 | note | Acceptance Criteria: Concrete shall not be placed until:
b60054a3-c4bb-594a-b0a2-fbeea42fa1dd | note | (i) the evidence that the forms, reinforcement, any stressing materials and embedments conforming to the requirements of this specification and the drawings, has been reviewed by the Superintendent
0c984e5c-149b-50c0-9908-8a806ca8cb6e | note | (ii) all foreign material has been completely removed from the forms
91fd72d8-359e-5742-a3b7-4b12333ba65a | note | • Superintendent requires 48 HR notice for inspection.
2edbf3dc-194d-5deb-b686-28e3dba5ab93 | note | Reference Documents: C.5.15
cab9c703-2dbf-535d-988d-054cf7fd428d | note | Inspection / Test Method: Inspection
5beb74a9-af76-5e25-b22d-bd885fbaefaf | note | Record of conformity: Pre Pour Inspection Checklist Completed
65422e32-b8f5-5ddf-92a0-e04f05253c19 | note | HP
8acd1511-f7e9-59d5-bbac-a41843d30a85 | note | Responsibility: Site Engineer/ Superintendant
f700bc1c-870a-5073-b8b1-f3799a1f5f93 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 6 - Placing and Finishing Concrete
| checkpoint | 6.1 - Pour in-situ Pits
0f7ba03a-0539-5f65-a2e7-5ee4ea6f77a2 | note | Frequency: Each Lot
7c11a96f-889d-50b6-8c31-a5537520709c | note | Acceptance Criteria: Pits shall be constructed to the detail shown on the drawings
646658d8-9eaa-5849-90b7-68ade124e813 | note | Reference Documents: EW-CE-DRW-526-001
2e3b37b5-a5b2-56c5-a751-266d436b85f7 | note | Inspection / Test Method: Inspection
ea15e7cb-7d25-5a58-a627-64109b2f0c83 | note | Record of conformity: Concrete pour record and delivery docket
e90afb25-ccca-529b-ab25-7f164cad70b8 | note | HP*
2df0c5c1-6dc8-54cd-b417-25670dae22eb | note | Responsibility: Site Engineer
f56ea57e-5869-5dff-9f26-a8ec9afa0bc3 | date | Date Completed:
| checkpoint | 6.2 - Finishing
4d37c0f4-a012-53cc-b8d5-558453d4a213 | note | Frequency: Each Lot
d1117932-317b-524b-8529-9e44ea965563 | note | Acceptance Criteria: Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces
74a1aeef-fd7c-5f9e-8fe8-98c70316a46b | note | • Concrete surface finishes to meet Class 4 requirements as per table 3.2.3 and 3.3.5.1 of AS 3610. (Attached Below)
2b79d422-9352-53ce-bd18-bd9baf30d57a | note | Reference Documents: Work Procedure
a9f9bada-a56a-51af-b7dc-c7e89e8a1f30 | note | Inspection / Test Method: Verify
4a94cbcf-17ad-5de1-b04a-59fdabb45c79 | note | Record of conformity: Completion of prepour inspection checklist
88583bba-a322-58ff-9c4d-0b78b103d50a | note | IP
67c7f229-1fe4-5bc9-a7ec-4a5d1dd0e79e | note | Responsibility: Site Engineer
34bc0954-085b-514f-b271-7e3ed0a548c9 | date | Date Completed:
| checkpoint | 6.3 - Installation of Pit Cover
0988c0ba-6bdd-5c25-b7ec-25a6aed343be | note | Frequency: Each Lot
d2ed28ee-5709-570f-b86f-ebea91d68f7f | note | Acceptance Criteria: Precast concrete cover or cast iron concrete infill SEP cover to be installed as scheduled
43ccdd4c-fa69-584c-b963-cc9f7796b54e | note | Reference Documents: EW-CE-DRW-526-001
191875fd-1240-53fa-9bd4-717ab164940d | note | Inspection / Test Method: Verify
e8f510f9-89f9-5c2a-84f8-04f2d476ed27 | note | Record of conformity: This ITP Signed
69a8532d-b34b-5d21-a696-d3d2d9b4cc72 | note | IP
b286b0eb-cf3c-5f4f-b94e-4cb3fcf8b003 | note | Responsibility: Site Engineer
de756b69-a7c6-5d3b-a11a-91054e6c9dc9 | date | Date Completed:
| checkpoint | 6.4 - Concrete Testing
1963fe79-9063-5a80-8d59-5d05c58ec1b0 | note | Frequency: Each Lot
8994b029-6f29-531d-afae-da868e8e31d6 | note | Acceptance Criteria: Concrete Testing to be carried out as per specifications. In AS 1379
6d96152c-9204-5367-bb94-a3ff95410e70 | note | Reference Documents: Work Procedure
12e2aeab-d7f7-5680-bfe8-02bc856ea54c | note | Inspection / Test Method: Verify
6883c5ff-83b3-570c-b10b-161fe79f7a65 | note | Record of conformity: Test Results
73934e9d-3833-5e71-bed1-50089520717d | note | TP
2ec7aef6-d926-5908-8774-9028cbcf451e | note | Responsibility: Site Engineer
b3c86552-5985-539f-91be-211e64380d8d | date | Date Completed:
| section | 7 - Post Pour Details and Inspections
| checkpoint | 7.1 - Concrete Curing
564d6a88-73d8-57d2-9438-7334917cae60 | note | Frequency: Each Lot
50c375ce-a080-58c4-938c-01dbc0a634b5 | note | Acceptance Criteria: Concrete to be cured as per project specifications
0de7bfa9-e192-5529-ad31-e51ba3a6294c | note | Reference Documents: EW-CE-SPC-000001
328652d3-0635-5f4d-84c2-22921ad54858 | note | Inspection / Test Method: Verify
b90db286-28de-57bd-909f-2ea6dba6c4c8 | note | Record of conformity: This ITP Signed
574f0000-e60f-5142-84e6-2909e8e56e93 | note | IP
9dc3dd8b-75e4-5f5f-930f-327a7a539253 | note | Responsibility: Site Engineer
a2320189-cd34-56aa-9562-41d62fa02f25 | date | Date Completed:
| checkpoint | 7.1 - Removal of Formwork
9ab6cec4-c9db-5cdc-9847-87cb5a14dc71 | note | Frequency: Each Lot
884dff44-6006-5a9e-984c-cd181609d329 | note | Acceptance Criteria: Stripping of vertical faces in accordance with AS 3610 as per Table C2. See Table C2 Below.
7e0ba4cf-530c-56d8-bec9-ac1dd47a8ded | note | – – – – – – – – – – – – – – – – –
2184b3fd-3fd6-5f3c-a7db-e79feb35adac | note | Table C2 Vertical Face Formwork Minimum Stripping Times After Casting
d47a2b6d-770b-5601-8ad3-afd24511d61f | note | Classification ¦¦ Average temperature (Greater than 20°C \ Between 12°C and 20°C \ Between 5°C and 12°C)
a8613d10-3d1b-5afa-a8da-1eaceefa6ade | note | – – – – – – – – – – – – – – – – –
83860127-7c51-56f6-9caa-a84e48464915 | note | Class 1, Class 2 or Class 3 (see Note 1) ¦¦ 1 d \ 2 d \ 3d
9c3579ba-cd4b-59f2-806d-27173f72bff6 | note | Class 4 or Class 5 ¦¦ 9 h \ 12 h \ 18 h
82a5e0b1-f046-55aa-817e-e7a982c37697 | note | All ¦¦ A minimum of 1 d applies to the stripping of vertical faces where frost damage is likely
bfd21f43-16f4-5050-8fa2-0ceef25fdb59 | note | – – – – – – – – – – – – – – – – –
359667b5-6db1-534a-96b9-4a1a6917c8d8 | note | Reference Documents: AS 3610
f3a83aa9-7c3d-5caa-83bb-f4366fc6269f | note | Inspection / Test Method: Verify
4f48d622-0a1e-5b20-94fb-2a336cc00b6a | note | Record of conformity: This ITP Signed
c4971835-dd80-5971-aacb-e079b7ed5511 | note | IP
5b51fb25-1d19-53bb-a871-541e2929b0c6 | note | Responsibility: Site Engineer
689a8f5e-b7ac-5ec9-bc52-e31369d9cbce | date | Date Completed:
| checkpoint | 7.2 - Allowable Tolerances Level & Alignment
ba6d0b14-b278-5a5f-9ab3-525c2ed35adb | note | Frequency: Each Lot
bc3dedf4-4047-5d67-a87b-54028d64fc1f | note | Acceptance Criteria: The horizontal deviation of any piped or box culverted drain shall not exceed 25mm from the true alignment. There shall be no obvious sharp changes of direction.
0d4e56f9-897e-5ac7-bad3-d25cfb98f22c | note | • The maximum deviation from grade shall not exceed + or - 10mm for grades flatter than 1 in 500 and + or - 20mm for grades steeper than 1 in 500.
d3165258-4a55-5e4b-bffd-707d81755790 | note | • The grade of any piped, box culverted, or open drain shall not exceed + or - 5% for grades flatter than 1 in 500 and + or - 10% for grades steeper than 1 in 500.
453fb24a-3996-51ec-9ade-86e681e47b0e | note | • Invert levels at structures shall not exceed + or - 10mm from the design invert.
b00d282c-1e91-5a73-ae0d-c4edf3611356 | note | • As-built survey completed for lot
58c08823-90df-5039-a4da-f8b427a6cb27 | note | Reference Documents: Work Procedure
18508920-f90c-553b-947a-27de3f6b6a07 | note | Inspection / Test Method: Verify
fdcd48ef-084f-556c-aab5-52234d8b7bcb | note | Record of conformity: This ITP Signed
7a4c303d-66f6-5b92-bf50-c35ad3a2da97 | note | SCP
8c381c18-79e8-5c1e-bdbb-d7ac0c76c2d2 | note | Responsibility: Site Engineer
acb22d1d-34f9-57e5-a8c4-88277a8397dc | date | Date Completed:
| checkpoint | 7.3 - Post-pour Checklist
3afd463d-7e2f-5d70-b32f-acf74b3adac3 | note | Frequency: Each Lot
78eeab88-43ba-58b8-87fc-6b01416a7ffd | note | Acceptance Criteria: Completion of Pre Pour checklist quality checks.
adde86a2-5147-5a5a-b04f-4ad8ba70f54e | note | Reference Documents: Work Procedure
6ccd0e60-a526-56af-97dc-986b19c2a74d | note | Inspection / Test Method: Inspection
9dd1fb26-0109-591c-a267-8cacbca3462a | note | Record of conformity: Pre Pour Inspection Checklist Completed
f6d75671-fecc-5894-940c-2a25f9bbe0da | note | HP*
d08e2db1-5f1d-50bb-a1d9-613685b3f0a3 | note | Responsibility: Site Engineer
4d3f48da-cfb9-56da-bfb3-d48595ca22f4 | date | Date Completed:
| checkpoint | 7.4 - Backfilling Around Pits
523cbb36-7c7a-5b84-9235-6dba39442c7e | note | Frequency: Each Lot
97194e9a-2394-54ba-9835-637f2c1a7e8d | note | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
3b18ca04-e98d-5d77-92da-69dbd877e073 | note | Reference Documents: Work Procedure
105c3c0c-9098-5b88-88ce-66dfe70343f7 | note | Inspection / Test Method: Inspection
f1a2eab1-ea9c-5230-aff6-853f28577b72 | note | Record of conformity: This ITP Signed
2fa906c4-de20-5723-8911-a728142552b2 | note | HP*
37f97d81-7d07-5cfe-b43f-6f9ed3d447e0 | note | Responsibility: Site Engineer
8b41a2ad-cf70-5169-ae9b-06105eb305aa | date | Date Completed:
| checkpoint | Final Inspection
d277cf9b-cd91-5a03-9d2d-932e4d3743fa | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
15d0984c-9276-5e59-9e7f-438d03d3d3f0 | textbox | Print Name:
af3961af-08ce-5798-ac9c-b9c92d02a77c | textbox | Position:
a3b35eed-ade2-545e-9289-e8e489c5c55b | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-009 - Unbound Flexible Pavement Construction | itp | GT4-ITP-009 - Unbound Flexible Pavement Construction | 4e3f6c53-b448-45dc-9cc1-2d96357d3dfa
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
5d7153d0-06d3-5aba-977b-fcad662e3e61 | note | Frequency: Prior to commencing any activity
083bfe36-24c0-52e2-af90-7df9d913a036 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
0ee5686d-51fa-58d8-baa1-3369105cc36a | note | – using the correct and complete set of drawings
b4e78189-d8ba-56dc-93b9-0a67a6d0ae99 | note | – all drawings are the latest revision
3ceb4fde-58cf-594e-9fbf-cb7531e8bfb1 | note | Reference Documents: Drawings and drawing registers
4e740a8f-6218-5231-907e-bb6282bbd531 | note | Inspection / Test Method: Visual inspection
cc60060c-ee12-53d2-9de7-edeaf22d00b9 | note | Record of conformity: This ITP signed
1d562dc1-8f26-5068-8eb7-38bb39865020 | note | HP*
1c3eace7-8660-5930-ac2e-f007500f1afd | note | Responsibility: Site Engineer
1d3fafe8-d524-5b84-bbd3-7b27c22d2dfd | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
d38902b3-c4ee-5f2c-ba83-9404f3f22eb0 | note | Frequency: Prior to commencing works
1d141e00-3c06-570c-a420-7bf41da8b407 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP`
e64051db-3586-5ee9-a089-f7a16a4ea596 | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
8b4209a6-64f2-5aef-a4de-ee52c8b5fec2 | note | Inspection / Test Method: Visual Inspection
909a61bb-5296-5a50-9054-c636029ce637 | note | Record of conformity: This ITP signed
68658650-be52-5cf8-99d5-e8e62e047bac | note | HP*
a442c38b-2105-52db-a87e-f790e7266638 | note | Responsibility: Site Engineer
8cc2f8ac-8b1f-59d2-a053-6ac1b054a93f | date | Date Completed:
| checkpoint | 1.3 - Plant and Equipment
1b2a2f4a-9558-5961-a81d-33e6e60e37d1 | note | Frequency: Prior to commencing works
178b7060-f162-5a6a-9fbc-53ab2d502d36 | note | Acceptance Criteria: Plant and equipment used in the Works are appropriate to achieve specification requirements and is inducted
222decf0-50fc-5c77-ba0c-fd7b7fd08208 | note | Reference Documents: N/A
ba9b9516-61f6-53e7-96e0-470cc9437f92 | note | Inspection / Test Method: Visual Inspection
a4402dfb-4c2f-5529-8142-79cb35100197 | note | Record of conformity: This ITP signed
fc7ec349-d2fa-557e-87f7-42df68a7e205 | note | IP
495969cf-d0af-54d6-b454-e8d4fbb4df22 | note | Responsibility: Site Engineer
20a119a2-7a72-5d9a-9bf7-2b1f428228b5 | date | Date Completed:
| section | 2 - Placement
| checkpoint | 2.1 - The commencement of construction of base and subbase
7547365d-0343-55a8-b69d-b68f34f0db87 | note | Frequency: Prior to placing subbase
6919dfe3-3169-5db8-8974-d3bd38013a5f | note | Acceptance Criteria: After the sub-grade has been compacted to approval, the crushed rock shall be spread in even layers of 150 mm maximum loose thickness.
ab957727-11b0-5c96-868e-175ad36fc63c | note | • The material shall be spread to produce the required consolidated thickness by means of approved mechanical spreader. The material shall be maintained within +/- 2% of OMC, with additional water being added if required during compaction.
4e94ff1c-1eed-5019-b8cd-049d8637d64e | note | • Materials shall be spread without segregation of large and small particles, between approved edge boards or kerbs
5119fed7-18ae-53cf-b7e6-be208c622b9d | note | Reference Documents: C.9.2
6abff012-91a0-5658-aa79-4446a9d23962 | note | Inspection / Test Method: Verify
fc2255e0-a818-58e1-ad54-59e792c9af43 | note | Record of conformity: This ITP signed
0e196c73-4e93-5792-bad9-b6aff05012ed | note | IP
a5619475-53a5-5b2e-b96b-edd7089162db | note | Responsibility: Site Engineer
44779ffd-dd9c-5210-a527-9fc82c36f27d | date | Date Completed:
| checkpoint | 2.2 - Shape
fdc9e166-f1f8-5acc-88b5-d54efc610f17 | note | Frequency: Each lot
4d5daa71-d0a4-5655-8cbf-baa97d1b8bfb | note | Acceptance Criteria: Rolling shall be performed in such a manner as to eliminate bumps and irregularities with the finished surface true to the required grades and cross-section.
ba014ccd-d73d-5831-a9f7-9092a5254738 | note | Reference Documents: C.9.3
f37f83ca-8997-5b14-a0ae-849ee0156655 | note | Inspection / Test Method: Verify
72036ee9-e9e3-5721-a9f9-322868c7c4ab | note | Record of conformity: This ITP signed
a1ee398f-7fc3-524c-9887-46a8c9018a36 | note | IP
22fa975f-f758-5441-a1b7-8f5f74aec7c5 | note | Responsibility: Site Engineer
4dbac5f5-9c48-51b0-9cf6-c477789b7876 | date | Date Completed:
| checkpoint | 2.3 - Delivery Dockets
343d4a9d-f604-506f-9be9-b67d4a7c7bff | note | Frequency: Each lot
ba02b1db-04e0-51c5-950e-a50fc67a8230 | note | Acceptance Criteria: Where material is scheduled for measurement by loose volume in delivery vehicles or by mass, a delivery docket for each load shall be issued to the Superintendent at the point of delivery.
5fc4c725-1e3e-5dd3-bff3-50033d239635 | note | Reference Documents: Work Procedure
f785085e-b3ea-5894-b110-83ac0bf0fbc4 | note | Inspection / Test Method: Verify
51e7a359-e385-53b2-9787-dfe558595d05 | note | Record of conformity: This ITP signed
97eed60c-adbc-5ea4-929c-906899412b03 | note | IP
c8b8d687-96c9-52fc-9176-2c9144a9940c | note | Responsibility: Site Engineer
2ea5c327-1224-5a4b-b474-381da9e609ba | date | Date Completed:
| checkpoint | 2.4 - Layer Thickness
18250d0e-cc1e-5688-9353-b2f83d416409 | note | Frequency: Each layer
c6dfd75a-9340-5041-a941-a1766665378f | note | Acceptance Criteria: Material is to be compacted to the overall thickness shown in the drawings (dependent on pavement type),
dff2ba0d-decd-5228-b389-7b4e7b6a7270 | note | • Subgrade to be within +5mm or - 30mm of design
0d8a9525-ed70-5983-b38e-6afd96a9e54e | note | • Subbase to be within + 10mm or - 20mm of design
c5ce51b4-71aa-599c-a06d-ca2e78d2dc0e | note | • Basecourse thickness to be 0mm from design level
17d69759-c720-5fa4-bbe4-2827af4b3c3a | note | Reference Documents: EW-CE-DRW-406-001, EW-CE-DRW-416-001 C.7.4
44a66ea0-cc27-51f7-8014-0246794459b6 | note | Inspection / Test Method: Visual and Measure
473fb4d0-b23b-5e7c-82a6-b7cb9d1f66a1 | note | Record of conformity: This ITP signed
b2f0503e-c9b1-53ce-a90f-764155affc7e | note | IP
8022c632-010f-5954-8caa-232137d587ad | note | Responsibility: Site Engineer
cee956c6-af85-51ee-b08f-6b48530a8985 | date | Date Completed:
| checkpoint | 2.5 - Conformity with Drawing
3645555e-d656-527d-9c52-b21bbf9bd664 | note | Frequency: Each lot
85afdc98-0c27-5ea9-8701-caec2b0f7a50 | note | Acceptance Criteria: Width of each side of the pavement shall not be less than the specified offset width or more than + 300mm outside the specified offset width when measured at right angles from the centre line or design line.
f44609dd-a978-5935-b968-f4b577a22b8b | note | • Where pavement is to be constructed to the lip level of kerb and channel, it shall be constructed flush with the lip of the channel or not more than 5 mm above.
3abfb819-e671-5e13-8a53-90feb7148345 | note | • Any material that has been compacted and then trimmed from the compacted surface to conform
1ecd84e3-bd6d-5d98-957a-5b1ca6df3896 | note | Reference Documents: C.7.4 Work Procedure
250d4534-1193-51c8-bb5d-b641bb25fb9d | note | Inspection / Test Method: Verify
728ab8e6-3451-5443-aac8-3c847ba20cb0 | note | Record of conformity: This ITP signed
00f6d732-6f88-5094-a239-66fe73c27a22 | note | IP
03583a0e-12fc-5295-a033-e776c65c613c | note | Responsibility: Site Engineer
c3c71ca2-315f-5d66-836e-8b87daf407b5 | date | Date Completed:
| checkpoint | 2.6 - Jointing
05e7f53b-a6ae-568b-97d5-155c4d27f0cd | note | Frequency: Each lot
679214b8-b98d-50be-907d-44361360264f | note | Acceptance Criteria: (a) material shall be spread in such a manner as to minimise the number of joints
a2beea88-4093-57e4-ba43-03c7618a5a09 | note | (b) transverse joints shall be offset from one layer to the next by not less than 2m
9581cf83-7fc9-51c9-ac7e-88719d417988 | note | (c) longitudinal joints shall be offset from one layer to the next by not less than 150mm
7bbb8a42-5220-5a6e-8c66-51ec71f0d192 | note | Reference Documents: Work Procedure
45cf0f0d-ef8b-56bf-b5e1-796d423c66f5 | note | Inspection / Test Method: Visual Inspection
e60a148e-9e0d-5d54-8fad-ad1fe141ed38 | note | Record of conformity: This ITP signed
cc45eeeb-5906-518c-9acd-4d66e172d02b | note | IP
42b6048e-51d9-50a7-b8ff-e380da0ef775 | note | Responsibility: Site Engineer
977927b9-5d9c-50cb-aa29-c7802bd5ebe0 | date | Date Completed:
| section | 3 - Testing and Conformance
| checkpoint | 3.1 - Test Rolling
c52ead6f-d0e9-568e-b476-24f9ee2c19f2 | note | Frequency: Each lot
a9f96e39-c692-533f-a43d-ac9640254b4f | note | Acceptance Criteria: All pavement layers shall be compacted to withstand rolling and shall be test rolled in accordance with table 5 of section C.7.2 prior to acceptance of the layer.
7457d6f1-b3bb-5c35-a8f3-e84af6ab44de | note | Reference Documents: C.7.2
0cd5df29-373c-5b8a-86ae-95cc9dc4cef3 | note | Inspection / Test Method: Test Roll
3da7c3ab-d777-50b6-b177-16bae9e5234f | note | Record of conformity: This ITP signed
b9180274-5ee7-5f4c-a302-e7b4f7c0060e | note | HP*
91bfda13-5019-54ba-b01e-96fa8232e55e | note | Responsibility: Site Engineer / QAV
9bcc95f5-f74c-5812-bdca-b08b22b550eb | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Compaction of road pavement
b6518bcf-656f-54ef-bf33-93b03ba6e8f4 | note | Frequency: Every Lot
16a9c3ac-274c-5bcc-b4cf-af9ac0c24643 | note | Acceptance Criteria: The minimum compaction achieved shall be 100% of the Standard Maximum Dry Density in the base course, and 98% of the Standard Maximum Dry Density in the sub-base course
f04a9f57-a3e4-5fd2-b100-39f41e865835 | note | Reference Documents: C.9.4
9502033d-f1e6-5f6c-a8d6-989ff65a84db | note | Inspection / Test Method: Test point
47858a3a-188f-5c5d-9cdb-e3fa81abab9f | note | Record of conformity: This ITP signed
25998cf0-0b2d-51a5-bd34-394150fed969 | note | HP
53c9c37c-e6c6-5b7d-8b29-e53e69d66eb4 | note | Responsibility: Site Engineer
5a5e1859-6dbc-5bef-8315-0ffe11b2f9b3 | date | Date Completed:
| checkpoint | 3.3 - Completed Surface Level Compliance
7e7d67ab-8110-5a52-8b11-e947531e8c3f | note | Frequency: Each lot
f91f31a4-bc0e-5e14-83c7-cedddae76e84 | note | Acceptance Criteria: Surveyed as constructed drawings to be provided showing finished contour levels.
dcdddc75-76fe-5d53-865f-8b8c54f99693 | note | ○ Spreading, scraping and consolidation of the various layers of the pavement shall proceed with each layer having a construction tolerance of;
f3a9ecd3-9a7e-547f-88ed-155851f060ba | note | • Subbase: + 10mm or - 20mm
9fa23e74-f609-5296-b7a4-87a609fd1a92 | note | • Base: + 10mm or - 10mm
31236767-a5d9-57c3-9c32-4d49b8730406 | note | Reference Documents: C.7.2, C.9.4
3ebf6f52-987b-53f9-8a98-3579db58b654 | note | Inspection / Test Method: Survey
3b34e359-19d9-5c42-a06f-0a18f5f9b558 | note | Record of conformity: This ITP signed
a8761064-e118-56e5-a7c8-d620a04958a0 | note | SCP
77c0a8d2-86dd-5d39-98fd-4259714a806d | note | Responsibility: Site Engineer
09eca7d5-28ce-5a6f-a1d7-29f54c6e5267 | date | Date Completed:
| checkpoint | 3.4 - Shape
80a7da86-ac57-5f7d-9a43-af824c70b44c | note | Frequency: Each lot
0fd39ec2-056e-5caa-bbbe-dc635d6b6156 | note | Acceptance Criteria: Layer to be finished to a smooth and uniform surface and after compaction and meeting the following tolerances:
3d828167-f185-56fb-8fdc-18a89cf4b94b | note | • Crossfall: + or - 0.5% of design
7b34c6e6-bc24-56b6-a6b7-6b2bae36ec06 | note | • Surface: + or - 15mm when tested with a 3m straight edge, laid in any direction.
22623f6d-13a8-5005-8aff-bc2bd00dc0f3 | note | • Longitudional Grades: The gutter grade shall be + or - 20% of the design grade.
64834a3f-7987-5508-a5c6-1589fbc01935 | note | Reference Documents: C.7.4
39725ee5-72fc-5dee-b36f-ab41ab6f8e7b | note | Inspection / Test Method: Test Point
8fb8f3a7-e478-5a8c-8af5-619500913a40 | note | Record of conformity: This ITP signed
c8702bc0-9c37-5ca7-aedf-6df61690a601 | note | TP
36770c0d-14aa-5e1b-9231-d8112dd61793 | note | Responsibility: Site Engineer
804c4e4c-7f17-5ef3-a176-d125ae951168 | date | Date Completed:
| checkpoint | Final Inspection
c2623af2-22ff-5802-a942-c5d400012d07 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
e27e4def-a14f-5efd-b343-8aa7307739a1 | textbox | Print Name:
3cdb022b-d9ed-5125-bc20-975e9c2ad9ee | textbox | Position:
2ee822bf-1945-508a-bfe7-913e3f16f9d3 | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-011 - Earthworks - Cut, Fill and Subgrade Preparation | itp | GT4-ITP-011 - Earthworks - Cut, Fill and Subgrade Preparation | aec322a2-b1d6-492c-bc7b-0cb64026f1fd
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
8a753a8c-32ed-508a-a5e8-6e2bfe58c5b9 | note | Frequency: Prior to commencing any activity
c42f3869-07c8-5153-90ff-5e0143b3193a | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
2b0cf2c0-a866-5033-9758-b7369b3c7414 | note | – using Issued for Construction (IFC) drawings
cf519249-9729-5d79-bb99-9a5f378b4847 | note | – using the correct and complete set of drawings
e924bb3d-7a8b-5545-84c5-5904b538040c | note | – all drawings are the latest revision
d0b14467-b6b8-5722-b1b6-37f5c9fb519f | note | Reference Documents: IFC drawings and drawing registers
fb81552e-e241-5740-8f85-4ed3db28727e | note | Inspection / Test Method: Document Review / Visual inspection
d6c677cc-c64b-5f7e-9d68-ce1f3f102ddb | note | Record of conformity: This ITP signed
4d49f17a-5390-5422-9a54-ac8c67665edb | note | HP*
b2881af2-af0c-5606-bf90-4be4641044f4 | note | Responsibility: Site Engineer
8e24da28-cc5f-5d5f-9710-9dad3a0f1288 | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
a5ef81ca-b524-5c2c-a4f4-a4f5d2a0cb95 | note | Frequency: Prior to commencing any activity
6d192dcb-b22b-5113-af61-0ce10a2e0600 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: OHSMP, EMP, TMP, SWMS & WP. Access and egress inspected and assessed for stability.
81e673ad-b2f3-58d5-9605-95352dd20cd0 | note | Reference Documents: OHSMP, EMP, TMP, SWMS, WP
d9d9e7a2-b9d7-5b56-ba2b-08bb5edb5812 | note | Inspection / Test Method: Visual Inspection
62d4ab43-04db-5417-95a5-cda6c300e22d | note | Record of conformity: This ITP signed
ac5d067c-8d0a-5318-943e-78c75095adcc | note | HP*
e64cd76b-0cc9-5948-8cc5-49a3167bedb9 | note | Responsibility: Site Engineer
c1c13eec-0449-5fb6-8a32-582b5a246cfd | date | Date Completed:
| checkpoint | 1.3 - Survey set-out
7edc15ba-478b-539a-8f22-7bbdb7b7a152 | note | Frequency: Prior to commencing
b0b5decc-6e94-5f3b-8dc2-e02a66350470 | note | Acceptance Criteria: Prior to any excavation, the general areas within the definded limit of works as part of the Early Works package, and site works within the contract shall be set out by suitable hurdles, pegs or markers.
1b6f5ea3-e5a6-54c3-a49a-1bea0f2ec3f9 | note | • Levels shall be established and pegged from a common datum.
520b5e53-21aa-525b-8207-b8b780b6f9cb | note | • All setting out shall be carefully checked against the drawings prior to commencement, and any discrepancies clarified before construction commences.
dbc6728e-ba1a-5ea7-bbf8-4b7d0e38e5ca | note | Reference Documents: C.2.3
b5123fb9-9568-5498-bd9a-1f0529608528 | note | Inspection / Test Method: Visual Inspection
36326ea6-fe40-5b0b-9810-71981a10441c | note | Record of conformity: Survey records and pegs on the ground
36bc7d3b-7776-5c3a-aa75-9d6b9b033687 | note | IP
48fa4998-1e6c-570d-b1f8-c64742bbcc8f | note | Responsibility: Site Engineer
bb9b68a8-058e-5494-b3d0-6781a6e1b27c | date | Date Completed:
| checkpoint | 1.4 - Ground Penetration Permit
5ebe2ab6-eef0-5a03-869c-506fe6f45d82 | note | Frequency: Each Lot
0ad29418-fe60-552d-b4b8-a6ece47b2406 | note | Acceptance Criteria: A ground penetration permit must be issued prior to excavation commencing.
2855f87f-2961-5219-ad35-b83439cbc040 | note | • Plant and equipment must be appropriate for the task.
d482a422-7721-52ae-a326-2ef568f27ef2 | note | • Excavation operations shall not disturb areas outside the limit of excavation.
957b70f6-a0ce-5a32-a81a-043ced4f8963 | note | Reference Documents: Ground Penetration Permit
41b81796-4c96-5c73-a7d0-62d8bc575fde | note | Inspection / Test Method: Verify
c93fc0d9-5c17-5ad3-bc34-c7eb7615da4b | note | Record of conformity: This ITP signed
8bc60e1d-c7ab-54bc-b812-c43e2ad76e17 | note | IP
92bfce06-f9ec-5ab3-856e-3c4cfcd8e455 | note | Responsibility: Site Engineer
f721063e-a74f-5fb7-a3a7-4d0807a29e9b | date | Date Completed:
| checkpoint | 1.5 - Protection of Services
a769e836-8113-5f83-9569-dc3a48e3d435 | note | Frequency: Prior to commencing
5274e7a8-8d96-57a6-bf7c-b8a8090d614a | note | Acceptance Criteria: The Contractor shall and all personnel on Site shall familiarise themselves, under his direction, with the location of all existing services on and adjacent to the site.
a408c880-0a29-5d04-9216-ec2043021471 | note | • The existing services shown on the Drawings may not be representative of all services within the site of works. It is the Contractor’s responsibility to locate all services both in plan and depth to avoid damage and disruption to authority assets
929fb532-55fc-5630-b7fe-cf8991c1733c | note | Reference Documents: C.2.4
70bcff31-c718-5818-aef3-db968dd69f92 | note | Inspection / Test Method: Verify
07fa7767-8708-50be-965b-b149e3aaa20e | note | Record of conformity: This ITP signed
856f1b3a-3c55-5639-b251-4ef0720bc2ce | note | IP
1a489b96-fb5a-5776-9f07-5f17b1ed9a00 | note | Responsibility: Site Engineer
baf66c69-f27c-548a-bcce-9453160e54ec | date | Date Completed:
| section | 2 - Earthworks
| checkpoint | 2.1 - Material Categorisation
ce83bdd3-7270-5799-a2e0-35357967c119 | note | Frequency: Each Lot
8291658a-9709-5da2-a467-e35aa8f3406b | note | Acceptance Criteria: Prior to commencing excavation in any area and during excavation work, the contractor and Superintendent shall inspect and agree upon the type / category of material encountered
3c035d91-1290-593c-b57f-2693fbd2d84b | note | Reference Documents: Work Procedure
60216bfe-ee2b-570c-a243-958b3cdf6de1 | note | Inspection / Test Method: Verify
9d9847ce-b410-5ace-8f48-ad2d970b4bb5 | note | Record of conformity: This ITP signed
4d6477f1-1430-508c-b4dc-c95479a78e17 | note | HP*
8edc43ef-10b6-54dc-b7e2-7b78b7af9347 | note | Responsibility: Site Engineer / QAV
8916c340-f4ac-5142-96b0-00fb572ae6ad | date | Date Completed:
| checkpoint | 2.2 - Stripping of Topsoil
fbd81d6c-c5e0-5989-a79d-24f9aca982b0 | note | Frequency: Each Lot
fb68dfbb-ec36-544e-8c48-d6349fd807e2 | note | Acceptance Criteria: Topsoil stripped to full width of the formation and placed in approved stockpile location. Stockpile shaped to shed water and stripped surfaces graded to be self draining.
f20f4fe0-865f-531e-a4f3-0a4700707d12 | note | • Spoil from site to be taken to 15-alpha in accordance with CEMP
d94ed560-57d2-56a5-8ffc-f802e7033118 | note | Reference Documents: Work Procedure, CEMP
97e05e36-5e00-5dbe-9ee8-9bb66ae97487 | note | Inspection / Test Method: Visual Inspection
f507f5c2-ff06-5852-ac19-b4534b9fe3c5 | note | Record of conformity: This ITP signed
4d5f313b-4091-5ecb-86bf-0efd9d212ab5 | note | IP
f9ee4709-0b47-58f8-b01f-3a8be41460ea | note | Responsibility: Site Engineer
5515fcd0-8e6d-5a08-a1db-f35691e0a00f | date | Date Completed:
| checkpoint | 2.3 - Protection of Works
29843573-7a90-5e7c-9b15-ef5792e0f692 | note | Frequency: Each Lot
df28280f-fa16-50dc-8817-bfc654ca5437 | note | Acceptance Criteria: Temporary earth drains shall be constructed where necessary to prevent water flowing onto the construction works and to take away water from the works. These drains shall discharge into a permanent outfall. Pumps shall be provided where necessary to dewater excavations.
6c855eb6-94cd-56e4-9e28-44638e82b48a | note | Reference Documents: C.2.7
1c6d4f7f-9dcf-576d-aed4-76d69951a4db | note | Inspection / Test Method: Visual Inspection
3ea845ba-da52-5bcf-9ea5-7be7d604acef | note | Record of conformity: This ITP signed
d97ad8b1-c46f-58f7-a04b-f08fe2678473 | note | IP
e0f6094a-811f-5d4f-90e6-4d43109ef4b1 | note | Responsibility: Site Engineer
5a4710ec-3357-5454-a5c5-e5aff38a2f50 | date | Date Completed:
| checkpoint | 2.4 - Unsuitable Material
47ae15c4-7f2d-5e18-8379-4775258b96fe | note | Frequency: Each Lot containing unsuitable material
d486f079-9b24-5ce8-9874-6328c6482684 | note | Acceptance Criteria: Subgrade to be free of soft spots; if localised soft patches are encountered an additional 150mm of excavation, replaced with subbase material shall be undertaken with survey records showing extents.
73d45e68-5733-5297-b6f8-2f89b712254c | note | • If multiple soft patches identified, contact Superintendent for assessment prior to undertaking further measures.
9d725849-13d2-5575-b75d-de92ae055c79 | note | • Should subgrades become saturated any unsuitable material is to be removed and made good with type B general fill and/or lime/cement stabilized as required in order to maintain subgrades.
d4b06c43-1816-555a-87d9-b11e978cc00b | note | Reference Documents: C.9.2 EW-CE-DRW-007-001
a6b3f766-132a-51b9-995f-8b9092dfb4d6 | note | Inspection / Test Method: Verify
0eff0246-f9ac-5f22-befc-94188a23dc8b | note | Record of conformity: This ITP Signed
d5762bbd-2319-583a-b3f6-9a7d755f832d | note | HP
ed904389-a493-595e-bd51-a437586c4028 | note | Responsibility: Site Engineer / QAV
9ecc5999-c325-5aba-825e-f32b76898d92 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.5 - Subgrade Material
0cdca440-cc9d-5c76-9c73-69109faccb68 | note | Frequency: Each Lot
ba4d507f-b661-57e5-be60-23e80f5997bc | note | Acceptance Criteria: The subgrade shall consist of a uniform type material, free of soft patches, oversize particles, topsoil, deleterious and/or perishable matter. Where the in-situ material varies then the Construction project manager shall direct any over excavation and replacement with approved material, either from site or off site to achieve a stable subgrade.
1421df49-0232-5fb9-b28e-de5305ec528a | note | • The sand filling over the site is considered a suitable subgrade for new pavements and only minimal proof rolling will be require preparation for pavement construction.
04cf0bbd-4c0b-5e55-b0a0-ed0c134fb8dd | note | • Note that sands will dilate if over compacted and minimal passed with a smooth drum vibratory roller are only required. Large rollers (>6 tonne) should be avoided to proof roll the sand and sand filling.
a1f0a703-efba-5966-ac97-843caa1f8cd5 | note | Reference Documents: C.9.2, C.3.2, C.3.3, C.3.4, 4.2 of 7345B
07517649-cba3-5c88-8d78-a6abb09c4602 | note | Inspection / Test Method: Verify
107e5d86-f6f8-56e8-9ba1-b76123dbd703 | note | Record of conformity: Test Report
612e492e-09a5-52e3-999a-33a0abfe94ea | note | TP
ea179bad-d02b-5b28-a12b-92d45d9be69c | note | Responsibility: Site Engineer
f3bd84c3-32aa-5eb3-9d7d-ece03265841e | date | Date Completed:
| checkpoint | 2.6 - Placing of Fill
ecbf44ca-dd74-5d10-8581-5ae3f2fd7100 | note | Frequency: Each Layer
b62fb685-68de-5443-9201-cf3494488ceb | note | Acceptance Criteria: Fill to be placed in uniform horizontal layers of 200mm maximum depth and compacted in accordance with the requirements of AS 3798.
6d00f8f0-6489-58b3-a9a0-29f010714fc4 | note | • All finished surfaces shall achieve a minimum compaction of 98% standard dry density.
207ecbc1-31ef-53cb-aca3-15879f0f07b7 | note | • Type A material shall comply with the requirements of Table 1 in C3.2
3493c0dd-4e06-5219-b33c-afb8fde5dae1 | note | • Type B material shall be in accordance with section C.3.3
70e368c6-fa08-5e32-b5d2-d42724ead00f | note | • Type C material shall be in accordance with section C.3.4
a6937db2-95bf-514d-9cee-69b12262ccb4 | note | Reference Documents: EW-CE-DRW-007-001, C.3.2, C.3.3, C.3.4
48e51951-5ad6-592d-a31d-cac80fe37adc | note | Inspection / Test Method: Visual Inspection / Measure
c77cb8cd-085d-5d6b-82b8-3f71e3dc80b5 | note | Record of conformity: This ITP signed
7677fc8a-4917-51e2-a92a-afffd82b07ce | note | IP
599fa68c-ce61-5aea-9353-7e2c1c4b9598 | note | Responsibility: Site Engineer
52170da9-fcd2-5647-acc5-b504523d365a | date | Date Completed:
| section | 3 - Testing and Surface Preparation
| checkpoint | 3.1 - Test Rolling
38fe66c5-a365-5625-9c69-ddb596598857 | note | Frequency: Each layer
a8134dee-e9f3-53c3-8030-ea60742b8dd8 | note | Acceptance Criteria: Test Rolling shall be undertaken in accordance with section C.3.8c and the Contractor shall advise the Superintendant when the proof compaction is due to be carried out, giving a minimum of 48 hours’ notice.
dba82d60-9c40-51d5-9ac1-a1ee817b527d | note | • The frequency of the test rolls shall be in accordance with table 5 in section C.7.2 of the project specification for the relevant pavement layer.
7823000a-eed6-59fb-83b6-121f89372747 | note | Reference Documents: C.3.8c, C.7.2
7bc9466a-6985-5eeb-96e1-d4ca5a480990 | note | Inspection / Test Method: Visual Inspection
410cd629-83c8-5fb6-9293-c1045de4e018 | note | Record of conformity: This ITP signed
6f665fc7-39b4-5854-9af6-f8234ad93085 | note | HP*
440b7703-407b-5934-a7e3-d7d44c0dbd7d | note | Responsibility: Site Engineer / QAV
2ea3970f-126b-5fc7-ae37-8c8c52fb8632 | date | Date Completed:
| checkpoint | 3.2 - Cut and Fill Tolerances
b4db88de-9d01-5c5f-9ff0-32cf4b146738 | note | Frequency: Each Lot
4bff4cfc-b8df-5993-b25e-d2e22fb61058 | note | Acceptance Criteria: The design surface levels are the levels on the completed earthworks including respread topsoil where applicable.
e84e8e37-bcb5-5985-8701-1a5443b5c060 | note | • The completed earthworks levels shall be –
242eea70-eda5-5a6e-9391-1ca2e072350e | note | a. within + 100mm to - 0mm of the design levels where there are no retaining walls; or
184fac46-86fb-5cd6-ad90-7bcc8375cef5 | note | b. within + 50mm to - 0mm of the design levels where retaining walls exist, are proposed, or will exist in the future.
c3092323-6def-5742-bcb0-5c512d0d69f4 | note | • Where material layer thicknesses are specified they shall be –
242c5769-63e2-5776-822a-1f89e214eb30 | note | a. within + 100mm to - 0mm of the design thickness for Type A1 – Structural Fill (Sand), Type A2 – Structural Fill (Gravelly Sand) and any other material described as ‘sand’ or ‘structural fill’; or
5b73f172-382d-5519-8715-a97934c5aae3 | note | b. within ± 50mm of the design thickness for all other material types.
c0b0bcad-478f-5278-aa8a-13b47944a16e | note | Reference Documents: C.3.13
8237b385-26cb-5fc8-b5c2-6e01f839ece0 | note | Inspection / Test Method: Verify
e7aa02ec-1f81-546d-877d-3af92f642aff | note | Record of conformity: This ITP signed
2e6ff8ad-14b0-5eea-b64d-27b85c7d0a74 | note | SCP
7803e90e-33fe-50bc-94a1-55fd212827d0 | note | Responsibility: Site Engineer
4c214dd0-1010-5b4f-969a-a6a05ef42c53 | date | Date Completed:
| checkpoint | 3.3 - Subgrade level conformity
3317ebf9-cefa-5d7f-9225-359144877b7e | note | Frequency: Each Lot
0548c9cc-88e1-554b-8098-d97f5f0c5842 | note | Acceptance Criteria: Finished subgrade level tolerances to be + 5mm or - 30mm ( +0mm )
54f6cf2d-d0e0-579b-acce-52069b2dfbe9 | note | Reference Documents: C.7.4
b44d117a-9934-5139-bf8d-b8ff6f0148c3 | note | Inspection / Test Method: Verify
40095d68-8974-5eba-9fa1-d2d78add7428 | note | Record of conformity: This ITP signed, Survey report
c05a09aa-d417-590e-a8c2-0daf00fe7774 | note | SCP
7937a92c-f105-594e-ad1a-76b09367f7d1 | note | Responsibility: Site Engineer
4095b6d9-c51d-55de-80df-942b922fa99b | date | Date Completed:
| checkpoint | 3.4 - Fill Material Compaction & Moisture Content Requirements
8a98538a-c85d-5d49-8283-586195fcc937 | note | Frequency: Each Lot
f84b1433-e624-508b-a4e2-636d1ecccf6c | note | Acceptance Criteria: Sub-grade shall be compacted to not less than 100% of the standard maximum dry density to a minimum depth below the surface of 300mm. The moisture content of subgrade is to be +/- 2% of Standard Optimum Moisture Content (OMC). Sub-grade to be formed to grade, crossfall etc. to ensure that an even thickness of pavement can be finally achieved.
aa651028-2dbc-5985-bd4a-59a8f712301b | note | • No further stage of construction to be commenced until the completed sub-grade has been inspected and approved by the Superintendant and the Local Authority.
30868bce-3995-5b99-bcad-150316d4ce85 | note | Reference Documents: C.9.3
26e90d24-44e1-5e7a-8d2f-dbb15edc8142 | note | Inspection / Test Method: Verify
b7499868-ca46-5e95-ac34-755ecf4177ee | note | Record of conformity: This ITP signed
e6fba524-2b9f-599e-b872-14920276fd01 | note | HP
f873c024-b288-56fb-9f49-1405440dbaed | note | Responsibility: Site Engineer
6b207a5d-90ba-5e0e-bbf0-c52da94af63a | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.5 - CBR Testing of Subgrade
29a388cb-b98a-5982-82cb-ca26558e807b | note | Frequency: Each lot
228937c9-715f-5ef1-9b3f-447ce2674e68 | note | Acceptance Criteria: Contractor shall test subgrade for minimum California Bearing Ratio (CBR) at frequency nominated in Table 5 to ensure the site CBR conforms to design pavement assumption. The minimum site CBR is to be 5%, unless noted otherwise.
1c8d5274-f171-57d4-addb-5fb231329bc0 | note | Reference Documents: C.9.2
208d6a71-5ff1-5da1-9024-ec4fb5487904 | note | Inspection / Test Method: Test Point
a9872cad-fff7-590e-b59f-581e22e3cd85 | note | Record of conformity: This ITP signed
b2827fdd-77b8-52bd-ba03-c8dd3f172f83 | note | HP
0b359fd9-c0ed-520e-a29e-6c806c4e873c | note | Responsibility: Site Engineer
7eeb6b52-8272-5cfd-bae3-070be925b15a | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | Final Inspection
6854f9a3-6f35-52f7-b061-e423bfef5637 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
e5551857-a6b5-591c-92e0-8528bd121987 | textbox | Print Name:
5497683b-28f6-5455-8f52-0d9d9cdccbe9 | textbox | Position:
6cfc5d4e-dbcc-5606-bcb3-0606f9f8c04b | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-012 - Concrete Structural Footings | itp | GT4-ITP-012 - Concrete Structural Footings | 17bf970a-fe1d-4816-ae05-7bd0e333549a
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check that current revision drawings are being used
e042817f-bc38-5ab8-8b4d-8aba0b78b231 | note | Frequency: Prior to Commencing Work
63c7fe16-f3fa-56e3-9010-e04e2e423608 | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
3a7eeb36-5a58-5757-85e1-7398959ac79c | note | Reference Documents: IFC Project Drawings/ Drawing Register
dc73a212-8e06-54e9-a98b-756a6fb779e7 | note | Inspection / Test Method: Document review
74e851b0-1d05-56ac-9174-3bc98da1686a | note | Record of conformity: Latest revision IFC drawings, ITP signed
e29df691-d154-5405-8fef-469060371256 | note | HP*
cf200e6f-548d-598a-9ca5-d1736a6d14e6 | note | Responsibility: Site Engineer
150ab7fa-d148-5a28-93e9-4668c90ee3f2 | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
3b10cc5b-bb0c-5fe6-a042-16cc53f77361 | note | Frequency: Prior to commencing any activity
05cb82e7-65f1-513a-b87d-5502eb352894 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
760eea08-bf03-544c-9701-7cb9138d05c1 | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
c59ec24d-86fa-5f2b-93d3-cc38195dac81 | note | Inspection / Test Method: Visual Inspection
2d97d6a6-c2a5-5517-8d5f-e9bc68dac3a9 | note | Record of conformity: This ITP Signed
d682bc9a-3f5a-5488-b5b8-760accc22144 | note | HP*
d73d18f3-9c1b-515e-9f80-cb7be7ab35a8 | note | Responsibility: Site Engineer
7bb33ce9-1ea1-5033-9cbf-5185a4b269ad | date | Date Completed:
| section | 2 - Material Conformance
| checkpoint | 2.1 - Materials & source Approval - Reinforcing
829383c6-d207-5eaa-8fd6-24379019fb96 | note | Frequency: Prior to works commencing 1 per delivery
12438b6f-aa2d-5502-8781-3a8125e438e0 | note | Acceptance Criteria: Reinforcing supply quantities in accordance with the drawings and AS/NZS 4671.
7aec7f90-31fa-51cc-a7f9-24d8eea61047 | note | Reference Documents: Work Procedure
db8b695b-cbc3-5f83-afee-e48da51de39f | note | Inspection / Test Method: Visual Inspection
88e912f4-f26c-5381-8caa-b85e7153e442 | note | Record of conformity: Receival inspection checklist
faed6a4e-b566-577a-bd1d-b8b8a2433e7c | note | IP
9b60e8c6-9b03-5a1f-a20b-4b2f5a12d672 | note | Responsibility: Site Engineer
befdfc04-5757-5ad4-a6b3-e32fb50a0d94 | date | Date Completed:
| checkpoint | 2.2 - Materials & source Approval - Cast-in Items
52c51619-2bf3-5252-bc7e-14c5af0ca091 | note | Frequency: Prior to works commencing 1 per delivery
f5202fbc-78be-59bd-83aa-6c2c2c0d7b62 | note | Acceptance Criteria: Cast-In items to be in accordance with the drawings and manufacturer specifications. All surface exposed, cast-in components are to be hot dip galvanised and fire protected as required.
dfeec2a0-c395-5bd9-a4a6-0d305f1293a4 | note | Reference Documents: EW-ST-DRW-10- 0005
b04ac50c-c760-54b8-9e86-2464e5dc9672 | note | Inspection / Test Method: Visual Inspection
322fe641-8e40-5137-ba50-c7af441cf756 | note | Record of conformity: Receival inspection checklist
3648e10e-3728-57cb-bff4-319a35053ce4 | note | IP
d2b7bc71-64c6-500d-97f2-6fa43d080161 | note | Responsibility: Site Engineer
ad83dee3-675b-5b7e-baea-624dfc9842d6 | date | Date Completed:
| checkpoint | 2.3 - Source In-situ Concrete Material
63002da3-803e-5f62-a180-369f83613d0f | note | Frequency: Each Lot
bfe5a6ff-b111-5e02-af56-e368c2b06eff | note | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation. Concrete slump shall be 100mm +/- 20mm
018d68ad-50ad-5c06-af02-88e01f663e49 | note | Reference Documents: EW-ST-DRW-10- 0005 Table 5.1 of AS1379
8a1d1914-018d-5bb3-aafd-07f446170005 | note | Inspection / Test Method: Verify
7128182c-8792-5ac3-b417-7a3361d1b462 | note | Record of conformity: Mix Design
8ed36877-9110-52cd-8e67-0b11573927a3 | note | IP
36f5fb7d-c078-5ef6-af1d-938752e66864 | note | Responsibility: Site Engineer
fb8e6a2a-b9a8-5bfa-9b62-ab45239fa550 | date | Date Completed:
| section | 3 - Construction \ Erection of Formwork
| checkpoint | 3.1 - Set Out
5cfc0a60-66cf-5f88-9f34-123705cb2168 | note | Frequency: Each Lot
aca1a1a9-03b8-58c0-804a-67f8f1e487aa | note | Acceptance Criteria: Provide 24 hr inspection notice for Superintendent confirmation of footings location.
62e67905-baba-55c7-a778-0e6630dfebca | note | Reference Documents: EW-ST-DRW-10- 0005
f7e7b934-922b-5a33-bb5e-6715b69605a3 | note | Inspection / Test Method: Verify
f676945a-c920-585c-8644-629ec4dc985e | note | Record of conformity: This ITP signed
449ae06d-9c91-55d0-93e5-30ce8af28de1 | note | HP
9d4e0a16-57a5-5cb1-a349-3d417fcbcdad | note | Responsibility: Site Engineer
99744db3-8f0f-5c02-9d95-d5c030c6a7e1 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.2 - Excavation
0cb23bc3-dca2-5ffc-9119-30e42b7e5b70 | note | Frequency: Each Lot
fcf98c0e-2d1f-5e34-b5cb-a6d4312b36c3 | note | Acceptance Criteria: Excavation to be to the depth and size required for the concrete footing.
c928ace1-efe2-503c-a923-6feb7f45d9c8 | note | Reference Documents: EW-ST-DRW-10- 0020
27182cba-bc57-58e4-b83f-3b468d04ba1a | note | Inspection / Test Method: Verify
b898e0c7-eab3-51fc-953e-6904e4cb4caf | note | Record of conformity: This ITP signed
945ebad8-7059-5777-88de-0734eb47326a | note | IP
dccc1f34-5f79-589c-a416-bb71688425c8 | note | Responsibility: Site Engineer
dab1644c-7306-5365-8d2b-a73403b6f5d0 | date | Date Completed:
| checkpoint | 3.3 - Blinding Concrete
a2a18cc8-44f4-5681-90b9-a090ff7bdfc2 | note | Frequency: Each Lot
ed62ebc5-05b5-5e25-8000-93eb5440b63a | note | Acceptance Criteria: Min. 200mm of concrete blinding layer below the base of the pad footing.
b8b17833-f993-55fa-a355-770b2a0d2d4f | note | ○ Where a footing does not extend to the level required within the acceptable founding material, the contractor is to provide a weak-mix blinding concrete (minimum N15) for the footprint of the footing to achieve the required depth
b5946aef-bd8c-5610-9c02-bb6496516055 | note | Reference Documents: EW-ST-DRW-10- 0020, EW-ST-DRW-10- 0005
698672ce-c177-596c-b8b8-b1f7593036e8 | note | Inspection / Test Method: Inspection
365671fb-bab6-5952-a4cb-ba1a28dd2cef | note | Record of conformity: This ITP signed
e5daa3ae-a702-5454-a5d6-453dd1206813 | note | IP
a493a29d-b0d8-5a60-b963-879012f7bd72 | note | Responsibility: Site Engineer
a3189298-0dd0-57c7-9cd0-7dbe7b34f6ce | date | Date Completed:
| checkpoint | 3.4 - Formwork
dd9b026e-bd78-5fb5-aad8-91a41644ab16 | note | Frequency: Each Lot
b98fb8d3-cd93-599f-9680-faa46c20ed66 | note | Acceptance Criteria: Formwork shall conform to shapes, lines, levels and dimensions of the concrete shown or indicated on the Drawings.
5a63456e-bd83-5f30-9f39-3166ee1863ca | note | Reference Documents: Work Procedure
cce791c0-5a8e-591a-b2a6-517668553815 | note | Inspection / Test Method: Verify
c7da5815-0514-5a79-b4b1-850a6ad8f528 | note | Record of conformity: This ITP signed
adfb99c1-ff6e-528d-b16c-c8e4fcaa14cc | note | IP
6c8ebaff-45a1-52e1-a8a5-0b7a62587359 | note | Responsibility: Site Engineer
303593b2-7b7f-5fdb-89dd-cfa7977dbd34 | date | Date Completed:
| section | 4 - Reinforcement
| checkpoint | 4.1 - Steel Fixing
d19b2f0e-6009-547a-bfea-410815efdebd | note | Frequency: Each Lot
c356ab9c-c365-550f-b92e-de2802d11ede | note | Acceptance Criteria: Reinforcement type and design to be in accordance with DWG EW-ST-DRW-10-0020.
9d50ec59-f0e4-56d2-bed2-43f13302a235 | note | ○ Reinforcing steel shall be bent and placed in accordance with AS 4671 and sufficient bar chairs shall be installed to ensure reinforcement is in the correct position.
34397f99-67da-5082-baf2-ff3918ad23d9 | note | Reference Documents: EW-ST-DRW-10- 0020 Work Procedure
863c0d38-ff96-50c2-b78d-773724803af5 | note | Inspection / Test Method: Verify
eff42568-57a6-5245-b3ec-730d7435171f | note | Record of conformity: This ITP signed
96e83f75-cda0-5467-a731-7b69df8d7047 | note | IP
a2deb96f-3a8e-59d0-ab4a-0e5678589dd8 | note | Responsibility: Site Engineer
f5ad3420-0a5e-5c36-a4c2-dea640594326 | date | Date Completed:
| checkpoint | 4.2 - Reinforcement Installation
1ef1b536-744d-5a03-9285-55f7a57fb029 | note | Frequency: Each Lot
7d9b19d6-df0e-5a4f-b19a-00c9ef983879 | note | Acceptance Criteria: Pre-pour Checklist Completed:
f80ebc3c-33f2-59c2-9d07-78ba9e8f06e6 | note | – Position and spacing check and recorded
09358062-8cba-50bc-b6aa-86b7f0f02033 | note | – Cover checked and recorded
bc889888-82e6-5ee3-8589-24624d8e0e46 | note | – Reinforcing supports checked and recorded
7993d713-06d1-5260-b86d-ecc9be443262 | note | – Laps at required length
76a2d624-60ab-5d69-9862-ecbde6e6b53f | note | Reference Documents: Work Procedure
bb81ee58-e2e9-5eb1-b292-4d6b465e050b | note | Inspection / Test Method: Inspection
b67afd47-bf9a-579d-a621-a6e01e59a865 | note | Record of conformity: This ITP signed
636b442e-c476-5730-b36c-90bb40a00f88 | note | IP
0cbe2900-f02a-5463-94d6-db4b3286f259 | note | Responsibility: Site Engineer
4a8209ff-7a71-5913-a12e-bc610e76f5ad | date | Date Completed:
| checkpoint | 4.3 - Cast-In Items
4d4b417e-637d-538a-83f2-211b5b996489 | note | Frequency: Each Lot
8b9f52b8-ebda-52fb-84e4-7a351e965ab3 | note | Acceptance Criteria: Installation of cast in items as per manufacturer specifications
b91002f4-866f-5ce8-92ae-3dd79fb77975 | note | Reference Documents: Work Procedure
ae9eb896-c340-5ea7-81dc-3f3eb54f5d87 | note | Inspection / Test Method: Verify
5f6edbc5-1513-5dd9-9d20-7473ae853f9b | note | Record of conformity: This ITP signed
6b9c2eec-d199-5a60-9441-571f788b6fad | note | IP
31187ace-7958-5a58-908b-93c588af04ce | note | Responsibility: Site Engineer
e0623d9c-47a2-5b46-aece-db0814dba3bd | date | Date Completed:
| section | 5 - Inspections
| checkpoint | 5.1 - Pre-pour Inspection
fe0b865d-5924-5c08-a2ea-361da9175d33 | note | Frequency: Each Lot
e743ea08-1ca2-5318-acd8-e59585724747 | note | Acceptance Criteria: Concrete shall not be placed until:
7d6ecb2d-abeb-578c-9b6c-f0252ef52438 | note | (i) the evidence that the forms, reinforcement, any stressing materials and embedments conforming to the requirements of the specification and the drawings, has been reviewed by the Superintendent
94558cd8-caf8-5d83-b1dd-9045ce733678 | note | (ii) all foreign material has been completely removed from the forms
8af1ed20-3b31-5b15-b078-9fea3bd42bb0 | note | – Superintendent requires 48 HR notice for inspection.
332cf48b-57d0-5896-b265-24d4e3c36a42 | note | Reference Documents: Work Procedure
c46d07e8-8a49-5f49-983e-cc3102464afe | note | Inspection / Test Method: Inspection
583bf6ae-2773-50d2-9d94-148caf432965 | note | Record of conformity: Pre Pour Inspection Checklist Completed
02bf06e5-fcd4-54da-9c8b-420482a9d65c | note | HP
73b2313b-ccb4-5065-8eeb-1259557ba651 | note | Responsibility: Site Engineer/Superintendant
5a3287c2-22bc-5d68-ba30-85c20d83d176 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 6 - Placing and Finishing Concrete
| checkpoint | 6.1 - Pour Concrete Footings
f7dbcb2c-1e75-5d64-ae5a-20a00b444d10 | note | Frequency: Each Lot
c7dc7b36-9b68-50ed-991c-d6003dd8ff7f | note | Acceptance Criteria: Footings shall be constructed in accordance with the detail shown on the drawings.
1c7f35e4-27d6-5238-accd-d3001c8b07e0 | note | Reference Documents: EW-ST-DRW-10- 0020
4b29888a-4235-5131-8f31-c907c290540e | note | Inspection / Test Method: Inspection
3e8f7362-1d6f-590e-9664-294cd51e8bb3 | note | Record of conformity: Concrete pour record and delivery docket
35d08bf8-6129-5dbe-b253-537d9e136fd2 | note | HP*
41111358-69fd-5fee-abd9-879e232030b3 | note | Responsibility: Site Engineer
30a2607d-7260-5f22-b37d-fd4af80baa00 | date | Date Completed:
| checkpoint | 6.2 - Finishing
c7de75f5-5f67-564c-93c2-d34214b0074a | note | Frequency: Each Lot
882f4930-d402-5060-8b6c-67073edd45a3 | note | Acceptance Criteria: Concrete to be vibrated to ensure compaction and air voids removed. Screed finish required on exposed surfaces. Concrete surface finishes to meet Class 4 requirements as per table 3.2.3 and 3.3.5.1 of AS 3610. (Attached Below)
f6728ca9-fe3c-5362-bdf4-39702c7b1ded | note | Reference Documents: Work Procedure
45e20c05-d943-53f3-8804-e180d7e67d7e | note | Inspection / Test Method: Verify
54d0f955-f0ab-5a12-bf6e-ea65834f5380 | note | Record of conformity: Completion of prepour inspection checklist
bac20014-3ce4-5e6c-88b6-a9a8d360272c | note | IP
02d48317-e4a5-56fe-ab67-82654ae23db6 | note | Responsibility: Site Engineer
a35c1b9e-c7b0-56f5-a93a-1c538425faff | date | Date Completed:
| checkpoint | 6.3 - Concrete Testing
b5ef7e95-ff44-50ad-8046-2f190ee5dde3 | note | Frequency: Each Lot
ddddae33-4866-5dfd-910f-60d011939daf | note | Acceptance Criteria: Testing for conventionally reinforced elements: UNO in specifications or on drawings, the contractor is to arrange for project sampling for every 50m³ of concrete supplied (1000m³ in the case of shrinkage tests alone).
85b42144-0090-55c4-98ac-25838d64231b | note | ○ Provide slump, 7- and 28-day compressive strength and shrinkage test results in accordance with AS 1379 and AS 1012.1 to the engineer, as a minimum.
a44acbfc-aaaa-585e-b144-2257095b0ae2 | note | ○ Concrete Testing to be carried out as per specifications in AS 1379
658e8331-2229-56fc-8d39-3e74fb3bb448 | note | Reference Documents: Work Procedure
e7370a4e-ea1d-5ade-bc8b-5f431dbd16c8 | note | Inspection / Test Method: Verify
4a81a058-bc78-5b16-b558-144b09845c6d | note | Record of conformity: Test Results
49649fed-89ec-5d42-b378-f670b59e5a65 | note | TP
d2da3098-36ce-5a81-a6fd-be856962c564 | note | Responsibility: Site Engineer
dc1bf875-6819-5eaf-b5b8-372d2543cf15 | date | Date Completed:
| section | 7 - Post Pour Details and Inspections
| checkpoint | 7.1 - Concrete Curing
aaee08da-ef17-59b8-8e24-0d38420f416e | note | Frequency: Each Lot
49fd1c16-5fc5-56f4-a990-1ab245eeb1cd | note | Acceptance Criteria: Concrete to be cured as per project specifications.
c7f42e8f-8dff-5f85-ac97-5f08675919cb | note | ○ All concrete elements are to be actively cured for a minimum of 14 days following pouring by ponding or an approved proprietary system. The contractor shall submit the proposed curing methodology to the engineer for approval prior to pouring.
65ce64b6-a500-546c-aa08-672e929e1906 | note | Reference Documents: EW-ST-DRW-10- 0005
e326c3d5-8124-5068-af9a-50e1a17436aa | note | Inspection / Test Method: Verify
5eb9c8ac-214e-5152-b9dd-5a2307de2a10 | note | Record of conformity: This ITP Signed
030ca864-6457-5720-9716-a4f19e00b096 | note | IP
beb3fc06-ead0-56e3-9e5a-5b98b1e9b275 | note | Responsibility: Site Engineer
ba09da84-32d4-5927-a1b7-9e766d14d542 | date | Date Completed:
| checkpoint | 7.2 - Removal of Formwork
eaee8a3b-ae18-5e2d-b979-d4c57f08eb64 | note | Frequency: Each Lot
0bfc57c7-ff3b-58bb-a368-502a24278cf2 | note | Acceptance Criteria: Stripping of vertical faces in accordance with C.1.8.13 of EW-ST-SPC-000001.
044af23f-d2e3-5041-963f-c7484f8cec57 | note | Reference Documents: EW-ST-SPC- 000001
2a13e1dc-2cc0-57d2-970b-e0de6533b44f | note | Inspection / Test Method: Verify
4da95a6f-d837-539a-aadd-c272afd5c592 | note | Record of conformity: This ITP Signed
53f32647-eb8b-5ded-ac76-46486eb8fa7a | note | IP
723bd709-d974-5cac-9d8d-2581609f941f | note | Responsibility: Site Engineer
0777bf64-2121-589e-9ab6-a40914bcd9d6 | date | Date Completed:
| checkpoint | 7.3 - Allowable Tolerances Level & Alignment
382f61d5-9b90-5f7b-98ab-0e28c1e6f529 | note | Frequency: Each Lot
bfb3eef7-4d5b-50e6-b013-02ca4ae3a939 | note | Acceptance Criteria: Surface Tolerances to be in accordance with Table 3.3.5.1 of AS 3610 As-built survey completed for lot
0d548b08-44e2-5b11-bdbf-962e92863bc9 | note | Reference Documents: AS 3610
d5b2da16-46cb-5f4e-82a6-909fbcd40eca | note | Inspection / Test Method: Verify
68d0fd7a-df6e-5c65-a027-039f3a29da40 | note | Record of conformity: This ITP Signed
7e738aa3-d262-5f89-ab2e-eae77cac3da8 | note | SCP
1bdeb4a8-435d-5a0a-8170-6aa3db75b899 | note | Responsibility: Site Engineer
84c56df4-249a-5d8a-bb16-58b8dfdba2a7 | date | Date Completed:
| checkpoint | 7.4 - Post-pour Checklist
2cecf2cd-2bd2-5d54-9752-0a773d2498f6 | note | Frequency: Each Lot
1359cbde-7b3f-55fd-937b-5abdfadafe22 | note | Acceptance Criteria: Completion of Pre Pour checklist quality checks.
ee53ea08-7acf-5339-b245-fe3d23b39137 | note | Reference Documents: Work Procedure
5555985e-c494-5d57-9456-2fdc229a72b5 | note | Inspection / Test Method: Inspection
f8459f38-5b84-53bd-97f5-987e2e2d22b3 | note | Record of conformity: Pre Pour Inspection Checklist Completed
2d74a70f-1ae7-54e9-9844-55ab7b4e533d | note | HP*
bc69b4d7-e1d1-53cc-b22e-6cc8b7816b61 | note | Responsibility: Site Engineer
ea5cc9f4-18cb-5c9b-a262-47984fd7b206 | date | Date Completed:
| checkpoint | 7.5 - Backfilling
c7a7316b-3f41-58a6-8d02-630cd07d945d | note | Frequency: Each Lot
6b3d52d1-6129-51b1-bdec-31f51eb7484d | note | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
0b38b463-25ab-5153-acb4-db905e214274 | note | Reference Documents: Work Procedure
0d2f127b-5eb7-5d0e-85dd-ce473fff9db4 | note | Inspection / Test Method: Inspection
fbcaf8c6-d493-54f3-a26a-d9d2e772211e | note | Record of conformity: This ITP Signed
57813096-0712-579a-af04-4281f142f367 | note | HP*
210ea275-5632-5cd9-a206-bde4f0c3a5cf | note | Responsibility: Site Engineer
d858f164-83f9-50ed-a452-c007f5ed5ad5 | date | Date Completed:
| checkpoint | Final Inspection
3481137f-75f6-5842-8f94-0271f06f114c | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
7821dbf9-a69a-5617-9f5a-80c598b19a9c | textbox | Print Name:
7f1d58ea-6186-5b89-a180-a0b72f8bdc83 | textbox | Position:
c8a49a26-8134-5e69-9a8a-c6925a9efe9d | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-013 - Precast Installation | itp | GT4-ITP-013 - Precast Installation | ba7014f6-72dd-4544-8a5f-f69aeb6eb8af
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check that current revision drawings are being used
753fafc5-2890-57d0-a449-ffe0d39f692d | note | Frequency: Prior to Commencing Work
50636f26-673d-5673-b0d7-4e1d32c63643 | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
7c33f1b4-013e-5ac9-b029-99596aa3c6c6 | note | Reference Documents: IFC Project Drawings/ Drawing Register
c01427ed-7fa3-5426-947c-69945bb8e4a2 | note | Inspection / Test Method: Document review
cea368b4-1c5b-54e9-89ed-db2475be692e | note | Record of conformity: Latest revision IFC drawings, ITP signed
f5d73643-05b4-5446-b65e-bdebb4879a44 | note | HP*
c4f0da0d-da6f-52f2-bca5-1b97c0ab7b48 | note | Responsibility: Site Engineer
204cf5d4-10cb-59e3-8f2e-2bf6490aa9e4 | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
59a7d250-2c36-5e30-adfc-5efb9627b0ab | note | Frequency: Prior to commencing any activity
0265309f-024c-55e3-9251-f1b219d88f65 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
9d80ea24-0a0e-5683-a242-12eea23314eb | note | Reference Documents: OHSMP, EMP, TMS, SWMS, WP
6c372cc1-3ad7-5b71-8db3-3b3cd2c87992 | note | Inspection / Test Method: Visual Inspection
e7c5bfd9-065e-5111-a40e-4340404e2d32 | note | Record of conformity: This ITP Signed
f08ea14c-b56c-5fbe-a5cb-a01508ed445b | note | HP*
ee4ca9af-77b9-51cd-bd55-915c9003377b | note | Responsibility: Site Engineer
acd59700-bded-57c8-b46d-a57c7a54b6ff | date | Date Completed:
| section | 2 - Material Conformance
| checkpoint | 2.1 - Materials & source Approval - In-Situ Pits
d66fbf9b-abfc-5f83-81b1-3d301bcc7990 | note | Frequency: Prior to works commencing, 1 per delivery
e05de1c3-2afb-53e5-816a-d0379167105d | note | Acceptance Criteria: Precast item resources and bedding specified or as shown on the Drawings.
d40a0abb-07ee-52e3-bac7-121b938e0277 | note | Reference Documents: Work Procedure
dd9bb550-efe5-5590-a6d5-6d873a586ef8 | note | Inspection / Test Method: Visual Inspection
99cc8658-a761-5aea-9323-7b722c519881 | note | Record of conformity: Receival inspection checklist
3ae34192-c078-5e41-b522-dfebcc6d5094 | note | IP
e64b5df4-067b-520c-9da4-6bb73c89f1f9 | note | Responsibility: Site Engineer
c9f172e0-afc3-53ad-92e7-c179b84e7bf1 | date | Date Completed:
| checkpoint | 2.2 - Materials & source Approval - Pit Covers
d9391d45-e18a-51c0-a5d1-c947d159b314 | note | Frequency: Prior to works commencing, 1 per delivery
a9011844-9493-5f48-957e-3259a23d0f02 | note | Acceptance Criteria: Pit covers shall be either cast iron, precast concrete covers or gratings as per drawings and shall be constructed and fixed to pits in accordance with relevant Tasmanian Standard Drawings
932e4624-b7d1-596a-82e9-0384bbf52954 | note | Reference Documents: EW-CE-DRW-526-001 - Pit Schedule C.5.16
484dcac6-12ba-5e4c-b4dd-0dd6cdf46023 | note | Inspection / Test Method: Visual Inspection
5e7a1b0a-478a-5a81-bd9c-620c9a84373e | note | Record of conformity: Receival inspection checklist
f538f3ae-f108-5648-892d-a557bce7accf | note | IP
72660bdc-11cd-59d0-bd18-bbbfa85bfd43 | note | Responsibility: Site Engineer
634555fc-fd62-5393-adfc-b63b3df4012b | date | Date Completed:
| checkpoint | 2.3 - Source In-situ Pit Material
d41eb121-e754-54d3-a2cc-4e3760e21753 | note | Frequency: Each Lot
855ba1ef-16b2-5979-9a22-4ebe9287cc30 | note | Acceptance Criteria: Concrete shall be at minimum 28-day strength, F’c of 32 MPa and when placed shall be well rammed to ensure thorough consolidation.
129f4086-1178-5f45-85af-c9a57dfe3edd | note | Reference Documents: C.5.15
7c9cd213-5141-5b2e-90bd-8207a1a835cf | note | Inspection / Test Method: Verify
43c53560-f1cc-55e1-a40e-45d4e0024c7b | note | Record of conformity: Mix Design
946479b3-6795-52a8-98a9-5e967c2ca2bd | note | IP
8c5d7185-859b-5177-8b71-85019abe3af6 | note | Responsibility: Site Engineer
16b87657-78b2-57fd-8ffa-2813cecfe1e6 | date | Date Completed:
| section | 3 - Installation
| checkpoint | 3.1 - Bedding
55edad19-f1d2-5948-9dc1-2f8c99d5db67 | note | Frequency: Each Lot
aca7bda1-ac72-5b4a-8ccb-d263f6e3e8f1 | note | Acceptance Criteria: Foundation and/or bedding as per drawings and specifications
1bfba07b-ef98-52d2-992e-2c1bdd5b23ee | note | Reference Documents: EW-CE-DRW-526-001 C.5.15
b156478b-afeb-5540-b635-16821f4967e8 | note | Inspection / Test Method: Inspection
c7b270b3-105c-55f8-971d-94bf796ea456 | note | Record of conformity: This ITP signed
26c2f9b7-565b-5b69-9e03-0e1b7606fd08 | note | HP*
0a9413ba-6766-5570-b010-735f453ecb8a | note | Responsibility: Site Engineer
0ebe8287-2ed0-5067-97dd-b8391b896506 | date | Date Completed:
| checkpoint | 3.2 - Installation of Precast Element
9d1ccd08-1981-5091-8905-b1f1377f24dd | note | Frequency: Each Lot
b3c3993a-2491-5f31-8992-0ca605306800 | note | Acceptance Criteria: Precast element level and position confirm with the the deisgn drawings and specifications
5e332f20-cefb-5ec4-96c7-43c3bcb10983 | note | Reference Documents: Work Procedure
74ed33ee-4a77-57bf-af99-2414911c644b | note | Inspection / Test Method: Verify
c2c6250d-387d-53b1-9491-9aff4b630c4c | note | Record of conformity: This ITP signed
3756c322-51da-5369-a20c-972027cbc43b | note | IP
019540b5-68da-57e7-af3c-d5147b243152 | note | Responsibility: Site Engineer
84cb347f-6a37-555e-ae80-fbc8161a9684 | date | Date Completed:
| section | 4 - Cast Insitu Lids/Frames
| checkpoint | 4.1 - Formwork
f073acf6-7597-5b68-b840-c437a5b18991 | note | Frequency: Each Lot
bc73d464-bfac-51f5-a5ae-f6174b96b0e6 | note | Acceptance Criteria: Pit lids / surrounds shall be constructed to the detail shown on the drawings
a7efe8b5-053f-51ba-804d-ad892c850dce | note | Reference Documents: EW-CE-DRW-526-001
e1e8b855-0697-5584-b44d-bd0ac69395b4 | note | Inspection / Test Method: Inspection
df11eee0-0d28-5b94-b634-35d32de130ec | note | Record of conformity: Concrete pour record and delivery docket
b8fb0c21-8ed1-5e22-b018-169a634a1bd0 | note | HP*
93447cef-5b63-57bb-a83c-ce250c7c761d | note | Responsibility: Site Engineer
68ebbcd3-c7b9-5189-984f-9eb571641e2a | date | Date Completed:
| checkpoint | 4.2 - Reinforcing
4a2b279f-dd66-575d-9991-cc30c6599053 | note | Frequency: Each Lot
e08f56ce-8efb-5906-a3c6-f7ac9d2ed9e9 | note | Acceptance Criteria: Checks
7c7faa7b-1c10-5d17-a5ea-6c6f78c2535c | note | – Position and spacing check
db8217a3-6eaa-52ab-ab9a-7efa96137aef | note | – Cover checked
7355002b-7bc0-545f-82db-e75688c761d0 | note | – Reinforcing supports checked
22668c53-a3f5-56c9-94ab-3bd639d97940 | note | – Laps at required length
495e0379-4999-5925-a77b-37cfff358a95 | note | Reference Documents: Work Procedure
ef122e87-c3b2-5d00-b919-bb0c8f252470 | note | Inspection / Test Method: Verify
141e00d0-4193-5881-aa63-b07648a8cf43 | note | Record of conformity: Completion of prepour inspection checklist
0994d67c-02dd-5c24-b9d7-de133fdb823c | note | IP
5fb0862e-45f9-59b0-b40c-075eeb97af2b | note | Responsibility: Site Engineer
9e9c22cc-73cd-5ed4-9a97-cb66a5b7933d | date | Date Completed:
| checkpoint | 4.3 - Concrete Pour
e97f2b53-2710-5a4f-adf1-9675722a8fa4 | note | Frequency: Each Lot
625b28af-dd09-5ce7-ab2f-5e132389fbdb | note | Acceptance Criteria: Precast concrete cover or cast iron concrete infill as specified
ca4b47ca-b9c8-558d-95b4-0c258cf35375 | note | Reference Documents: EW-CE-DRW-526-001 AS 3996
aa959aa1-ffd5-58aa-9870-72dab3f35de0 | note | Inspection / Test Method: Verify
9db2c58d-33e3-50a2-b682-7874e7f592cf | note | Record of conformity: This ITP Signed
696f116e-4568-5631-a06a-d90d96ead30e | note | IP
5144279c-531d-54f0-b834-2b621a51ea56 | note | Responsibility: Site Engineer
464c29ae-5159-5b0d-8707-eb190100ad66 | date | Date Completed:
| section | 5 - Post Pour Details and Inspections
| checkpoint | 5.1 - Allowable Tolerances Level & Alignment
fd1e9255-ab08-50c3-9f2c-001ba8a31a68 | note | Frequency: Each Lot
70c461e9-f9f1-5e0b-9aee-be8c196769b3 | note | Acceptance Criteria: The horizontal deviation of any piped or box culverted drain shall not exceed 25mm from the true alignment. There shall be no obvious sharp changes of direction.
f1dbd24f-9f3e-5ec9-ae20-927d09802857 | note | • The maximum deviation from grade shall not exceed + or - 10mm for grades flatter than 1 in 500 and + or - 20mm for grades steeper than 1 in 500.
777866b0-915b-5e3e-b1bf-0e8b63bb5e2c | note | • The grade of any piped, box culverted, or open drain shall not exceed + or - 5% for grades flatter than 1 in 500 and + or - 10% for grades steeper than 1 in 500.
a41ed93c-db2c-56e0-b6ee-b8fc0a204e06 | note | • Invert levels at structures shall not exceed + or - 10mm from the design invert.
e90d4087-3829-5727-8229-95cb70ebf9e4 | note | • As-built survey completed for lot
89ce1372-07d3-51eb-8650-7409aa66233c | note | Reference Documents: Work Procedure
e21f364e-b121-5426-b8ff-09a8877b8100 | note | Inspection / Test Method: Verify
f3bc41d3-d262-5e23-b17a-82e1d092a57d | note | Record of conformity: This ITP Signed
fa99de08-c9ad-5bfe-9ae6-52a833d69ae3 | note | SCP
c659276d-468b-59ed-883f-196cb1b2d030 | note | Responsibility: Site Engineer
586e4ac4-edf1-59bd-b53a-d83c667688c3 | date | Date Completed:
| checkpoint | 5.2 - Backfilling Around Pits
3c6fa6ba-407f-583b-8ae7-8d376870f628 | note | Frequency: Each Lot
d0f3dc6d-e4b7-5226-84e1-5af7be6612c4 | note | Acceptance Criteria: Backfilling to match pavement design and to occur min. 72 hours post concrete pour.
63988e4d-1cb8-5434-97b9-a45d86ce17a4 | note | Reference Documents: Work Procedure
80cd381b-74cb-5385-9894-eaa28d3a058a | note | Inspection / Test Method: Inspection
34129f55-8527-5582-b253-f041d1ac1f28 | note | Record of conformity: This ITP Signed
82947586-0aa3-5552-800f-e4c154e60fb8 | note | HP*
6a49d771-fc66-515b-b026-9a73cb82dc34 | note | Responsibility: Site Engineer
0757f158-078a-502f-9afb-6aaaef932992 | date | Date Completed:
| checkpoint | Final Inspection
af04b244-1f71-5088-8f02-1aee8fb2d4bb | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
27e28587-0ae1-5033-aed9-c49c050ff5f4 | textbox | Print Name:
802b9a3c-b487-5f26-ae7e-6e281cae9de1 | textbox | Position:
fb767570-3e5c-538c-a294-1cea7ea57ca7 | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-014 - Electrical Works | itp | GT4-ITP-014 - Electrical Works | cca7e9be-f7b7-4ee3-8d09-046b4de3e61e
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Define physical bounds of a lot
2013e2f3-bbef-50f2-be67-92f6d2567401 | note | Frequency: Prior to Commencing Work
748d43b6-5e44-500f-a42a-45cf942c27d4 | note | Acceptance Criteria: Maximum lot size = Single run to the location of field equipoment. Multiple cables can be included in the lot
a0e85c32-8b8c-5011-aa9a-405d043fdbb2 | note | Reference Documents: Lot Map
724fe329-fd7e-5c45-ba01-379a6d9333b5 | note | Record of conformity: Lot map
cec3ddc2-ff59-5266-a14a-b7a44023b5f5 | note | HP*
d5b2ea8c-0023-5826-8b14-408741c623a1 | note | Responsibility: Site Engineer
c9476cf8-2ada-5911-8107-927d2262a786 | date | Date Completed:
| checkpoint | 1.2 - Site Access available
7efb809b-d0d0-5064-b301-9a762847ebca | note | Frequency: Prior to Commencing Work
96b9e722-32af-56df-9e5c-39adc33c2772 | note | Acceptance Criteria: Confirm Site access to area with Supervisors. Confirm all safety procedures including car and pedestrian barriers are in place - as required.
9d396dc8-3fa2-5ff5-a532-a7886719b86f | note | Reference Documents: Current safety requirements of the site
2a7f83fb-1046-557d-96c3-2e5c0f982822 | note | Inspection / Test Method: Site inspection
036bc5f7-7ada-5d10-a329-b07f729f9b82 | note | Record of conformity: Photos
65cbc08d-5e26-5710-938a-802bd00e223a | note | HP*
4d41ac6f-81a4-5146-9085-b41654aaed83 | note | Responsibility: Site Engineer
8b7ff225-4ff6-5b25-aa15-8b5cd790bdfc | date | Date Completed:
| checkpoint | 1.3 - Underlying lot(s) conform
d784f2ef-34c8-5ee3-8091-155f8e374d5b | note | Frequency: Prior to Commencing Work
d1eab0ea-c582-5e8a-959a-ed920e618ad4 | note | Acceptance Criteria: Contractor to verify all underlying lots are closed, or lots open but acceptable to proceed with work. Confirm "Service Trenching & Install CTN-ITP-003" has been completed and signed off.
50f4621d-ac83-5dd4-b7d9-a579fce709d6 | note | Reference Documents: "Service Trenching & Install CTN-ITP-003"
cfecc6b9-f13e-51b6-83be-61d0746210b0 | note | Inspection / Test Method: Site inspection
7bf61edb-ec88-5506-b348-0790383f0e73 | note | Record of conformity: Previous related ITP completed and signed off
b96a172b-de70-5e59-91ea-da99120e0a41 | note | HP*
2506b68f-d3c1-5f3d-be8e-2acee88fb7d3 | note | Responsibility: Site Engineer
dad6c3c9-feba-5e6e-820c-d17301551867 | date | Date Completed:
| checkpoint | 1.4 - Ensure current Termination drawing revisions and cable schedules are available
d6c648f4-cf1f-5226-9c71-458dccab805b | note | Frequency: Prior to Commencing Work
961b9140-25eb-5aff-b10a-162074ebf5ce | note | Acceptance Criteria: Identify and use latest drawing revisions.
8d71e1ee-13d4-51f2-8979-1eae12c47e67 | note | Reference Documents: latest relevent drawings
299b8542-ba69-5337-a4d0-eff74573a17a | note | Inspection / Test Method: Document review & Site inspection
7669a0d9-1087-500a-8172-22297ca08686 | note | Record of conformity: List drawings and version
21ccce91-5541-5d76-ace3-01e2ad36f549 | note | HP*
c14f3774-f4f4-5179-90f5-75d1fbf11d2b | note | Responsibility: Site Engineer
5e80bed5-2911-5a6d-a0c1-2ef4e4765238 | date | Date Completed:
| section | 2 - Subcontractor ITP
| checkpoint | 2.1 - Receive completed FLE ITP SS107 - Fence and gate installation
3edbf162-f9ab-5926-99bb-dbcca59d2dfe | note | Frequency: Per ITP
39f8ab71-0c16-5676-9aee-74b626c3c00b | note | Acceptance Criteria: ITP per lot package satisfactorily completed
665ec274-54c1-51e8-8ac1-b249d182d7e8 | note | Reference Documents: Signed and completed ITP
3d8df007-81da-52b9-98da-11119fd6e773 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
735a7ab7-f19b-5c30-8751-cd8868416afe | note | Record of conformity: Signed ITP
2030c765-6366-503f-9abb-371f345ed1c5 | note | HP*
b2a46b22-f6a0-5e9e-b720-b87924bd5dde | note | Responsibility: Site Engineer
52340157-9941-5dac-8309-fd6c03007acf | date | Date Completed:
| checkpoint | 2.2 - Receive completed FLE ITP SS108 - Internal road
393b8d37-2cc9-537f-bbf4-46bcd16bee07 | note | Frequency: Per ITP
6967a878-fd24-5713-be3d-0ab8118ed0f1 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
a215ae1c-03c6-5faa-959f-59dce8f1c2b5 | note | Reference Documents: Signed and completed ITP
68230d56-e1ac-5e78-93d1-0e526eac523a | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
3c85acf4-fcf4-54d0-9fc2-c5b987d6678b | note | Record of conformity: Signed ITP
ce117278-458b-57cf-a68c-44a3437c55cb | note | HP*
94ac1357-8bbf-59cf-bf0d-e14bbe05d8f9 | note | Responsibility: Site Engineer
f184202b-602f-5ebf-9a27-880aecf9ccdd | date | Date Completed:
| checkpoint | 2.3 - Receive completed FLE ITP SS109 - Switchyard Surfacing
c53c41df-3363-58c3-b301-b0855ec9a97a | note | Frequency: Per ITP
d00121a5-54e8-55fb-925b-9274450a6fa3 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
9d1646ee-1741-5a29-8517-01eaacf29c2b | note | Reference Documents: Signed and completed ITP
52f09c96-f4bb-5e39-85e1-0d0a4e2245b2 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
cb79c5fa-e087-5de2-a965-2444de374fdf | note | Record of conformity: Signed ITP
1de0d2ac-da55-51bd-9abb-03a3e6b9dd27 | note | HP*
3b4aabbb-765d-5d97-8515-1850653bcf2b | note | Responsibility: Site Engineer
1b3e998b-7862-531d-82d6-ad6075178eba | date | Date Completed:
| checkpoint | 2.4 - Receive completed FLE ITP SS110 - Stormwater Pipe Installation
b190e8af-088a-55df-ac95-ee677d1b8c99 | note | Frequency: Per ITP
7bd7724f-b0f5-5def-96d8-394363f4c0aa | note | Acceptance Criteria: ITP per lot package satisfactorily completed
b069abf9-4b16-566a-a421-62907ff87e66 | note | Reference Documents: Signed and completed ITP
78ba56f6-127d-563b-9c50-29d11b6657f6 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
2346005f-21a4-50ea-8235-a4e1345a0fc4 | note | Record of conformity: Signed ITP
a152ed43-ffa3-5742-929b-8582d76634bc | note | HP*
7f5ff26a-0d04-5246-b261-544241e28b98 | note | Responsibility: Site Engineer
094c2a3c-81b4-52a3-a5c2-da6bc22caa79 | date | Date Completed:
| checkpoint | 2.5 - Receive completed FLE ITP SS200 - Structural Steel Installation
86c3db10-e271-567f-9375-92f2755f01c8 | note | Frequency: Per ITP
5e89c2b4-9ec5-5a49-b7bd-2fc56e4c66cd | note | Acceptance Criteria: ITP per lot package satisfactorily completed
cb6ed715-bbe6-51aa-96e9-4bc1f221bcd1 | note | Reference Documents: Signed and completed ITP
f724d845-90f0-5350-a574-cc0faebef848 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
3e6bb671-afd4-5171-bb41-5b2c4d899d9c | note | Record of conformity: Signed ITP
54bde4fd-4db5-5af9-8096-7a5c108b2bcc | note | HP*
5b3263a3-4365-59da-bed3-7435cd59d04b | note | Responsibility: Site Engineer
edd9d119-8992-549f-ada5-a437539924f9 | date | Date Completed:
| checkpoint | 2.6 - Receive completed FLE ITP SS301- Substation Earth Grid Inspection Checklist
6ab9cd62-c13d-528c-a432-67ce5542245f | note | Frequency: Per ITP
44c64ae0-4dc8-5a12-9cdf-515eab325928 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
05646d8e-2a19-5782-8e23-3c832f513358 | note | Reference Documents: Signed and completed ITP
a41b1dcc-fbf9-5c84-bfca-fda7622a1440 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
10c9c098-e537-5631-8ca4-4eaae21217ba | note | Record of conformity: Signed ITP
27c99dae-e31d-5c38-87e8-30bb2351a3ca | note | HP*
5c47bbea-ef0c-5e68-ac7a-305659901382 | note | Responsibility: Site Engineer
d1855bcb-de94-5bdb-bbb6-7d7df17bb02b | date | Date Completed:
| checkpoint | 2.7 - Receive completed FLE ITP SS302 - Current and Voltage Transformer Installation Checklist
f31c36b0-67e4-5bc3-adc2-da34d05a0fee | note | Frequency: Per ITP
6d201c41-96de-5148-9466-2eadd990a45b | note | Acceptance Criteria: ITP per lot package satisfactorily completed
4dde1f37-0584-59fc-9ba3-afc182c64379 | note | Reference Documents: Signed and completed ITP
7688600e-71f6-5df6-aa06-3af05e5c8160 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
2ecc9617-888a-573e-81a2-ff844634acaa | note | Record of conformity: Signed ITP
2a67f1b7-dcfa-5148-8d76-0a38ddc70697 | note | HP*
1beb2030-970e-5989-8ff7-15cd856446aa | note | Responsibility: Site Engineer
91c217f3-bf2b-5b82-bf8c-7ceabdb90413 | date | Date Completed:
| checkpoint | 2.8 - Receive completed FLE ITP SS303 - Isolator and Earth Switch Installation Checklist
4328a9e8-9843-5484-b262-3068aafa30df | note | Frequency: Per ITP
b943c5c7-1338-567a-bdbe-3e7d8e8fda2f | note | Acceptance Criteria: ITP per lot package satisfactorily completed
dea7810f-b6bd-5ea8-9878-e305f9f83833 | note | Reference Documents: Signed and completed ITP
c06cab17-75de-5199-9360-9c837b964564 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
71c2a502-1d93-5659-9d89-a4211ccae918 | note | Record of conformity: Signed ITP
da9d64e1-8a47-5e67-8c58-ffa6f3c62a2e | note | HP*
902b46ef-a017-5105-ab3e-4aab69abe5a7 | note | Responsibility: Site Engineer
1b227f69-f2e1-57a9-935b-0cc2f4aea9fd | date | Date Completed:
| checkpoint | 2.9 - Receive completed FLE ITP SS304 - Circuit Breaker Installation Checklist
e4382413-78b6-5051-8ffd-6df6344ebfe7 | note | Frequency: Per ITP
ff25a0d0-2d28-5874-8413-fa3b93a85c74 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
f554dc23-bf63-5c4a-a278-bd164f6dd47e | note | Reference Documents: Signed and completed ITP
ec6bb70c-57f5-59ce-8660-2d41b6d27e41 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
f388f587-e88f-511e-ae10-5f5d3832cbec | note | Record of conformity: Signed ITP
dec847f1-9925-5158-b00c-bf2a18938147 | note | HP*
44b04694-8072-5d6a-beab-62c54367069b | note | Responsibility: Site Engineer
d1101fac-d9bb-52d7-b280-f5983b7dece0 | date | Date Completed:
| checkpoint | 2.10 - Receive completed FLE ITP SS305 - Post Insulator Checklist
e5dd62a0-ef3b-514f-b24e-f8f7bf18fbc4 | note | Frequency: Per ITP
d3122ff2-af1b-5cd8-8544-8bda731fa6d0 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
526632b2-0bb1-5535-a54c-e1c845fb430d | note | Reference Documents: Signed and completed ITP
01d05049-8ee4-5252-a11d-91f3bd26ba76 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
19c2808d-f9da-5b1a-b5b3-bb1c288c1819 | note | Record of conformity: Signed ITP
a73d2557-b7e5-525e-aa30-68d1b4d2938a | note | HP*
2c734f20-5ffb-5aba-acdf-9530ffb89f6e | note | Responsibility: Site Engineer
ffe47701-2e1f-5815-b75a-57d0879ae472 | date | Date Completed:
| checkpoint | 2.11 - Receive completed FLE ITP SS306 - Bus Bar and Clamps Installation Checklist
4f7c4a8e-23ca-5193-963f-a55ec72860b9 | note | Frequency: Per ITP
509db4fc-314b-59f6-8b56-3b7b87d7eb4e | note | Acceptance Criteria: ITP per lot package satisfactorily completed
77ddc562-7716-5250-9726-a36214c961ed | note | Reference Documents: Signed and completed ITP
5747d405-83aa-5536-b2ae-7218b47b4a45 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
aa91afbf-78f2-5009-9f51-f713de9e0c4c | note | Record of conformity: Signed ITP
fa47f8b2-8b8a-5c74-8d63-6157e0eff216 | note | HP*
fa3069fb-4a06-54fa-b7f4-f8bc36e96053 | note | Responsibility: Site Engineer
275a3bde-1296-5ed9-a9d0-b356b145bc68 | date | Date Completed:
| checkpoint | 2.12 - Receive completed FLE ITP SS307 - Control Panel Installation Checklist
12e06f97-1982-544e-a79d-e2986a5d7d66 | note | Frequency: Per ITP
f410e722-2a4f-5c64-aaf3-30f29c0ef1a8 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
faa16c15-e881-532f-984d-1a7d7e4ec2bf | note | Reference Documents: Signed and completed ITP
15aadd74-deb9-5021-9399-343d48bbc063 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
d2df3914-3248-5a16-b509-942b76ce7982 | note | Record of conformity: Signed ITP
b61348a8-dac2-55c5-abf2-6b4f5e1593f4 | note | HP*
faa2f9bb-e87f-5ea2-8fbf-74a64165fff6 | note | Responsibility: Site Engineer
53c937cc-c61e-5393-a1dc-bea1ab3328fc | date | Date Completed:
| checkpoint | 2.13 - Receive completed FLE ITP SS308 - Lighting Mast Installation Checklist
4fc3386d-ac7e-540b-b676-dcafec03f519 | note | Frequency: Per ITP
7949a3e0-bc43-5bea-b13d-4d2193d15788 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
80da7b19-9061-55cc-a850-c21bda9da95e | note | Reference Documents: Signed and completed ITP
220bf728-3eee-5ed0-ac7d-8a1052e6fcf0 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
57fd093f-c09e-5901-a526-336b3f88f54f | note | Record of conformity: Signed ITP
af27e2f2-50e1-5c83-b24b-249d8ed3fabf | note | HP*
fa83c492-0fd2-53a2-a050-a055c71ab848 | note | Responsibility: Site Engineer
137717a2-911b-5fd3-872d-2b7c61897c26 | date | Date Completed:
| checkpoint | 2.14 - Receive completed FLE ITP SS309 - Low Voltage Cable Termination Checklist
34ff7a40-afff-5a59-bfba-9989ead2c3f0 | note | Frequency: Per ITP
e01b78ef-3414-5010-bfab-6d64bc66ca99 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
2ead78e1-4688-5c15-a0d0-bd86c8ba6448 | note | Reference Documents: Signed and completed ITP
23b81137-69b8-53c5-9e7f-21eafd7018e1 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
b4193d9a-296d-536c-bd76-87d4cffbdf36 | note | Record of conformity: Signed ITP
7c912d8e-7b2d-5ea2-ae94-9cce2e251b07 | note | HP*
41f4dbf0-9b21-59c0-a562-a12c50a3630e | note | Responsibility: Site Engineer
67b03e41-861c-5c45-b429-9e432ef77289 | date | Date Completed:
| checkpoint | 2.15 - Receive completed FLE ITP SS310 - Ductor Test Results (Insulation resistance DLA/DDF)
e914c482-305b-575e-b891-ac9c6cb58f21 | note | Frequency: Per ITP
81305a37-26e4-586a-988a-9cea02cf6465 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
6bfeb68f-709a-58d2-91c5-1bf5b2483016 | note | Reference Documents: Signed and completed ITP
3a850046-094f-52e2-8e92-0003c4b7c5af | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
ad7af829-8bad-5ba1-b2ef-1e51681461fb | note | Record of conformity: Signed ITP
51dafac2-ef29-512e-ab22-706843ba6c89 | note | HP*
4cad94c0-aac6-5bb7-8451-55f6b0126399 | note | Responsibility: Site Engineer
3b9701af-8fae-5392-a42f-c9b197248b22 | date | Date Completed:
| checkpoint | 2.16 - Receive completed FLE ITP SS311 - Marshalling Box Installation Checklist
54457018-03d3-569f-aefe-45c0c6c56209 | note | Frequency: Per ITP
17094e0f-f9f2-5123-b923-09a5e394f723 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
fa04ef50-532a-53f9-906c-63a5acde5ba4 | note | Reference Documents: Signed and completed ITP
7df36cd2-64c8-5e99-bf5d-fce6c9b09035 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
204c31be-eaee-5b29-9a02-77dcb7e3fe56 | note | Record of conformity: Signed ITP
eaa816af-c9cf-531e-b991-61f6bc4f9490 | note | HP*
a4eb368f-8f70-50a3-aa4d-4a7147261d33 | note | Responsibility: Site Engineer
eee55797-822f-507a-a0fd-0aed3e9344ee | date | Date Completed:
| checkpoint | 2.17 - Receive completed FLE ITP SS312 - HV Cable termination
e9c1b1b0-ca22-573a-865c-ef82b7ef1591 | note | Frequency: Per ITP
f2cb88aa-44ce-56a9-acc2-e51e8a8f3bc4 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
d30c7852-99d0-5967-a331-6471ae3e9f4e | note | Reference Documents: Signed and completed ITP
1314cd95-e43b-5452-8f20-301c79cab5a4 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
6a37c35d-ff80-5627-8c89-328645657a18 | note | Record of conformity: Signed ITP
190c46b5-031f-5435-b4b9-5956c6e3105e | note | HP*
0a5ef813-4297-57ba-820e-2538ec8a8fc9 | note | Responsibility: Site Engineer
92178d88-77ad-5a8f-943e-caf305d1df88 | date | Date Completed:
| checkpoint | 2.18 - Receive completed FLE ITP SS313 - Light and Power in Substation Building
f5b93aba-9d25-539a-91d8-1d58f08bdd5f | note | Frequency: Per ITP
a26e0431-7e47-5c42-94fa-5e819ea37e27 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
3380a5b3-99f8-5779-b464-65cd87f5ae63 | note | Reference Documents: Signed and completed ITP
f6d0be86-6293-5be0-b747-725ebdad0c48 | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
839a762f-bc35-53fa-8475-24992e8f008f | note | Record of conformity: Signed ITP
1048d948-83e6-5694-a303-1e80223b0788 | note | HP*
7323686b-da43-5b37-8e98-548814905aaa | note | Responsibility: Site Engineer
6d53d406-12f8-591d-b366-7ef5c97b7ab7 | date | Date Completed:
| checkpoint | 2.19 - Receive completed FLE ITP SS314 - Field Cable Installation
21881c0d-bf93-575d-bb26-1599816b58f9 | note | Frequency: Per ITP
4dae6fcf-9c94-506a-99fe-00467a062b18 | note | Acceptance Criteria: ITP per lot package satisfactorily completed
44df8283-fb87-5059-89ce-fd91b0359761 | note | Reference Documents: Signed and completed ITP
080e9573-be59-5092-a1fa-1e60ea14312f | note | Inspection / Test Method: Verify to TDESTD AS/NZS 300
09351a5d-1073-5835-acbd-16fe74fd1f15 | note | Record of conformity: Signed ITP
47d000ea-bbe5-51d1-84aa-ab9be92b9a45 | note | HP*
cbd2164e-981d-5316-8188-2d441803703c | note | Responsibility: Site Engineer
b48c413a-3ca1-5c1f-be0a-d8548af34cd1 | date | Date Completed:
| section | 3 - Final Inspection
| checkpoint | Final Inspection
95942443-6527-56a2-b5ea-a4842155354c | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
e429ccfd-dac4-56fe-98e5-c732c36bfacf | textbox | Print Name:
34591ab1-ca50-5d59-bbbf-8840503e32e9 | textbox | Position:
ff7e91c2-5747-5459-8d8c-d06032683757 | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-015 - Container Farm Construction | itp | GT4-ITP-015 - Container Farm Construction | 6c4da8cf-3197-44a8-a451-b8a5533689cb
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
b8b9c150-909d-5c14-8867-2a60f3a629c4 | note | Frequency: Prior to commencing any activity
f1039d57-1bae-53e9-9a13-7fbf3f3ac546 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
7682e887-2033-52be-a8c2-da225d63a939 | note | – using the correct and complete set of drawings
978175e5-45f6-56dd-96c5-6db2518e7d6e | note | – all drawings are the latest revision
e70d5b6a-eb58-5fd8-ba62-019a71c58824 | note | Reference Documents: Drawings and drawing registers
3433ba6a-f7f6-5a4d-b16d-d86584217747 | note | Inspection / Test Method: Visual inspection
f66f55ed-8f7a-5151-9d36-5cf993648836 | note | Record of conformity: This ITP signed
ca67151e-bdd6-56ed-913f-e324743d7188 | note | HP*
a44344df-e14e-5d3b-978c-3fa359c8c8e0 | note | Responsibility: Site/Project Engineer
863088fb-ac13-5c82-85a5-7c02f17697c2 | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
dee0c6de-0fc8-583e-8e08-d500c2a1e8a9 | note | Frequency: Prior to commencing works
7b3b61dd-3e70-5996-8b05-878770a833e8 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP`
cb55b8ff-75a3-5239-b58f-dfca2dab7b57 | note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
da584b1d-5c5f-5e2d-9e75-44d4d713caf9 | note | Inspection / Test Method: Visual Inspection
c037285e-5341-59ee-a869-2767030496b5 | note | Record of conformity: This ITP signed
1dd9bcf8-6fdc-5174-ac2a-9797494abc86 | note | HP*
ae5228dd-7d42-58be-8657-1a80dca1cfda | note | Responsibility: Site/Project Engineer
0e7a7c51-2354-518c-b641-ad9d955d6a6b | date | Date Completed:
| checkpoint | 1.3 - Plant and Equipment
95a89a28-6df9-55c0-a0b1-aa7dcd6e74b7 | note | Frequency: Prior to commencing works
50df320d-14d0-58b1-a5c0-c0bfabffd985 | note | Acceptance Criteria: Plant and equipment used in the Works are appropriate to achieve specification requirements and is inducted
9f7c2a9e-52b2-57cc-afea-7ea2c7b00fd2 | note | Reference Documents: N/A
dc1a5fe1-a5ca-5dbb-94a1-a61e570025a4 | note | Inspection / Test Method: Visual Inspection
8c946410-f7fa-5da0-b8b1-7b4edf16f5fd | note | Record of conformity: This ITP signed
a3ce0272-7fe1-5aab-8039-cc4c7f510501 | note | IP
b2d5e08e-09a9-5b69-b527-811393b18fe9 | note | Responsibility: Site/Project Engineer
cb42b359-afbf-59b3-bfb8-cdefc4ad73d9 | date | Date Completed:
| checkpoint | 1.4 - Service Locating and Proving
642c81b6-42e8-51d6-8163-68c61e2d3613 | note | Frequency: Prior to commencing works
2a6a8eff-9015-5e2b-af36-9ae06916474e | note | Acceptance Criteria: The Contractor should familiarize themselves and all personnel on site with the location of all existing services on and adjacent to the site and ensure that all services are fully verified and evaluated against the proposed works.
3ccd609a-654c-56c7-9252-86e25defc5ea | note | ○ All due care shall be taken to protect existing services, structures, and works in and around the site and adjoining streets
6e9faf0f-4a69-5b90-976b-e08d5ee7513e | note | Reference Documents: Project Specification Section 1.2.1
b3fe7b4e-a585-511c-a030-eaa5f93445c8 | note | Inspection / Test Method: Visual Inspection
49aa25e2-fd76-553b-9b07-870425c18599 | note | Record of conformity: This ITP signed
c16d37f3-668d-5bf1-8904-4bb89d3cbe71 | note | HP*
f0d17545-f810-5a49-bda1-ac3436af81f8 | note | Responsibility: Site/Project Engineer
3a0230be-9ef8-505a-a039-9a38d061fbde | date | Date Completed:
| checkpoint | 1.5 - Protection and Remoal of Services
5cd8a538-94e6-5a97-8e2d-930be3fce447 | note | Frequency: Prior to commencing works
b6797ff4-dae4-5ed1-9c99-90d4ce233926 | note | Acceptance Criteria: Before demolishing and removing any part of the works with electrical wiring, gas or water pipes, conduit, telecommunications, or similar items, the Contractor shall notify the Superintendent and relevant authorities to ensure that these items are out of service and can be removed safely.
65088927-d55a-5857-9c20-53d34f25a045 | note | Reference Documents: Project Specification Section 1.2.1
ecadb343-d850-51ca-9a7c-2789ae9400c1 | note | Inspection / Test Method: Visual Inspection
d68afe0e-b9e8-5323-9272-e9e459e38694 | note | Record of conformity: This ITP signed
b4e5d6d8-a7b9-54cd-b6d3-7db0808f0063 | note | HP*
428ac2e9-9d1a-529f-a398-aea5e8a08d54 | note | Responsibility: Site/Project Engineer
27d1e86b-d7f2-5722-9899-d05468ae9b21 | date | Date Completed:
| section | 2 - Clear & Grubbing
| checkpoint | 2.1 - Tree Removal
9db23b43-cb2c-5f6e-958d-fa5ce8565134 | note | Frequency: Each Lot
2ec68a2f-d141-5455-83b9-69ad52a76409 | note | Acceptance Criteria: The clearing shall consist of removal from the area designated in the drawings of all trees, standing or fallen, and other vegetation, boulders and rubbish and shall include the grubbing out of all stumps and tree roots to a depth of 600mm below the natural surface or 400mm below the finished cut surface, whichever is the lower, and disposing of all spoils resulting from the clearing and grubbing.
e5d17181-31d1-5103-a26a-4dcb5265e603 | note | ○ Any holes left after grubbing shall be filled and compacted to the same density as that of the surrounding undisturbed soil.
aad4639f-43af-5e20-a6d7-5cda642c9b6d | note | Reference Documents: Project Specification Section 4.5
fd64b8aa-bfe4-56b6-81d2-9b0ae4fef589 | note | Inspection / Test Method: Visual Inspection
e275e6ae-d9aa-576b-aa1e-46a91b63ca15 | note | Record of conformity: This ITP signed
4de521bf-11b4-58a1-b49b-d7dd4bd25895 | note | HP*
24a446ca-6c88-5f5f-896d-9c5d26a905d8 | note | Responsibility: Site/Project Engineer
e42e8d52-fc21-585b-b66e-34591e13e093 | date | Date Completed:
| checkpoint | 2.2 - Mulching and Chipping
c43f9d5b-11e8-57f2-a954-0f4b6b7dce80 | note | Frequency: Each Lot
4bffbb85-1db1-57b3-891e-0333495772f9 | note | Acceptance Criteria: All tree trunks, branches and stumps smaller than or equal to 400mm in diameter, including leafy material, shall be mulched (unless noted otherwise) and neatly stockpiled in a site to be determined by the Superintendent.
f0a65803-50cf-5135-9e22-5705d9c98a1d | note | Reference Documents: Project Specification Section 4.6
0921c6ad-f9b9-5f4a-b3e6-fe024ffe82e0 | note | Inspection / Test Method: Visual Inspection
dcdb409a-6662-5d2a-92dc-67e47a362b74 | note | Record of conformity: This ITP signed
abed0f51-d8a0-5c39-9998-0672278664e0 | note | HP*
2374fa48-d8e6-506b-a244-041b226eacee | note | Responsibility: Site/Project Engineer
01e393bc-ab1c-5d06-8c29-723bc6dbdaa7 | date | Date Completed:
| checkpoint | 2.3 - Stripping of topsoil
b295916c-e68e-5fa2-8195-11cda4d2af06 | note | Frequency: Each Lot
2b846cae-b22d-52da-baa0-87633b542e6c | note | Acceptance Criteria: The existing topsoil shall be stripped from all areas to be earthworked, prior to the commencement of the earthworks, and stockpiled on site.
510b5b07-52fc-51ce-9c8a-03729e8f6588 | note | ○ Topsoil is defined as the layer of surface material containing humus, roots, plants and organic material exceeding one percent by weight.
03fa3a88-1ee4-5314-ba88-e50dc936532c | note | Reference Documents: Project Specification Section 4.7
7e872fe0-5b07-51ea-bcad-57befd534a31 | note | Inspection / Test Method: Visual Inspection
25f539e0-dc49-5f1e-8577-313db2904664 | note | Record of conformity: This ITP signed
afcc6e38-e135-5d8b-b6af-bc16bf70eb9a | note | HP*
065300c6-36cd-58fb-ab0a-61271302a087 | note | Responsibility: Site/Project Engineer
a80a8d32-b081-5460-956e-56b491e9f06c | date | Date Completed:
| section | 3 - Excavation
| checkpoint | 3.1 - Earthworks
f7502675-99f2-5e42-9df9-3dfcbdacdac2 | note | Frequency: Each Lot
e28bf7a0-6124-5010-b71a-c0543d943ca9 | note | Acceptance Criteria: Excavation shall include the removal of all materials encountered below natural ground level, including all obstructions of any nature that interfere with the proper execution and completion of the work.
499aef62-7479-5d18-8af2-009be6104701 | note | Reference Documents: Project Specification Section 4.2.1
70b55db2-67b9-5274-b1e9-b83c78029fd6 | note | Inspection / Test Method: Visual Inspection
4bd81092-bad3-572f-9593-8ac01be9f51b | note | Record of conformity: This ITP signed
f44b5947-bde6-535b-aff6-ed4ba95b4398 | note | IP
f12d0057-9b41-5c2e-a5d4-7da15515ad3a | note | Responsibility: Site/Project Engineer
4218902c-8f8b-529b-a15e-0e237bb783c2 | date | Date Completed:
| checkpoint | 3.2 - Subgrade Preperation
2b787ef3-2105-5ea6-9cf2-4baa1c15f0ef | note | Frequency: Each Lot
c3822628-3e65-5b67-9cc4-05aa25430ac2 | note | Acceptance Criteria: The sub-grade shall be trimmed to an even surface free from loose material. Remove roots, boulders and other unsuitable materials such as silt or organic matter as directed by the Superintendent.
2b1fde7a-9799-5bc3-870a-4ad4cdd715ca | note | ○ Grade depressions to drain to the edge of the formation. Where the subgrade is unable to support construction equipment or it is not possible to compact the overlying pavement because of a high subgrade moisture content the Contractor shall refer to the project specification for treatments.
5ba1875a-2a12-5cd0-9742-345875de582a | note | Reference Documents: Project Specification Section 4.13
7a3fe008-0a58-5a16-bcf3-8e14bb474611 | note | Inspection / Test Method: Verify
cc74a245-f2c3-5772-85b1-a6dd65098d9d | note | Record of conformity: This ITP signed
af9a8717-b0e7-59a8-8319-084ed2700fb5 | note | HP*
3ec35b37-5f39-5a50-bea7-7061d994b123 | note | Responsibility: Site/Project Engineer
3c5c9df2-0f44-59ac-88c5-a768a51354ad | date | Date Completed:
| checkpoint | 3.3 - Survey Conformance
f459d0e5-9906-5a8d-b4d3-b80f4fc2c67d | note | Frequency: 1 per project
071baf4e-2d08-5384-a575-5f3cfeed74f5 | note | Acceptance Criteria: The subgrade formation surface shall be finished within the following tolerances:
c3908d7e-efb9-53b9-b1bc-67ff5cb5591e | note | ○ Variation from a 3 m straight edge 10 mm
acbb2490-7328-525e-b826-4cafd144f572 | note | – – – – – – – – – –
c15a30d1-6d95-5bd0-b830-53cbc4a41c03 | note | Test/Record Frequency
73629f5a-3ac5-5c58-9669-5c3e1955db3d | note | – – – – – – – – – –
777242f5-b549-5609-9d50-7768a9f84125 | note | Finished subgrade level ¦¦ + 5mm or - 30mm (+0mm)
a80ff8a0-31f1-593b-b8cd-d090f97fe5d5 | note | Sub-base width ¦¦ + 300mm and - 0mm
c2216a2b-0e19-5ba5-a850-2d9188b24d36 | note | Finished sub-base level ¦¦ + 10mm or - 20mm
a3e9cda2-24e7-57c6-8429-8c2c5ccc6c1d | note | Basecourse width ¦¦ + 300mm and - 0mm
0ad6e7a6-f212-562d-9f9a-16bcbcb9d5c3 | note | Basecourse thickness ¦¦ - 0mm
b6b8005a-50d3-500c-bbf2-1f2891d38ca1 | note | Finished basecourse level ¦¦ + 10mm or - 10mm
b0d9b4a4-614f-5fce-ba62-8381620248b1 | note | Thickness of AC ¦¦ + 5mm or - 0mm
8ab0ba60-64e6-52ea-b2a6-b986abb957f8 | note | Finished AC or brick paving level ¦¦ + 10mm or -10mm
1c48c4d2-4abe-52ff-9ebd-300ad43d7112 | note | – – – – – – – – – –
79b20a9a-0147-57f7-a969-9ea184012e44 | note | Reference Documents: Project Specification Table 4.3
afe4bb52-9976-54fe-8a53-a41a8f614be4 | note | Inspection / Test Method: Verify
939f9630-6ca9-5973-a23b-5a85b2aab71a | note | Record of conformity: Conformance Report
8890adab-1991-54c6-93af-8186592010bf | note | SCP
62274308-3a84-566b-82d3-8ee075383ca6 | note | Responsibility: Site/Project Engineer Surveyor
e3530280-bfad-54f8-9489-34833cf2799e | date | Date Completed:
| section | 4 - Placement of Crush Rock
| checkpoint | 4.1 - Placement
2be8fcab-151a-5ff1-a27b-4d8a0b5cfc6b | note | Frequency: Each Lot
a766c93d-6316-5d2d-af86-ca444f3e0ebc | note | Acceptance Criteria: Once the sub-grade has been approved, crushed rock shall be evenly spread in layers no thicker than 150mm
9135cd9d-aa5e-58d7-8f41-c13d911a8a61 | note | Reference Documents: Project Specification Section 6.8.1
5bc901d8-256e-5e09-aa7c-4ddc7b84fbb8 | note | Inspection / Test Method: Visual Inspection
aefe3b38-edb0-59ae-8e10-017c6a51a277 | note | Record of conformity: This ITP signed
7ced1f61-cb4f-5916-aebd-4b72f9e34eb6 | note | IP
48618217-e466-51c9-b77b-f4b01d70f2bc | note | Responsibility: Site/Project Engineer
3f65f320-89e4-5f86-8559-ee9bb57b492f | date | Date Completed:
| checkpoint | 4.2 - Material Quality
1b68dac4-f60f-5fe4-b213-b4ea2a4bb363 | note | Frequency: Each Lot
9eeac628-a9f3-51d3-a824-6abd68c1980f | note | Acceptance Criteria: The material should be spread without segregation and between approved edge boards or kerbs.
05fd4fe9-8839-5669-bd08-578218d86dc8 | note | ○ The crushed rock should not be spread on waterlogged sub-grade, and any soft spots or areas with mixed materials must be dug out and replaced with approved material.
9e3536fb-74ce-578d-bb3f-a16b2cff726d | note | Reference Documents: Project Specification Section 6.8.1
44501160-5a42-551e-8429-9c4bc738c4dc | note | Inspection / Test Method: Visual Inspection
e19c4d4e-01cd-51e7-9166-0459eff139ba | note | Record of conformity: This ITP signed
ba4a6332-27dd-57e3-bd9f-7c4d368b10c9 | note | IP
3a81b1ee-792f-5e6f-908a-b7b3b1214e69 | note | Responsibility: Site/Project Engineer
8d39b5e0-eb84-5815-82ad-6451a82b1c7c | date | Date Completed:
| checkpoint | 4.3 - Testing and Proof Roll
ded87d32-1e73-5123-9ae1-768bd99cf698 | note | Frequency: Each Lot
a38b990a-4009-54cc-9341-90153923aecf | note | Acceptance Criteria: Rolling must be performed to eliminate bumps and irregularities, with the finished surface being true to the required grades and cross-section.
7cf7aec2-bdb7-5b71-b74f-c7658eca1211 | note | ○ The crushed rock must show no movement under a six-tonne smooth steel-wheeled roller, and the minimum compaction achieved must be 100% of the Standard Maximum Dry Density in the base course and 98% in the sub-base course.
0a1304a4-aa8f-568c-98d3-b2692171f01a | note | ○ The thickness specified is the minimum required.
028249db-301d-5a3b-9726-b464ec4152a5 | note | Reference Documents: Project Specification Section 6.8.1
4195e96d-ff9f-58bb-9529-299449e61f4d | note | Inspection / Test Method: Verify
dd9ca005-0a2a-5bd2-a677-96a1319c16dc | note | Record of conformity: Test Report
07c5c72f-2bc7-5ef5-9604-cead1c16aa0a | note | TP
eb43c1dc-bd98-5bc4-9329-2284038dfa8f | note | Responsibility: Site/Project Engineer
13824539-afc1-58ac-9abf-e2c20470a37a | date | Date Completed:
| checkpoint | 4.4 - Shape
a342a170-668d-5109-88db-1ff856474d56 | note | Frequency: Each Lot
3a678a90-2566-5edc-aa59-1cba33a6587c | note | Acceptance Criteria: The shape of the road must be checked frequently during final shaping and compacting and corrected as necessary by grading under the direction of an experienced foreman.
de5ef2b5-1197-5370-b728-cf6352d83fd3 | note | ○ The crossfall, super-elevation, and smoothness of the grade must be checked using a straight edge and built-in level.
9268de27-7ebb-5c65-9528-462a74134770 | note | Reference Documents: Project Specification Section 6.8.2
2efc3695-d627-5fb3-aaaa-c976c95b73be | note | Inspection / Test Method: Visual Inspection
fbf79b38-3a38-58ca-a017-39cddb5394ad | note | Record of conformity: This ITP signed
1d7061c5-0d89-546d-8c60-9cd0dcd2ab31 | note | IP
06dcb92c-b82c-5da8-92b1-534878a9fb6a | note | Responsibility: Site/Project Engineer
155b0501-c0b9-5efc-b812-d1e285733c87 | date | Date Completed:
| checkpoint | 4.5 - Conformance
8335be9f-f841-51f4-96f5-4afb1b4d05dc | note | Frequency: Each Lot
e6c7b1a4-e7ee-55c1-aeea-07c45a9fc4e6 | note | Acceptance Criteria: The following construction tolerances must be achived by the contractor
04a6867a-d792-52ad-9c6c-2157155bb9ba | note | – – – – – – – – – –
82d6b080-e2df-5a48-a0e0-f8aa9ddb9eec | note | Test/Record Frequency
69c89bad-32b5-5ddc-9ffc-372ef0d8f1ac | note | – – – – – – – – – –
3ba0d6a6-6eab-5d11-8c29-62735fb5c625 | note | Finished subgrade level ¦¦ + 5mm or - 30mm (+0mm)
4f730778-f72c-5018-af10-82c704dcd4a6 | note | Sub-base width ¦¦ + 300mm and - 0mm
9d918ce1-4a36-59af-a2b9-4824abe32976 | note | Finished sub-base level ¦¦ + 10mm or - 20mm
fb895833-418a-59ce-8b10-3c706d94864b | note | Basecourse width ¦¦ + 300mm and - 0mm
93083d07-fd34-51c1-83ca-62edbddc36dc | note | Basecourse thickness ¦¦ - 0mm
0de2f310-91b9-5e51-8688-d7d62699a743 | note | Finished basecourse level ¦¦ + 10mm or - 10mm
7e8b04ff-733c-589c-b4ec-2ffb59de5a28 | note | Thickness of AC ¦¦ + 5mm or - 0mm
93b806c9-aadb-5f60-8efe-3f1b0377aa59 | note | Finished AC or brick paving level ¦¦ + 10mm or -10mm
2748baa3-e53e-5092-9147-971d9c3255c8 | note | – – – – – – – – – –
b2bcb694-3397-5f2a-9e7c-8ec23656bf91 | note | Reference Documents: Project Specification Table 4.3
bbd3944c-c112-55ca-bad7-256db466dc0b | note | Inspection / Test Method: Verify
32edc792-eb81-54d3-add5-6823845ed3b4 | note | Record of conformity: Conformance Report
64987616-e6c7-5e6d-9ded-ecbadb8517f1 | note | SCP
6e7514da-9b2f-54e9-affb-a3f63e36e5bf | note | Responsibility: Site/Project Engineer Surveyor
1ce9f9ef-9322-54d2-b50b-78df95174b9b | date | Date Completed:
| section | 5 - Asphalt Path Placement
| checkpoint | 5.1 - Asphalt Mix Specification
5dd0b0c6-8216-5fdf-92b7-9134bf5cf77c | note | Frequency: Each Lot
bbd4ec31-071a-5f44-a01d-5680a76c2047 | note | Acceptance Criteria: The bitumen grade is to be Class 170. The bitumen is to conform to AS 2008 and the current Austroads Guide to Pavement Technology Part 3. Aspahlt to be a 30mm compacted depth of 7mm NS type L asphalt
4ea490d3-6625-5305-8144-e74a47014006 | note | Reference Documents: Project Specification Section 6.5.3
a0e54723-b77e-545f-a005-f7b89eb6fbc0 | note | Inspection / Test Method: Visual Inspection
bf43be89-f6d9-50aa-95dc-c1c8c2bde45d | note | Record of conformity: This ITP signed
975a0389-9407-5dd8-b0ab-38d987d249bb | note | IP
11e1b4a3-96fd-5775-9027-807d6b14ba77 | note | Responsibility: Site/Project Engineer
327cb94f-8fb8-5432-aab5-726b424815a2 | date | Date Completed:
| checkpoint | 5.2 - Placement
25196335-49fd-5747-826a-009316df7665 | note | Frequency: Each Lot
ea553d3d-e98f-57fe-b18e-868a5ac0dcc8 | note | Acceptance Criteria: The temperature of the pavement to be surfaced should be at least 10 degrees Celsius, and no rain should fall during the placing of the mix.
15d8c45f-aee4-5724-985f-4051f5eb2842 | note | ○ The surface must be dry.
61da410e-0f77-5b6a-82bc-3bb22cfb07ee | note | ○ Asphalt should be placed at a rate that will provide the required compacted thickness shown on the drawings.
e74617a8-6148-5ed0-9b07-a0d01e88288c | note | Reference Documents: Project Specification Section 6.9.2
ede3dc99-fb80-5d29-a10e-9b65fc021456 | note | Inspection / Test Method: Visual Inspection
8c5ac0a2-def1-5086-8c47-09646516c548 | note | Record of conformity: This ITP signed
1c62eed5-ca63-50f7-a35d-6b67e62f539e | note | IP
f2705441-feec-5013-b58f-96082b747d12 | note | Responsibility: Site/Project Engineer
6b47f7b2-875b-5fed-888e-d337d1f16142 | date | Date Completed:
| checkpoint | 5.3 - Jointing
3be959db-6b6e-5a22-9546-f93ad308fa38 | note | Frequency: Each paver run
a5ae53d5-5744-503f-9f7b-7a37245707ee | note | Acceptance Criteria: Joints must be waterproof and formed as necessary to ensure a smooth and even profile over the joints without ridges or depressions. Joints must be in accordance with AS 2150 Section 12.6.
6dcd35a1-13bb-5458-bebe-2a40683e8095 | note | Reference Documents: Project Specification Section 6.9.2
5885fdc0-dac8-5f35-83a8-a0226b840d62 | note | Inspection / Test Method: Visual Inspection
fbf126c5-f41b-5a0b-8684-9d143d3bf096 | note | Record of conformity: This ITP signed
6b598b2f-1e46-5d95-b382-ae866977cefb | note | IP
c33d2e9a-caf8-50ca-8537-e0dce0c1454e | note | Responsibility: Site/Project Engineer
1833461a-5a4a-5c4b-aebf-71c3db83cb5d | date | Date Completed:
| checkpoint | 5.4 - Compaction
87bbbcd3-2acd-5e28-a63b-89cadb8739a4 | note | Frequency: Each Lot
163efb8f-0a48-5cac-9d4e-135f4e3e2665 | note | Acceptance Criteria: Rolling procedure to be confirmed by contractor on site.
7965cb39-9a5b-5b2e-97eb-4c3d313b19d2 | note | ○ If the asphalt begins to shove or crack, rolling must not continue until the cause is determined, and corrective measures are taken. During all rolling operations, drums and wheels of rollers must be kept wet with water and be clean.
2e0c5180-24c1-5a85-b6d3-be1e8c232e4b | note | Reference Documents: Project Specification Section 6.9.2
8336ed67-e3b3-5456-92a1-95626aeed00c | note | Inspection / Test Method: Verify
38f00a23-7a12-595e-92f6-bfcd3cf1d553 | note | Record of conformity: Test Report
40ddff03-24ea-542b-b13e-a39010e90948 | note | TP
7be6f566-0419-5c12-bf7f-3b05fc8e6c23 | note | Responsibility: Site/Project Engineer
bf49365f-1d71-5726-8c48-d14cbf0e29d4 | date | Date Completed:
| checkpoint | 5.5 - Layer Thickness
f61fc9ab-b078-57c7-983b-7f2539e21f63 | note | Frequency: Each Lot
e61d7efd-cd4d-5641-bd89-e99c3c0c639f | note | Acceptance Criteria: Asphalt thickness to be 30mm with a construction tolerance of + 5mm or - 0mm
9f81154d-5a59-5b5c-a08b-dcd51741272f | note | Reference Documents: IFC Drawings
7145dcec-b520-59ca-8e90-484556979b8d | note | Inspection / Test Method: Verify
9dfcd72d-a010-55bb-aeb4-81ffaaf2e8bf | note | Record of conformity: This ITP signed
d0dd06bf-211b-5d81-ab2d-806e549516ac | note | IP
a2201c7d-3dec-5c25-9e4c-1b80cde98767 | note | Responsibility: Site/Project Engineer
bb4291f2-00dc-533c-a949-b8701e5d214b | date | Date Completed:
| checkpoint | 5.6 - Tolerances
9ba9013b-f250-5bd4-bea5-08b074ecd805 | note | Frequency: Each Lot
98048b12-ac19-5a94-9099-adcb06153c0a | note | Acceptance Criteria: The following construction tolerances must be achived by the contractor
b11622ed-5cd2-5fc5-b3ee-b88317f0eee2 | note | – – – – – – – – – –
504f2e35-9158-5e37-85ea-377f504f0b87 | note | Thickness of AC ¦¦ + 5mm or - 0mm
d229b064-1434-52b3-bfa8-97fa7fd0f75f | note | Finished AC or brick paving level ¦¦ + 10mm or -10mm
ea9db91e-62b0-5ef7-a89e-e882dc5d5bc4 | note | – – – – – – – – – –
130fcd22-a538-5c04-9758-8ed7affe4e21 | note | Reference Documents: Project Specification Table 4.3
59f91816-2ff5-5331-8d06-63b4228eefdc | note | Inspection / Test Method: Verify
fcc6895e-5865-5010-a836-20bd86b40127 | note | Record of conformity: Conformance Report
145171d8-5533-5fef-ac4a-f6266c0bb115 | note | SCP
f1c08c99-eec8-5224-828a-749ea9fc7792 | note | Responsibility: Site/Project Engineer Surveyor
69758d88-8eeb-5355-b55e-7aac9f515154 | date | Date Completed:
| section | 6 - Concrete Ramps
| checkpoint | 6.1 - Concrete Mix Design
a1e92ad0-cdb3-558f-9906-3c669d8ba289 | note | Frequency: Each Lot
bbd55d15-0331-50f0-a22e-509669cee763 | note | Acceptance Criteria: The concrete used must adhere to AS 3600 and must be obtained from a concrete supplier that conforms to AS 1379.
e31e801b-ef3c-5540-81b5-3baf9df1d6c4 | note | ○ It should possess a minimum characteristic strength of 25 MPa (N25), a maximum aggregate size of 20mm and a slump of 60mm.
7e44a8f9-0f3e-5837-9201-636ea7f75dcc | note | Reference Documents: Project Specification Section 5.5.5
2fff5386-c4ad-560c-bb46-3851bccc7b8c | note | Inspection / Test Method: Verify
a4b2b022-f608-5257-9bc4-8db1dc7991c8 | note | Record of conformity: This ITP signed
ec2175c3-2c30-5ae1-bddf-c78720ec21fd | note | HP*
77425e8b-3d7d-5088-a426-57ba5514372d | note | Responsibility: Site/Project Engineer
fc268692-1c10-5420-bcc6-bdd3c3435937 | date | Date Completed:
| checkpoint | 6.2 - Reinforment
54278865-8862-5afc-8100-9268106b3290 | note | Frequency: Each Lot
c9ebf277-ecd0-58ee-81d0-774717b4c9cb | note | Acceptance Criteria: Reinforcement to be SL72 Mesh as per the drawings
2cccbfab-e896-5036-81e8-5a1746dc6f27 | note | Reference Documents: CV-130
d99bf0ed-004b-5f5d-a983-49e3d6b928ce | note | Inspection / Test Method: Verify
1037451b-e8ac-5a80-82f8-e7dd01737a39 | note | Record of conformity: This ITP signed
82e4525d-e6e7-575a-bf14-bba9278f21c8 | note | IP
15469c2f-4142-5ed7-8682-98f039147ef9 | note | Responsibility: Site/Project Engineer
3400806c-b741-51c6-870d-62f1bb44bddc | date | Date Completed:
| checkpoint | 6.3 - Placement
01117ba7-838c-5488-92a5-470944f61229 | note | Frequency: Each Lot
ad844cc9-c367-5e50-901d-439ff5727e8b | note | Acceptance Criteria: Contractor to ensure concrete is adequetly vibrated during placement.
e413e90e-705e-5af9-a91d-e4e672ef5215 | note | Reference Documents: Work Procedure
410384a3-f631-5353-89b0-3e13911b4d94 | note | Inspection / Test Method: Visual Inspection
b2840b0d-54f1-5d82-9bc3-889377affa5c | note | Record of conformity: This ITP signed
88cb1043-a898-5c12-a549-a0e8b3ea655e | note | IP
1809e0ce-68c3-5a3d-9192-21b141964c25 | note | Responsibility: Site/Project Engineer
3a2b2c5b-8847-5721-a3cf-4ea4a81f8a78 | date | Date Completed:
| checkpoint | 6.4 - Tolerances
c87d545a-0b5d-5461-9302-b34ab183d3e7 | note | Frequency: Each Lot
e5fcf028-390b-54fb-92a8-afc6f539568f | note | Acceptance Criteria: Concrete to adhere to the tolernaces of a class 3 finish
a7b7d3d9-75b2-58a7-9156-110ef4634798 | note | Reference Documents: Work Procedure
434bc447-d542-5b07-94d8-81b30f8045fa | note | Inspection / Test Method: Verify
c0ff09ed-bfd3-5549-bb8e-cc123f4dc017 | note | Record of conformity: Conformance Report
ba632028-7297-5c3f-800e-75fb4d50014e | note | SCP
6f3a9872-8f92-551a-84b9-b6f4cb160ced | note | Responsibility: Site/Project Engineer Surveyor
11048e5e-f12d-521b-9cb9-38f515b093d2 | date | Date Completed:
| checkpoint | Final Inspection
24d95d55-e9f0-5c99-acf3-3c4de57b5893 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
b1b7c6eb-961c-5912-930d-8676d19dbe9c | textbox | Print Name:
75809418-c2a1-5e00-aa65-9e584d55dbff | textbox | Position:
6586e8b3-7387-53e8-8c9f-de21217f1bee | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-016 - Cement Treated Crushed Rock | itp | GT4-ITP-016 - Cement Treated Crushed Rock | 2240fd55-240a-48a6-9f16-9ad9fc4c1d27
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check that current revision drawings are being used
cf291b18-de52-5de9-ac1b-beb344c81988 | note | Frequency: Prior to Commencing Work
e263a7b5-a463-5963-b902-3825d5c5d6fa | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
f948ab12-a59e-5bf8-8451-260016540f51 | note | Reference Documents: IFC Project Drawings/ Drawing Register
bd48a409-e6e9-52a7-ba4c-d602b71fd389 | note | Inspection / Test Method: Document review
616a30cd-2523-5f3e-a445-610bd272706a | note | Record of conformity: Latest revision IFC drawings
7da88eec-fe08-56ac-908b-95e704a266fc | note | *FH
63b26a0f-1d30-5c86-abcb-8adab3d3d833 | note | Responsibility: Site Engineer
c51fa852-37fa-5199-9e62-bc1a3bd3a9e4 | date | Date Completed:
| checkpoint | 1.2 - Confirm understanding of current EMP related to the work area and that all prescribed environmental controls are in place
33b93d1b-71ec-5a81-8a12-8d4a237c314c | note | Frequency: Prior to Commencing Work
db3dfc38-93b7-56c3-a1c9-1923f1b5248e | note | Acceptance Criteria: All environmental measures to be implemented as per current EMP and local authorities. Sediment control measures to be installed and protected vegetation to be clearly identified
978c9ec7-1bbf-555d-ae28-50cff2e4f478 | note | Reference Documents: EMP, Site induction
b1c1aad8-eb3c-5205-b789-770846e65574 | note | Inspection / Test Method: Document review & Site inspection
2b738745-8021-5879-b57b-7ca09886197c | note | Record of conformity: ITP signed
b5bf32c8-f3a9-5f1b-9d3a-961fe96d5ae4 | note | *FH
36f09ddf-2c3e-5f66-8c0d-bc3481d3275c | note | Responsibility: Site Engineer
cac76a4b-bf2c-582d-8363-e68a16cc230f | date | Date Completed:
| checkpoint | 1.3 - Traffic Management (When required)
24747068-437c-5129-bedd-0fdac6e5a436 | note | Frequency: Prior to Commencing Work
c0d83f08-a67c-5b1f-9f67-53049e083a96 | note | Acceptance Criteria: Approved TMP
a7f5bbc3-736f-5837-b9a6-43ff7886b13a | note | Reference Documents: Applicable TMP
43221b9e-be8b-5278-87b6-1659d16f5af0 | note | Inspection / Test Method: Document review & Site inspection
a994542d-2554-5e44-950d-86a5b5c4227f | note | Record of conformity: Approved TMP & MOA
1e731bef-92bb-56d2-a6af-e99066f3d577 | note | *FH
85de30f6-e78c-5491-9c85-ca0cc291bbda | note | Responsibility: Site Engineer
8a1f970a-5df1-5ed3-97e4-4db233576baf | date | Date Completed:
| checkpoint | 1.4 - Survey set out works
35749df3-ccf7-518e-8418-f49289ad5a3c | note | Frequency: Prior to Commencing Work
486437fb-8095-5497-884d-960d6d459307 | note | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
c082d46c-8e8c-5a66-9ed0-5d96633fe609 | note | Reference Documents: Applicable DWG
d2801102-ecea-54d2-9614-d9dc3238097b | note | Inspection / Test Method: Site inspection
6bcc142e-8906-54ae-8450-b361a4a6a097 | note | Record of conformity: Survey records & marks on the ground. This ITP Signed off.
fcbd6caa-acb9-5a14-a924-3d67bd14a189 | note | SCP
e2c50ad8-a692-5ddf-9a54-26220812f551 | note | Responsibility: Site Engineer / Surveyor / Superintendent
2b4a4838-685f-5515-979c-c8970cbcad3b | date | Date Completed:
| section | 2 - Placement
| checkpoint | 2.1 - Delivery Dockets
c53926de-0b01-5923-a589-e0e7f8ee512d | note | Frequency: Each lot
371055ab-130a-5916-9728-abb61504ae11 | note | Acceptance Criteria: Where material is scheduled for measurement by loose volume in delivery vehicles or by mass, a delivery docket for each load shall be issued to the Superintendent at the point of delivery.
1a8e7bcb-e3cb-51a4-bf2f-3289f5686a90 | note | Reference Documents: VicRoads Sec. 306.07 (b)
8884a081-9ea2-52f7-90a8-ae12e69db902 | note | Inspection / Test Method: Visual and Measure
ad86069b-d7fd-5649-954b-6ebd3ae5c9ac | note | Record of conformity: This ITP signed
d5d17753-675b-529f-8bf7-52d94737c381 | note | IP
aa1d36a5-c053-501c-9c11-ca7cb088ed88 | note | Responsibility: Site Engineer
3bebbe5e-4b5f-531b-82e8-880262e95627 | date | Date Completed:
| checkpoint | 2.2 - Placing of Crushed Rock
c2c5d71c-bdf9-57e4-a21a-3105b88b2023 | note | Frequency: Each lot
de86d94f-3d6f-5c80-9a53-d8d02bc97680 | note | Acceptance Criteria: Crushed rock to be a single layer 150mm thick constructed within the tolerances specified in Clause 306.03.
07ca1ef9-5121-5bd9-b059-bd62bca735bd | note | Reference Documents: VicRoads Sec. 306.03, 306.11
7c66bacc-95c6-526e-8be6-55f76f25e52a | note | Inspection / Test Method: Verify
8d3bd9d2-55a9-57a4-a31a-4ed46601cd0d | note | Record of conformity: This ITP signed
d7100472-850c-5823-9bdc-d5a3fb161ad2 | note | IP
ecd16e80-8ea0-5c32-a28f-97066983dcb0 | note | Responsibility: Site Engineer
259d7e2f-73e3-554a-8770-265d8947fdc9 | date | Date Completed:
| checkpoint | 2.3 - Moisture Content
858b91d4-4e28-5a1d-ad71-0c22472c6448 | note | Frequency: Each lot
34cb0689-9f30-5e29-91e7-f2840a4cebd0 | note | Acceptance Criteria: The moisture content of the material at the time of spreading and compaction, expressed as a percentage by mass, shall be within plus 2% and minus 2% from the Modified optimum moisture content.
7c47349e-4a08-5075-aa26-f5e6be34c05d | note | Reference Documents: VicRoads Sec. 306.05
ed0ed0ea-cb09-5166-8575-398a94445556 | note | Inspection / Test Method: Verify
e8b15f76-7ee3-54b4-9c02-5fc952dd2784 | note | Record of conformity: This ITP signed
29b221c0-4c8e-57de-a25f-a4cbf3c7cea6 | note | IP
0657ed55-3b97-58f0-b6c5-b295db2b996b | note | Responsibility: Site Engineer
399772c5-b183-5b98-a7a5-c1e2c5b8200c | date | Date Completed:
| checkpoint | 2.4 - Water
a2feedd5-7506-50b5-a1b7-ae6d92993a5f | note | Frequency: Each lot
3d03e4ab-fdb6-523e-9ba3-f7c9e4bc44d6 | note | Acceptance Criteria: Except for the purpose of curing, no water shall be added to the cementitious treated material.
e7d37df5-d5ee-5e0d-a373-e3259f4a4f5e | note | Reference Documents: VicRoads Sec. 306.06
b41e5b68-e6a9-53b8-b26c-ec70401e2229 | note | Inspection / Test Method: Verify
2075d32d-ebcf-575e-8977-f5e8d0c162a6 | note | Record of conformity: This ITP signed
2ca1f50a-aa6e-53b7-95ea-a2b6c7aadd1c | note | IP
01edbb9d-39ee-58da-a918-e09097763431 | note | Responsibility: Site Engineer
d4ae502e-cf49-59cf-a42f-62e29ef735da | date | Date Completed:
| checkpoint | 2.5 - Conformity with drawing
7759f833-af0f-5fd8-b6bb-21934ab8bc7e | note | Frequency: Each lot
7fe1ca9b-cf10-5406-a2e2-4b818f39c713 | note | Acceptance Criteria: Pavement subbase shall be finished to a smooth and uniform surface and shall, after compaction, conform within the following limits to the levels, lines, grades, thicknesses and cross sections as specified or shown on the drawings.
e75fb2ec-8bc8-5a52-bc97-350e4930fd37 | note | For Scale B Pavement
d0600d7a-5c22-5731-b9d9-c5b1396b1c21 | note | (a) Width and Alignment
78cb2595-5066-51e7-8871-a165a7bed62f | note | ○ The width of pavement measured on each side of the centreline or design line shall not deviate by more than 50 mm from the designed offset when measured at a right angle.
cede793a-6859-51aa-8a38-1281d31d6849 | note | (b) Surface Level Requirements
dc8f9b3b-8ab7-506c-bac6-0b3415aadc30 | note | ○ Minimum Number of measuremnts per lot: 40
b5bff45b-ee7b-5144-beda-398828e66d68 | note | Reference Documents: VicRoads Sec. 306.03 Table 306.031, Table 306.032
faf30db0-a1ee-5d48-a1e3-f24e6f32dbbe | note | Inspection / Test Method: Survey
15e984c4-ef6f-5258-b468-dd206e2ba187 | note | Record of conformity: This ITP signed
8fcdf841-9430-528e-91aa-0b469f7aa89c | note | SCP
9654da72-a5c7-508e-ad0e-0959c312e5d1 | note | Responsibility: Site Engineer
2baf0e1b-6499-5172-b5a6-1d62c15a4ac3 | date | Date Completed:
| checkpoint | 2.6 - Jointing
dd30af0d-6cbc-5d73-b0a7-9fb0efc923b2 | note | Frequency: Each lot
e26d08b3-088e-56c7-952a-a46fe945608c | note | Acceptance Criteria: The layout of joints shall conform to the following requirements unless otherwise approved by the Superintendent:
96eff8f0-9f0b-52de-8cdd-28a3cb61f532 | note | (a) material shall be spread in such a manner as to minimise the number of joints;
b6f2d705-e424-5246-ad65-02e80a1cbe6f | note | (b) in any layer, transverse joints in adjoining paver runs shall be offset by not less than 2 m;
9d9ca3c7-5307-59ad-b632-8b390a0ebcb3 | note | (c) transverse joints shall be offset from one layer to the next by not less than 2 m;
2793a9e9-bc23-50cc-b54e-d7fda7969463 | note | (d) longitudinal joints shall be offset from one layer to the next by not less than 150 mm;
51110ea9-99c0-5248-b531-55104c97bc19 | note | (e) longitudinal joints shall be located within 300 mm of the planned position of traffic lane lines or within 300 mm of the centre of a traffic lane.
f89256da-7f2e-5010-9ea9-ec62561db051 | note | Reference Documents: VicRoads Sec. 306.08
bcfaec3f-f774-5c29-960d-61b2e85b9de0 | note | Inspection / Test Method: Visual Inspection
6c14716f-80de-5861-806e-21533327f9f9 | note | Record of conformity: This ITP signed
585b9907-01c1-57d5-be38-2bd4c692c145 | note | IP
d957bad0-a9b7-550e-8f41-ee52a78d6e29 | note | Responsibility: Site Engineer
d9447a82-811d-5df3-8175-9523e8eb697a | date | Date Completed:
| checkpoint | 2.7 - Compaction
043d4e6d-6b7c-5aa2-8b51-6fbf184979d5 | note | Frequency: Each lot
b58dc642-7ec6-5d0b-b5bc-f12f26d231dc | note | Acceptance Criteria: Compacted to at least 95% modified dry density ratio with a mean value of at least 96% modified dry density ratio.
081c8e90-59d9-586a-b848-adae6598cb69 | note | ○ The cementitious treated subbase material shall be placed, trimmed to level and fully compacted within the maximum allowable working time specified in Table 306.091 depending on the binder type and the time of year the subbase is being placed. (Table Attached Below)
a7f05715-893d-5a87-912b-f9f1a4ae37fe | note | Reference Documents: EW-CE-DRW-406-001 (Rev D) VicRoads Sec. 306.09
972c31ba-aee6-5edc-b43d-920b35ca5f5b | note | Inspection / Test Method: Test report
da188151-03c5-50c6-a038-ddbc8ae678cb | note | Record of conformity: ITP signed
69b1f5c5-f733-53b5-8593-7fa17e10e7af | note | TP
e250050e-f185-5186-8b10-6185123e3cdf | note | Responsibility: Site Engineer
32278647-6cd6-5fda-85df-27e6fba8cf1a | date | Date Completed:
| checkpoint | 2.8 - Curing and Protection of Compacted Layers
bc45f4d5-d8c9-5371-9239-ee7f6f9962ba | note | Frequency: Each lot
de1e8914-bd49-59a5-8dee-a5d270014dc8 | note | Acceptance Criteria: For Minimum Youngs Modulus of 500MPa,
c7fa7cf4-0a7a-5086-912d-1ea4f6dcab9c | note | ○ The surface of each compacted layer shall be kept moist for a period of seven days unless covered at an earlier stage with the succeeding layer or with an approved curing membrane.
10932341-08fc-5a28-8d21-13ed1702cdc1 | note | ○ Construction or other traffic shall not use a compacted layer within 24 hours of placement without the approval of the Superintendent.
5420a89b-0f35-55f6-96d5-f213543d62d4 | note | ○ The subbase shall be kept in good order and condition and free from contamination.
8f21e95d-e708-50ab-8394-8f4cd0ddc91c | note | Reference Documents: EW-CE-DRW-406-001 (Rev D) VicRoads Sec. 306.11 (a)
0c4692dd-4888-57e4-8933-259f8faf0747 | note | Inspection / Test Method: Verify
e02b91a2-6122-5582-b94b-4e2d84fb8ba8 | note | Record of conformity: ITP signed
2de44f50-fd8c-5d23-bebc-227e58adc11a | note | IP
7f848fb3-8c47-5868-acba-cb19c8b363eb | note | Responsibility: Site Engineer
d922ed66-d7ef-559c-8c74-9b530a0195fc | date | Date Completed:
| section | 3 - Conformance
| checkpoint | 3.1 - Test Rolling
eee7d904-5b9b-5e58-ae42-55364fccfd90 | note | Frequency: Each lot
3587cff9-b653-5366-acbf-189a065aabec | note | Acceptance Criteria: Test rolling may be carried out in accordance with the requirements of Section 173 (Specifically Section 173.03) on the cementitious treated pavement subbase layer within the maximum allowable working time for the relevant binder and time of year as specified in Table 306.091.
df38a555-9da0-5894-a77f-461740923584 | note | Reference Documents: VicRoads Sec 306.10
7f129e90-661f-51bf-8947-e2a2f37219b8 | note | Inspection / Test Method: Test Roll
8cdf5376-4460-5f53-a8ca-ae33e00805ff | note | Record of conformity: This ITP signed
2157d086-bfa6-5b9f-a1f9-168f9733a16b | note | *FH
8ccf9301-946e-5f38-bc1e-f7ac68da4adb | note | Responsibility: Site Engineer / QAV
be268333-9f11-5849-ae39-93da21c9960c | date | Date Completed:
| checkpoint | 3.2 - Testing and Acceptance of Compaction (Scale B)
87765629-8af0-52fd-b972-040d9981f7c1 | note | Frequency: Each lot
5ae7559c-d640-5825-9b71-7a7a05779698 | note | Acceptance Criteria: The work represented by the lot will be accepted as far as compaction is concerned if the mean density ratio for the lot is not less than 96.0%
eab9ed9e-194d-5f0a-a8d3-e0e7b73d52f2 | note | Reference Documents: EW-CE-DRW-406-001 (Rev D)
27ac6b67-b8d5-50e0-a4ea-8ef2ec5ae09f | note | Inspection / Test Method: Test point
2f18b6ad-5487-52fe-94d2-7d8bf20bf295 | note | Record of conformity: This ITP signed
ce9ab979-dc0d-54a2-b465-a928f2bf69fa | note | *FH
b4b8e5bf-985b-549e-9d21-225845c9082a | note | Responsibility: Site Engineer
393ffd2a-ecf5-58de-a1a1-0ca80fe1fc3c | date | Date Completed:
| checkpoint | 3.3 - Survey Conformance
65b22e2e-fece-58ed-8f70-13144ff1ea64 | note | Frequency: Each lot
9d4e6169-6f44-5327-97de-b7ad9a58d1b5 | note | Acceptance Criteria: Mean values of all level readings taken in the lot: +6mm to -12mm, Maximum Standard Deviation of 13mm
b365380d-697a-579a-8568-5b283bb0fbe6 | note | Reference Documents: VicRoads Sec. 306.03 Table 306.032
ef038073-c4ea-5686-8a62-0d3438448320 | note | Inspection / Test Method: Survey
842e858b-8c6b-5d31-926e-d6f5399773a2 | note | Record of conformity: This ITP signed
fd3edb68-1394-5613-9ecc-1f1049e64c3a | note | SCP
54c7491e-53d1-50a4-9144-619a801fcef7 | note | Responsibility: Site Engineer
80f0d53d-e0ea-524a-ac14-929772c0a949 | date | Date Completed:
| checkpoint | 3.4 - Shape
e265378c-4fe3-562d-9003-d609b122c995 | note | Frequency: Each lot
a376fea0-1f5f-590b-b8e5-877971e0f6bd | note | Acceptance Criteria: No point on the prepared surface of the subgrade shall lie more than 12 mm below a 3 metre straight edge placed on the pavement in any direction.
79250ad3-0726-5947-b64f-000cffd7a23e | note | No point on the surface of the cementitious treated subbase layer shall vary by more than 8 mm from a 3 metre straight edge, or 10 mm from a 6 metre straight edge, placed in any direction.
0140f500-d356-528f-96ae-020b72f2acf3 | note | ○ Water shall not pond on the surface of the cementitious treated subbase.
cf70c5be-a3f4-5f70-b062-e13f8b5e33a2 | note | ○ Reference Documents: VicRoads Sec. 306.03 (c)
e4b31da0-1c45-5fd8-b5ed-a4dc68774f7d | note | Inspection / Test Method: Test Point
5e1970b8-94e1-5434-acbb-cdcabfe39a61 | note | Record of conformity: This ITP signed
85596e29-c362-5820-bf7d-8f885119376d | note | TP
caea527b-5012-5501-9a13-e19c64dac829 | note | Responsibility: Site Engineer
fbc83eca-5ef9-559c-a483-14349f1676d7 | date | Date Completed:
| checkpoint | Final Inspection
13eefa15-0675-55c2-bf7c-3b664521a478 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
00101fc5-1612-59ab-86d3-d7e0462316c9 | textbox | Print Name:
111eb441-abda-59e5-9613-97b7b1135b54 | textbox | Position:
c9d415aa-99fb-539b-a85a-b57fad3adb93 | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-017 - Concrete Rigid Pavement Construction | itp | GT4-ITP-017 - Concrete Rigid Pavement Construction | 6390e2fa-8ea4-409c-a4f4-eefc118ebb97
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
77ca3d5e-fefe-54df-9aad-f93b5da81dbd | note | Frequency: Prior to commencing any activity
2f48d7e9-cc96-510b-87ae-f86983af9ccd | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
ba920d83-ae69-5582-8c95-157426b81b1c | note | – using the correct and complete set of drawings
9bc6eeed-7db6-52d5-bf37-1b9df51f8fe9 | note | – all drawings are the latest revision
6aef51e7-9941-52f7-8a12-a015f073d475 | note | Reference Documents: Drawings and drawing registers
dc3e828a-7349-5797-9abc-ef6729053fac | note | Inspection / Test Method: Visual inspection
4f83c34b-a4d1-5366-8725-2a287ba9ab13 | note | Record of conformity: ITP Signed
28a9b336-3eed-549f-ae60-ae1d7a424903 | note | HP*
13c3a2be-402a-5568-8739-a1931d64ac7a | note | Responsibility: Site Engineer/ Site Foreman
4f30ce79-7c79-5b72-a751-207a7cfd932f | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
12e8116f-5ca3-5083-9591-fcffe6d9fcf5 | note | Frequency: Prior to commencing any activity
14f00673-2df6-51de-a189-c7edafd06687 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
21571afb-6f07-54aa-92dc-83936eb7f21e | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
74989f3f-02a8-5c8d-b224-90c3ba97ecc0 | note | Inspection / Test Method: Visual Inspection
56e6bb26-e680-51f0-9d34-fb6362cd50ff | note | Record of conformity: ITP Signed
3da83ec5-4c58-5d0c-9421-18bbc0ef4e37 | note | HP*
ad0a895e-c2bd-59fe-9928-2a25e008a84f | note | Responsibility: Site Engineer/ Site Foreman
d7203656-3f5c-5ed8-bcb1-15bb5219074e | date | Date Completed:
| checkpoint | 1.3 - Concrete Mix Design
386b9d7a-db0c-5d87-88c2-ead0232bc2ca | note | Frequency: Prior to first concrete pour
93ac3fac-329e-5e6c-b4cf-233e0efcec70 | note | Acceptance Criteria: Concrete shall comply with the requirements outlned with defined pavement options specified within the Early works, Civil design drawings. Unless specified, then concrete used in this construction shall conform to AS 3600 and be provided by an approved pre-mixed concrete supplier, conforming with AS 1379.
81331be9-243f-5f9c-8c61-ba207d1ee0ee | note | Reference Documents: C.10.1 Work Procedure
92f9f7c6-09c5-5388-bdba-be8feb339b82 | note | Inspection / Test Method: Verify
b27d45d6-4033-55c4-b67d-62a442fa74b5 | note | Record of conformity: ITP Signed, Mix design approval
917c29c8-66d5-5b12-89aa-e2953b0123d8 | note | HP*
7ce8d1ba-dbbd-5f43-830a-35e48cd82447 | note | Responsibility: Site Engineer/ Superintendent
7be539a2-29d9-563d-ad23-74d5a439f168 | date | Date Completed:
| section | 2 - Initial Works
| checkpoint | 2.1 - Setting Out
1176e655-64c0-5653-97fe-98c0d924debc | note | Frequency: Prior to start
b924e70f-ba46-5180-98db-158270f9dea6 | note | Acceptance Criteria: Set out work in accordance with drawings. The Engineer and Supervisor will review and confirm set out with the surveyor.
145f0e7e-e56e-538c-a3f1-8ff947bc0751 | note | Reference Documents: Work Procedure
3801db40-a902-54af-aba1-63990305b01e | note | Inspection / Test Method: Verify
4885824e-4717-538a-873e-348bbeea77b6 | note | Record of conformity: This ITP Signed
1dba591b-a3ec-5b83-ae34-0a5fa9042b9b | note | HP*
d129002d-1ebf-5f76-a2f1-f47af1f68dc3 | note | Responsibility: Site Engineer/ Superintendent
7acb8162-b988-5c0b-8379-e065a51643a8 | date | Date Completed:
| checkpoint | 2.2 - Pre-Seal Inspection
e4b47f88-365a-585b-b226-8cfa115d9576 | note | Frequency: Each Lot
235baf81-4133-57f5-bc9d-66acaf39a047 | note | Acceptance Criteria: Pre-Seal Inspection will be completed to ensure surface adequate for spray sealing
b7db21dc-455d-5419-9b8f-6442c3a1b2ef | note | Reference Documents: Work Procedure
2577db34-6505-5711-baca-37c456fe9b71 | note | Inspection / Test Method: Verify
1413418d-23aa-5072-9ac5-51a1d3cc2a82 | note | Record of conformity: This ITP Signed
a21c99d1-2c18-500d-b693-319e21b9ccff | note | HP
7c9e518e-ece1-58b9-adb9-b5a6067a650c | note | Responsibility: Site Engineer/ Superintendent
4173fc1f-da55-5d7b-8462-49f3e5cf07ce | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.3 - De-Bonding Treatment
863d8e3b-80ce-5c47-a604-129fca8d61fb | note | Frequency: Each Lot
2c6ddebc-dced-56bc-8db8-8ca58aa33314 | note | Acceptance Criteria: Bitumen sprayed seal with 5-7mm aggregate or bitumen emulsion to be placed between Cement Treated Crushed Rock (CTCR) layer and Concrete.
f38a69b5-56ea-5969-8cb9-ac80fdf5a9ce | note | Reference Documents: EW-CE-DRW-406-001
9c999a14-5a89-5bc3-aa77-18bc9c3028a6 | note | Inspection / Test Method: Verify
fcf99568-aa87-54ed-91c5-eb4e1e80e3a8 | note | Record of conformity: ITP Signed
e86e2873-a0da-5130-b6e1-17cb8a8294e6 | note | IP
4aa08401-4c0f-501b-909d-9477987ae8ee | note | Responsibility: Site Engineer
1f420199-3a70-5989-84c1-093b6fb9bd18 | date | Date Completed:
| section | 3 - Construction Works
| checkpoint | 3.1 - Formwork
a2b83075-9c53-512f-acd6-514d5af08f77 | note | Frequency: Each Lot
db734b75-e795-5ab5-8a2d-4644c975ff96 | note | Acceptance Criteria: All formwork, shall be accurately constructed to the required lines and strong enough to remain in position without displacement during placement, compaction and support of concrete, and shall extend to the full depth of the concrete.
08715ca5-a92e-5423-86db-b61c306f1813 | note | Reference Documents: C.10.5 AS 3610
99381a91-350f-55df-a7c2-46feac78c00e | note | Inspection / Test Method: Verify
2c59e129-eb12-5e41-9c99-2370d2a2f6bb | note | Record of conformity: ITP Signed
6386e638-1aee-5234-96cc-80d87e8c9e6f | note | IP
d0710688-d3e8-579e-9f70-8b6275902670 | note | Responsibility: Site Engineer
13a5a5a3-661f-5a93-90ee-98977c11f6bb | date | Date Completed:
| checkpoint | 3.2 - Reinforcement
d91df344-1737-5ebf-92a5-84970903b096 | note | Frequency: Each Lot
4108d74b-3e2b-5573-becf-740200cc61f2 | note | Acceptance Criteria: SL82 Mesh to be installed with a minimum 60mm cover to the surface. Reinforcement must comply with the requirements of AS/NZS 4671. Reinforcement mesh is not to continue through joint.
d9f9b903-c138-54fb-a5f8-e6a7c1fc95c5 | note | Reference Documents: DWG EW-CE-DRW-416-001 (Rev C) C.10.10
be3fb2d7-4882-57ce-b138-ff6d0bfb8b3d | note | Inspection / Test Method: Verify
7b34dd32-fcaf-5d7e-b0f4-46e524a81256 | note | Record of conformity: ITP Signed
688c6789-7ff6-55f6-bb37-9bbf39b9212b | note | IP
a3b22152-394f-5843-9ba3-24a9e0608a66 | note | Responsibility: Site Engineer
b953ff16-af94-5f87-a9c9-b58d2b1d1bab | date | Date Completed:
| checkpoint | 3.3 - Dowels
34f8bd47-b329-5641-962c-8888351d2bf1 | note | Frequency: Each Lot
989a38f8-d384-50b5-ae85-46bc4c3c0a91 | note | Acceptance Criteria: Dowel bar size, length and spacing along the joints (Section 9.4.6 of Austroads 2017): 24mm diameter, 450mm long Grade 250N round bars at 300mm center to center spacing.
e5c8e84e-e26e-595e-96a3-384ff292d183 | note | Reference Documents: C.10.28 DWG EW-CE-DRW-416-001 (Rev C)
68db0c1f-83b2-5075-a95b-1e38caccf557 | note | Inspection / Test Method: Verify
ca20115f-fa05-5fed-861e-4fcb1221ec17 | note | Record of conformity: ITP Signed
f6f7f92e-9460-5577-9ae1-2b0b5350d6f9 | note | IP
ef950215-8b49-5ed5-9a54-c5ea08d3964c | note | Responsibility: Site Engineer
07dadead-921f-577c-b08d-b82404047c5e | date | Date Completed:
| checkpoint | 3.4 - Tie Bars
c3c96085-c9c2-53f8-8512-cbf72589e0d8 | note | Frequency: Each Lot
92db08b9-9f5e-5c68-9402-8e4004f473c3 | note | Acceptance Criteria: Tie bars should not be installed within a distance of 500mm from a contraction joint. The tie bars are recommended to be at least 1m long, 12mm diameter deformed steel bars. The spacing of tie bars can be determined from the ‘drag’ formula identified in Austroads, 2017.
2d8a082a-6123-5ac3-92f7-8234c65ce404 | note | Reference Documents: C.10.29 DWG EW-CE-DRW-416-001 (Rev C)
bec5ceae-d84d-56f8-9319-16457a5141e5 | note | Inspection / Test Method: Verify
fddb459b-532a-5d19-a9bd-3520dc22b579 | note | Record of conformity: ITP Signed
6352af1b-849c-5761-8392-6cd5949b9504 | note | IP
c1d2aad4-6a62-5222-a268-d971d33d60e6 | note | Responsibility: Site Engineer
d42c0897-9e7f-58d3-a483-01fd15d10255 | date | Date Completed:
| checkpoint | 3.5 - Authority to Place Concrete
eb9c0439-431d-537b-b735-4e3edef0dca1 | note | Frequency: Each Lot
ab6234c5-e452-58d4-9b3c-a2ac0c932029 | note | Acceptance Criteria: Concrete shall not be placed until:
6fe63981-3031-5540-b7db-cb27d917b89f | note | (i) the evidence that the set-out and any formwork or reinforcement is conforming to the requirements of the specification and the drawings and has been reviewed by the Superintendent
a57af6d0-6694-5929-9e22-d36609cc3b7a | note | (ii) Prior to placing concrete, all formwork, equipment to handle concrete, excavated areas, reinforcement and existing adjacent concrete are to be clean of all foreign matter and water.
7211b782-deec-5082-bfc0-812a7fb5662c | note | ○ Superintendent requires 48 HR notice for inspection.
5a810981-de11-5f4e-b5ba-778c5695042f | note | Reference Documents: C.10.6
002cbbdd-1b65-583a-aed3-f2e04b8d9780 | note | Inspection / Test Method: Inspection / Test Method
989ad5ce-88bb-5e38-a892-fc91962b3d54 | note | Record of conformity: Inspection Checklist Doc No: 65473-CI-01A
b632b872-d26e-5c6a-9d68-817e5a609572 | note | HP
9de899b8-1ba6-5c87-af90-1025878a98e0 | note | Responsibility: Site Engineer / Superintendant
52ce5a17-57a4-5548-8264-7849f0dfa8ee | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 3.6 - Concrete Placement
24fdb60c-2e71-5fb8-bc7d-5af6f572a585 | note | Frequency: Each Lot
4a60b116-7c7c-5e34-8886-1023c7bdaf4b | note | Acceptance Criteria: The concrete pavement shall be a 160mm jointed reinforced concrete pavement with a characteristic 28-day flexural strength not less than 4.5mpa
faaa3112-385d-5608-ae8d-840c78c373ca | note | Reference Documents: DWG EW-CE-DRW-406-001 (Rev E) C.10.6, C.10.26
50b2b73d-7762-5485-ae84-0fff8c5139f0 | note | Inspection / Test Method: Inspection / Test Method
9c953d2a-3cb7-57ff-9ee3-dd91de1c03ef | note | Record of conformity: Visual Inspection, doc. No. 64573-CI 01D
f088a660-7571-5483-a49d-43d7da81f089 | note | IP
27c0eb34-c56a-5f1b-a857-0569321b9e0b | note | Responsibility: Site Engineer/ Site Foreman
e47d2cb4-5a11-5be3-b585-b63b36bbe409 | date | Date Completed:
| checkpoint | 3.7 - Compaction
597aa36a-8d1b-5262-b569-709a3708a553 | note | Frequency: Each Lot
6378b077-9fbd-5372-ac09-a193d74a3208 | note | Acceptance Criteria: The entire volume of the pavement shall be thoroughly compacted using vibrators to ensure each load of concrete is vibrated into the face of the previously placed concrete and into edges, joints and around dowel bars and the like.
7ca381b8-7ef4-58b6-892f-2c31a98cf4cb | note | Reference Documents: C.10.7
e875a8a6-20cc-5326-ac8e-8421727b4618 | note | Inspection / Test Method: Visual Inspection
c8738735-24cb-513e-85c8-26bce91a0422 | note | Record of conformity: ITP Signed
6ac66545-1162-5d01-97d4-94660ca76f45 | note | IP
29b450a0-078e-5487-bd86-37236f122d23 | note | Responsibility: Site Engineer/ Site Foreman
e0152096-7aaa-5cf0-887b-65418e83ed05 | date | Date Completed:
| checkpoint | 3.8 - Surface Finish
986a7a9c-0540-5fa9-8fee-58baa87187ba | note | Frequency: Each Lot
1f73d7e7-177f-5b1a-82ed-ae282f594754 | note | Acceptance Criteria: Concrete pavements shall be finished with a steel trowel to a smooth surface at the correct levels, grades and shapes. After trowelling, the surfaces of pavements subject to traffic shall be broomed to form a non-skid surface with the pattern of the lines running in one direction only.
bb3e97e2-62aa-53ac-b23b-152e9a002565 | note | Reference Documents: C.10.12
54220184-1ca8-5f0e-8604-82826ee1e8d0 | note | Inspection / Test Method: Visual Inspection
9ff35224-7913-5046-8220-14d1de5d5556 | note | Record of conformity: ITP Signed
47d18098-5c18-5f05-a8e1-dccb6ddfae5c | note | IP
f4bb45ea-b0bd-54be-b8aa-74a4dbaa3624 | note | Responsibility: Fulton Hogan Engineer
e499f60c-5771-53f3-884b-6d3c9891f3a4 | date | Date Completed:
| checkpoint | 3.9 - Joints
9e7d5ee8-93dd-5309-a858-460eb8300280 | note | Frequency: Each Joint
2a5767fe-c499-55c8-9727-91fda076e57d | note | Acceptance Criteria: Dowelled Expansion Joint
c207d715-1993-55a5-b031-d9ec891ac9f0 | note | ○ Dowelled expansions joints shall be installed for transverse joints at 6m spacing.
c85c8de0-4a5f-5c23-848e-fa3842c78f28 | note | ○ Dowells to be 24mm Ø grade 250N, 450mm long dowel bars @ 300 CTS debonded at one end.
aa44142a-a741-595b-9c18-b75fea116925 | note | ○ Cover from dowels to surface to be D/2 +/-25mm
68f84504-701d-5082-866b-4ced2004c0ba | note | ○ Cover from mesh reinfoircement to expansion joint to be 75mm each side.
91799f6c-37c9-5c9c-a457-18da1c646ec0 | note | ○ Joint to be sealed in accordance with Detail F of NSW transport RMS Standard Drawing DS2014/005559 ED2 Rev 0 (See below)
05f42fb5-b6dd-5f91-9f7b-8062f7d6829d | note | Tied Construction Joint
407d1e0b-6bb5-5628-a243-e3d940879908 | note | ○ Reinforcement to be N12 deformed bars @ 500 cts. 1000 mm long extending 500mm +/-35mm into each side.
a24d74fa-f9a2-5978-9833-3245a4b61101 | note | ○ Joint to be sealed in accordance with Detail F of NSW transport RMS Standard Drawing DS2014/005559 ED2 Rev 0 (See below)
4f361dfa-46f5-5881-9e16-f85c4a89f7a6 | note | Reference Documents: EW-CE-DRW-416-001, NSW transport RMS Standard Drawing DS2014/005559 ED2 Rev 0, See Drawings Below
6acd88f8-b0d8-5c9a-b590-db19d289f4b7 | note | Inspection / Test Method: Visual Inspection
7fc20b90-a45f-5d60-8967-b5bb7f102c66 | note | Record of conformity: This ITP Signed
ea7a6fde-c6fa-5933-aed7-170cfbf203aa | note | IP
5e32f3d1-3c1f-5841-9191-a840be7ac0b8 | note | Responsibility: Site Engineer/ Site Foreman
28f656d9-6523-5352-b034-8fb971bf6193 | date | Date Completed:
| checkpoint | 3.10 - Protection of concrete
8ac24a20-3b70-507e-bc5d-af569b2d93c7 | note | Frequency: Each Lot
d5356151-93a3-5d45-b5ae-b0e994cc7e50 | note | Acceptance Criteria: The finished product shall be protected from damage by passers-by and construction traffic through the use of bollards. Pavement to be protected for a period of 28-days following the last concrete pour. During this period the area shall remain untrafficked.
313b4cb8-f5f0-5fde-a1ad-508cd70978eb | note | Reference Documents: Work Procedure
595136c4-07f3-5c64-bb2c-0b99d9076159 | note | Inspection / Test Method: Verify
b658dcb4-c9a9-5124-a3a9-0329d7ae0a07 | note | Record of conformity: This ITP Signed
7dca49b6-d4e2-5c3d-aff2-c10c5a742614 | note | IP
37966bfe-b01d-52e0-b065-51467754b53b | note | Responsibility: Site Foreman
909f6069-54be-5cb9-964a-888b93f28a6a | date | Date Completed:
| checkpoint | 3.11 - Curing
25f64218-c23d-531c-9c9b-f133e82c5325 | note | Frequency: Each Lot
9b8e053b-f637-5fdf-b6b7-211dc658d3d7 | note | Acceptance Criteria: Approved covering shall be provided to protect the concrete surfaces against rain, hail, dust or any other cause that may damage the concrete during the carrying out of the work. The formwork may be stripped after 24 hours, but sufficient timbering must be provided to protect all exposed edges for at least four (4) days or longer, where in the opinion of the Builder, damage is likely to occur. The contractor will apply curing compound as per C.10.13 of the project specification.
2d82d078-2d5a-52ca-904a-32041d0dc863 | note | Reference Documents: C.10.13
d00cd90d-22f9-508b-ac6d-acd0f24673a7 | note | Inspection / Test Method: Verify
d46377ea-3538-5f68-a156-31f5fe371907 | note | Record of conformity: This ITP Signed checklist doc no: 65473-CI 01E
7e9b6b3a-e411-5771-a8c2-8565ae8d1b39 | note | IP
5e2f3cb3-2691-5890-b4ab-80c90a058304 | note | Responsibility: Site Engineer/ Site Foreman
cfe32d23-15f5-52b8-be07-b6853d063175 | date | Date Completed:
| section | 4 - Completion
| checkpoint | 4.1 - Carry out sampling of concrete - strength and consistency
a8b5f2a6-9f29-5a9e-9c3a-65b9984acb05 | note | Frequency: Each 50m3
5981f594-d9a1-553d-8fb7-dafffba757ce | note | Acceptance Criteria: Sampling and testing of the strength of concrete shall be carried out in accordance with Clause 6.2 of AS 1379.
cd0f06b3-27f1-5cd2-af26-1d7eb167803b | note | Reference Documents: Work Procedure
c71e7d07-da62-58ae-aae6-fa167a8cd8b3 | note | Inspection / Test Method: Checklist
4dd8d909-5e29-5b31-ad03-75287ca88f9e | note | Record of conformity: ITP Signed/Test Records
45133550-5737-5b43-ae9a-0ef796c7a939 | note | TP
719eb82d-cbf5-5ac1-be1e-8370b97230e4 | note | Responsibility: Site Engineer
f914ac24-a48b-5c19-850e-23da9aaaa2d9 | date | Date Completed:
| checkpoint | 4.2 - As-constructed survey and conformance documentation
21ebd102-9ebd-53d4-b182-36e7e75e206d | note | Frequency: Each Lot (1 per day)
4ec90f8c-8f41-58a6-8302-0fba5714e94e | note | Acceptance Criteria: As-Built Survey Lot Maps shall be completed to show the extent of works for each lot.
7f0bd119-9d23-5bc4-85a0-8df75d90857b | note | Reference Documents: Work Procedure
a50a053c-4f4d-5cf3-8d2c-6e7cc0f1cf53 | note | Inspection / Test Method: Verify
549013d8-0d86-54e2-b303-66a44410f5ae | note | Record of conformity: Visual match existing / This ITP signed off
5c07fd13-6985-5cd6-9a68-2c66732ad201 | note | SCP
da29b892-abba-58e5-8031-1a8d5af98619 | note | Responsibility: FH Engineer/ Surveyor
73568047-0bf0-50b2-8e52-2906a1de12c9 | date | Date Completed:
| checkpoint | Final Inspection
da6ef5bd-9b4c-59fa-b4a5-442b8a4ca0fe | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
0cc90c16-1ba3-5ca4-b632-74f29057fdf2 | textbox | Print Name:
a4f6f82e-b45b-5766-8b02-fdc6dc57e01a | textbox | Position:
30ba9e31-37bf-5f87-9a1d-e9e54141ce40 | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-018 - ACO Drain Install | itp | GT4-ITP-018 - ACO Drain Install | f0bd4940-e12d-453e-8a42-e35e8a0806ee
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check for correct documentation
580d9e4d-b114-544d-9b00-0db77a8f0447 | note | Frequency: Prior to commencing any activity
1955e9ef-be41-51cf-aa09-86753dcf59b9 | note | Acceptance Criteria: Ensure that all employees and subcontractors are:
3906f6ba-0ece-58f4-a8d2-8a9046032dd2 | note | – using the correct and complete set of drawings
9eb96d81-51d7-52d4-9555-ef5dbc72a684 | note | – all drawings are the latest revision
2062015b-20ae-590e-8c7a-dd7f91688e0e | note | Reference Documents: Drawings and drawing registers
f8455431-6c9c-5565-9010-ff3edc6c5e94 | note | Inspection / Test Method: Visual inspection
61a9b8c9-935d-52c8-870e-830436abb31f | note | Record of conformity: ITP Signed
ae63120e-d04c-54c2-b2c2-357602ff2e6d | note | HP*
ce3754b4-2616-57f3-91e0-176ac0bc90ef | note | Responsibility: Site Engineer/ Site Foreman
f06d8533-c8f8-5c0a-9a9b-fdcdfcda418a | date | Date Completed:
| checkpoint | 1.2 - Implementation of all measures and controls
22c0ab84-e9cd-5b41-a547-d9e1f8efafc5 | note | Frequency: Prior to commencing any activity
f3670592-ad45-52f7-8fe2-b711bb5134a7 | note | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WP
2246c6f9-30df-5a86-bf5e-d87a05d36892 | note | Reference Documents: PSP, EMP, TMP, SWMS, WP
47581a7f-4657-51de-b208-b96e82c3ff83 | note | Inspection / Test Method: Visual Inspection
68870950-4a47-5d43-ac20-eb13d397be94 | note | Record of conformity: ITP Signed
fecf5007-d38d-5765-9a53-f0ddb26e9196 | note | HP*
9f3f1250-e979-5f25-adcd-8e99ba6cdfe0 | note | Responsibility: Site Engineer/ Site Foreman
8cc5b3f5-7607-5afb-ab64-ac0ae59509ba | date | Date Completed:
| checkpoint | 1.3 - Submission & Approval of Concrete Mix Design
903f5f12-7963-5fa9-8796-adc40c207ed1 | note | Frequency: Prior to first concrete pour
ce681f55-74bd-5572-8c81-2101ade13a28 | note | Acceptance Criteria: The Contractor shall submit the concrete mix design details for review by the Superintendent not less than 4 weeks prior to the placement of concrete. Concrete shall not be placed until the mix design has been reviewed by the Superintendent
ae8f4eac-bc93-53fc-87d2-5ee8c6e80096 | note | Reference Documents: 610.07(b)
3684398f-0a56-5ae4-a4d4-77473c1db3cd | note | Inspection / Test Method: Verify
5a7467f9-a834-50a0-95a7-74f9ab2aa7d0 | note | Record of conformity: ITP Signed, Mix design approval
e9fde53f-edc2-5abe-9ae1-b19c5f8f8436 | note | HP
deb7c051-081a-56df-a7c5-87d603c85da0 | note | Responsibility: Site Engineer/ Superintendent
59992b01-6bb4-54ca-8229-cdc72ca2fe7d | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 2 - Construction Works
| checkpoint | 2.1 - Setting Out
eb72fed0-a3fd-5f1c-b8da-bcaab8d1f729 | note | Frequency: Prior to start
d1c9840c-69ba-553c-9955-732f15a5937c | note | Acceptance Criteria: Set out work in accordance with drawings. The superintendent will review and confirm set out. The alignment and survey/level pegs will be indicated to the Contractor on the Site by the Superintendent prior to the commencement of work. No survey/level pegs to be removed by any persons until completion of works.
3e50060e-52d3-568b-85fc-6330b6f264b8 | note | Reference Documents: 703.17
b0d6f99b-72b5-5ad5-a97a-3a7b9453ed01 | note | Inspection / Test Method: Verify
3f9237ea-de30-5662-9458-7c0af69a8832 | note | Record of conformity: This ITP Signed
3df1f12f-badf-541b-be3b-82884e9cdcce | note | HP
4c6c4ae3-67ef-5c81-8ed6-5fbeafdb1b1f | note | Responsibility: Site Engineer/ Superintendent
118b374b-a5c7-5534-8877-9a3b6f295080 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 2.2 - Excavation Permit
0205923e-9847-525d-b70e-4c238ff0a327 | note | Frequency: For Each Day of Activity
32b93545-62d7-528c-a78a-894984ea5eac | note | Acceptance Criteria: An excavation permit must be issued prior to any excavation commencing. Plant and equipment shall be appropriate for the task.
e5dcaf1d-6637-59a8-8a81-4988253c29d1 | note | ○ Excavation operations shall not disturb areas outside the limit of excavation
6f8bd2d7-46fa-5e51-b8ac-8656052c6aa2 | note | Reference Documents: Excavation permit
f6658c0e-bb89-54c7-b464-5b2fe6d21b9f | note | Inspection / Test Method: Verify
2967a763-f52b-541f-867e-9852b752c6cd | note | Record of conformity: ITP Signed
251c6f16-4c15-5d2d-87e8-dcff00eef69f | note | HP*
0a411ed1-7ce5-5e19-bf22-fa81f411cff5 | note | Responsibility: Site Engineer
9e2fbcf5-303b-5df9-9754-6c28c12a0428 | date | Date Completed:
| checkpoint | 2.3 - Excavation
b576a9f0-40e7-5adf-bc46-58de8402983f | note | Frequency: Each Lot
8590d9c2-e360-5b6b-b6fd-2c6e64053a64 | note | Acceptance Criteria: Excavation completed to required depth to allow placement of the concrete blinding layer.
54cca9cf-0e37-5850-b73e-ef7c967927ef | note | Reference Documents: 703.2
407a23f1-d26c-51ec-bf47-9a653807c2e5 | note | Inspection / Test Method: Verify
0dcf6398-7518-5378-af7c-ae2b8dff5737 | note | Record of conformity: ITP Signed
e130bf35-fd64-5750-bb94-e6fef21133b6 | note | IP
1ed6ee05-76fa-5cf2-9607-9790ceaf4aae | note | Responsibility: Site Engineer
31db3681-ee5d-5060-892a-f7a2d792445f | date | Date Completed:
| checkpoint | 2.4 - Dowel
632bbcad-4dbe-58b4-8b9b-2c5303d716ed | note | Frequency: Prior to concrete pour
74818511-a768-5d88-a32c-cd50e4fae6d6 | note | Acceptance Criteria: 12mm Diamond dowel at X centres
72b798de-12a0-531f-9efe-7231cb9bdff1 | note | Reference Documents:
90fe478d-eba9-589d-a4f3-5bf2cfb416e0 | note | Inspection / Test Method: Verify
a8d112e3-493a-58dc-babc-73291c7c4caa | note | Record of conformity: ITP Signed
50b6a1cc-e758-5d4e-bebb-d4f40945c9bb | note | IP
471748a3-1c80-5768-91eb-9e7261d2be2e | note | Responsibility: Site Engineer
614aa4a1-04de-54ec-9781-668d44866bd2 | date | Date Completed:
| checkpoint | 2.5 - Bedding
5c657448-bba9-573b-8568-01986b39ef98 | note | Frequency: Before placement of ACO DRAIN sections
afd0f378-ab2f-5be5-bd9e-e4234d6cb79b | note | Acceptance Criteria: 150mm concrete blinding to base of proposed ACO DRAIN.
7a023d8f-248f-5d47-bc38-db347949e36a | note | Reference Documents: Trench grate joint detail with concrete pavement
14c25fb8-dd94-5bf7-ad72-82b940fbc0b0 | note | Inspection / Test Method: Visual Inspection
abb87fbe-96ee-56e1-8bb6-5ceab95d5b2b | note | Record of conformity: ITP Signed
b809f15e-327c-5572-9689-12c1996bcf15 | note | IP
4b134abf-0f14-585e-b4ff-b00575690164 | note | Responsibility: Site Foreman
95365525-96fb-5c66-80a9-f06a0782250d | date | Date Completed:
| checkpoint | 2.6 - Formwork
dc41d5ee-01e0-5efc-997c-658f2f502fc3 | note | Frequency: Each Lot
7a1aa597-aff9-56c1-9d72-d55b3de326c0 | note | Acceptance Criteria: Formwork shall comply with the requirements of AS 3610 where required
98d6ea38-33d0-5039-89c0-db8745b604f9 | note | Reference Documents: 703.12, AS 3610
42490b7c-17ab-5b3c-ad72-93ce8240cd2f | note | Inspection / Test Method: Verify
6e4fa9a3-0c4f-5448-aa63-718f74ffcedd | note | Record of conformity: ITP Signed
24be9320-0443-5c23-922d-8d85526ced14 | note | IP
775bb5fa-7452-534e-9698-645f463849fd | note | Responsibility: Site Engineer
f95a9ed3-0b0f-58f9-a2ab-437693aef4d6 | date | Date Completed:
| checkpoint | 2.6 - Expansion Joint
fba6a9a7-51f9-5658-b2eb-4873a639b5ee | note | Frequency: Prior to concrete pour
314b35e9-989d-593f-bf5e-279c4a5a8d55 | note | Acceptance Criteria: 12mm Abelflex seal with approved sealant against existing and adjacent concrete pavements
6ab09bfb-46a3-503b-b5fe-d2d41cc3fafd | note | Reference Documents: Trench grate joint detail with concrete pavement
f2a5a0e2-fa7a-525f-bfc1-fddc3e3127d1 | note | Inspection / Test Method: Visual Inspection
eb918f6c-1603-5305-a523-f02817366e5c | note | Record of conformity: ITP Signed
de13a996-d181-5441-84da-0c5bbcf2b220 | note | IP
c130d1f7-d965-5cda-a7e8-e7c8884ea98b | note | Responsibility: Site Engineer
8a8b55d8-74f7-5292-82c5-8da9a2e6bd39 | date | Date Completed:
| checkpoint | 2.7 - ACO Drain placement
55341a9e-28b3-52f5-be1a-77df6d983c83 | note | Frequency: Prior to concrete pour
787f9ccb-fc98-5f79-a3dc-05adf9f070a3 | note | Acceptance Criteria: ACO drain sections to be placed in trench with lid surface flush with adjacent pacement surfaces. Ensure a 150mm width either side of ACO DRAIN to existing pavements.
783c77b0-c537-5632-9a21-07837557527e | note | Reference Documents: Trench grate joint detail with concrete pavement
4ae03229-5ff4-5265-9644-b01c7bcc5905 | note | Inspection / Test Method: Visual Inspection
444cfeb2-0ed4-5fb9-8449-b28897bd230d | note | Record of conformity: ITP Signed
a7e6c224-cfa3-547f-b57b-07aac45dac14 | note | IP
5e228067-4588-5f63-a785-b81a5aa84f7c | note | Responsibility: Site Engineer
4d7cbeae-851f-5038-8946-adcc8f0597ac | date | Date Completed:
| checkpoint | 2.7 - Concrete Encasement
b60eba86-f277-5a1d-8eba-14fdf214dd3c | note | Frequency: Each section of ACO trench
f707a3e1-0421-5f42-a3e7-7927cf040d33 | note | Acceptance Criteria: Concrete shall be thoroughly compacted via contious tamping and internal vibration. Where concrete is unformed it shall be hand tamped to a smooth surface and screeded in accordance with the construction drawings.
049643d5-b102-589a-9a47-be707519e358 | note | ○ Where fresh concrete is being placed against concrete which has taken initial set a properly formed construction joint must be used.
0447abbb-3093-5be5-82fc-84077f05bf0a | note | ○ N25 concrete as per installation drawing - ACO Drain
63785172-2f18-550f-93c9-fd5875be4c91 | note | Reference Documents: SPECIFICATION CLAUSE KLASSIKDRAIN K200 - LOAD CLASS A-B
ad93be38-55b5-5181-8550-182d53bfd201 | note | Inspection / Test Method: Visual Inspection
e7e8ac53-38bd-5676-b29a-8820a2a3d178 | note | Record of conformity: ITP Signed
46450159-fc8c-5f4c-9ddd-cf575caab5e5 | note | IP
9eb7f84a-fec6-5405-b295-9be2565296e1 | note | Responsibility: Site Engineer/ Site Foreman
2f9f5350-2b6c-5c42-ae3e-916673e12676 | date | Date Completed:
| checkpoint | 2.8 - Record location of each batch
c1ca6968-d59f-5719-a422-e154510253c7 | note | Frequency: Each concrete pour
9a5602b7-baba-57b2-a66f-9c491443e308 | note | Acceptance Criteria: Batch location recorded on Load Batch Traceability Checklist
34477c49-8386-5d91-89ff-7eaf9935bc03 | note | Reference Documents: 610.15, CL001D
b6fd134a-8f0b-5b9b-9063-574490e8cb9a | note | Inspection / Test Method: Checklist
6f0e9af0-f1ad-5c27-90bf-7afd42164a4c | note | Record of conformity: This ITP Signed
47de3eda-68bc-53d1-b729-35a80d3148fe | note | IP
c7b58748-08f8-5069-a9c4-e7f5822ac684 | note | Responsibility: Site Engineer
531f47da-cc16-5948-9001-b999b1309781 | date | Date Completed:
| checkpoint | 2.9 - Surface Finish
d721550b-fb42-5da9-808a-bfa366d57e3c | note | Frequency: Each Lot
d3ecbe23-37ff-5cda-913d-56ed5637f253 | note | Acceptance Criteria: Concrete elements shall have a Class 3 surface finish for external surfaces and a Class 4 surface finish for permanently hidden surfaces in accordance with AS 3610.
ecb1b753-80b9-5ac8-a23c-faf1d594dbe7 | note | ○ Footpaths and other Surfacing shall be compelted with a wooden float.
b07534e2-e790-5825-ab11-b37e4515c92a | note | Reference Documents: 703.25
d54e2285-8232-57ef-aca1-c2bcfb5f9a23 | note | Inspection / Test Method: Visual Inspection
95588e93-7621-5bfa-b238-a383054e29c3 | note | Record of conformity: This ITP Signed
32ab0b41-9733-53af-b7d9-2f4d2a6de8b1 | note | IP
8e829ab7-e3aa-5ea1-8c4d-87e86786d62e | note | Responsibility: Fulton Hogan Engineer
1eddc6b8-6e2e-5f86-b1c3-1431adccf018 | date | Date Completed:
| checkpoint | 2.11 - Joints
5400931f-2234-5601-99d6-cea7e8a6bbbd | note | Frequency: Each Joint
3d517eca-7a21-5fb3-a80a-7c75c52fe415 | note | Acceptance Criteria: tool joints to be formed at each ACO joint.
3504b891-6087-5196-afa5-257198eb8cd1 | note | Reference Documents: SPECIFICATION CLAUSE KLASSIKDRAIN K200 - LOAD CLASS A-B
eb43cf2c-7bc3-540a-8f04-aa3887cf2ca5 | note | Inspection / Test Method: Visual Inspection
a7317dcf-ebc5-5f7b-9cf9-3036187254e6 | note | Record of conformity: This ITP Signed
0663c4bc-2173-5a27-8240-125a91965e3b | note | IP
2b308bca-8e79-562e-a09b-f7567eeae377 | note | Responsibility: Site Engineer/ Site Foreman
2091337e-a08f-5b73-96ff-0ec8641d0a57 | date | Date Completed:
| checkpoint | 2.12 - Protection of concrete
b7f7ab95-c77a-5ee0-9b6a-5b5c962fad46 | note | Frequency: Each Lot
8e525b56-c29a-5d5d-a774-db1b2ed6116f | note | Acceptance Criteria: All concrete shall be protected from damage from early loading by pedestrians, animals, vehicles and from rain or any other cause.
d8520868-464f-556e-93b3-79c69be4c706 | note | ○ Vehicles equal to or less than 1.5 tonnes in weight may be permitted to cross after 4 days, vehicles greater than 1.5 tonnes may be permitted to cross after 7 days.
ca7c5cd7-a5e6-5da9-aa62-35fd1e53a8bb | note | Reference Documents: 703.27
bd1fa59a-815b-5332-88e5-c199ba3119f4 | note | Inspection / Test Method: Verify
afac45e1-c80c-5173-a721-f349dd8ca80b | note | Record of conformity: This ITP Signed
ded48f9c-b070-5962-9bad-7ad40241af6e | note | IP
608af33f-e8e4-5cc3-bb52-8fc691ed7842 | note | Responsibility: Site Foreman
4842259f-0908-5227-b6a8-912659c8a367 | date | Date Completed:
| checkpoint | 2.13 - Curing
66d659a7-4d55-5a3c-a4b6-bf0f60b98cd6 | note | Frequency: Each Lot
87a6a39d-5e07-5fbb-8e34-3790ddb3427e | note | Acceptance Criteria: Concrete shall be cured immediately either by water curing, wet hessian, polyethylene sheeting which is adequately sealed, curing compound or a combination of these.
67c9bc73-1ef9-5d2e-9889-3ab148a390e6 | note | ○ Curing compounds shall comply with AS 3799. The curing compound shall be applied in two coats using a fine spray at the rate stated on the certificate of compliance
2f61c109-3f26-58fe-b745-f97663c13d36 | note | Reference Documents: 703.1
e1d24749-9861-5b8f-aa59-69c04911df68 | note | Inspection / Test Method: Verify
23eb7b35-ebf2-5329-92af-22ef74dc8321 | note | Record of conformity: This ITP Signed
85f2050a-36cb-55cc-879c-6102946742e8 | note | IP
9ba7f7a8-6ce7-5d5b-bcd1-0f3c813d46f2 | note | Responsibility: Site Engineer/ Site Foreman
10b8ae58-c270-5861-94a5-13e7feab06b8 | date | Date Completed:
| section | 3 - Completion
| checkpoint | 3.1 - Carry out sampling of concrete - strength and consistency
c0e89b59-96f2-546c-8432-d1773e3db946 | note | Frequency: Each 50m3
80f38aaa-1ff1-55ec-a6c4-34229695750e | note | Acceptance Criteria: Sampling and testing of the strength of concrete shall be carried out in accordance with Clause 6.2 of AS 1379.
0e7d3c4d-2ba9-5df8-a178-2478f6c7c1fd | note | ○ The consistency of the concrete shall be determined by a slump test of each concrete strength sample in accordance with AS 1012.3 and Clause 5.2 of AS 1379
8d32aa85-752b-5441-b8a0-c1cbec83b94c | note | Reference Documents: 703.11, CL001B, CL001C
2aa0c2ad-f903-5277-8b7a-52bd7a3b0b73 | note | Inspection / Test Method: Checklist
807533b0-79ef-56fc-9fee-6343aa56f43f | note | Record of conformity: ITP Signed/Test Records
079fd7d4-55cd-5c55-9d78-fa905c4f7b8b | note | TP
b9e6b889-2ce1-5d99-b324-819faeadde80 | note | Responsibility: Site Engineer
e071d8d0-1377-563d-9121-1ee1fe50ed0f | date | Date Completed:
| checkpoint | 3.2 - Tolerances
0698db62-c925-5195-ad82-e6f925cb8ef6 | note | Frequency: Each Lot
3f18fb2c-912f-5b0b-bed7-22c7a499f151 | note | Acceptance Criteria: Where matching in with existing surface levels, the new surface shall be within ± 5mm existing.
2aedcb6a-8477-50b8-bcf5-494dd02a2daa | note | Section dimensions shall be constructed within the following tolerances:
518ed71b-abd2-57c1-b32b-25d33bc59b23 | note | ○ 5mm and 15mm for width; or
361fa4d4-726a-5477-adea-6a20ef39da09 | note | ○ ±3mm for dimensions less than 25mm.
897f0427-323c-5d7d-968d-cf0fff28af58 | note | Reference Documents: 703.15, Drawings
e6dd27aa-592f-52e1-88ef-1f16eab30048 | note | Inspection / Test Method: Visual Inspection
78413da0-58af-5242-9eac-8cc57b4d592b | note | Record of conformity: This ITP Signed
7264ee0c-0533-529c-b1cd-c946787c70f1 | note | IP
57d75253-49e8-5a87-9d02-99a7f828ddca | note | Responsibility: Site Engineer/ Site Foreman
f3087c0e-fc53-55df-b80b-840b2d619924 | date | Date Completed:
| checkpoint | Final Inspection
9a3061a7-695e-5634-b7ef-a8adb1da2cf2 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
2be25ce2-63b5-5dc9-b79e-a28338975e82 | textbox | Print Name:
1548a836-1f09-5366-ba68-673e92e43460 | textbox | Position:
f2881ab9-5c7c-52dc-bcca-35e06da5457b | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-019 - Fire Services | itp | GT4-ITP-019 - Fire Services | 451cc426-4bce-4f2a-8ef5-fdc89c3f37a8
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check that current revision drawings are being used
fe20a117-5b1c-5402-85cb-82813fac8b96 | note | Frequency: Prior to Commencing Work
79ecc4d3-0de1-5a32-9d83-15856fc59ad5 | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
5de14894-3697-5d43-8332-89538858a398 | note | Reference Documents: IFC Project Drawings/ Drawing Register
244057e4-1b06-522c-8942-0d78f7fd7886 | note | Inspection / Test Method: Document review
a89cdb15-a5fe-5761-803e-3f8dbde3d015 | note | Record of conformity: Latest revision IFC drawings
fd14528c-bca0-5006-861e-58f7da80e741 | note | *WP
be99f18e-7f19-5055-8184-c684d9f92aab | note | Responsibility: Site Engineer
4511c637-b3c1-5ebd-b0eb-501e1135a87f | date | Date Completed:
| checkpoint | 1.2 - Confirm understanding of current EMP related to the work area and that all prescribed environmental controls are in place
0e4b6266-7b11-51b3-ae30-1a64261cb82c | note | Frequency: Prior to Commencing
fefd8610-f8c1-513c-b8f0-7f1af713a63f | note | Acceptance Criteria: All environmental measures to be implemented as per current CEMP and local authorities. Sediment control measures to be installed and protected vegetation to be clearly identified
aba1c803-b319-5561-9e24-6ac3b31aee84 | note | Reference Documents: CEMP, Site induction
5c7090d1-3017-5876-aeac-c866d027b90a | note | Inspection / Test Method: Document review & Site inspection
96b4bf66-044d-5005-8982-cf6bc6d98f35 | note | Record of conformity: ITP signed
e33b83a4-b5f5-5ed5-bdfe-128dafb5e303 | note | *WP
c1c196e9-3c07-5d66-9cfa-9ea8d87bb2b6 | note | Responsibility: Site Engineer
fc53da6c-04ec-5905-9b78-74225aab10f8 | date | Date Completed:
| checkpoint | 1.3 - Traffic Management (When required)
3041f5f9-1c41-5164-93b0-48b7726d78d8 | note | Frequency: Prior to Commencing Work
28b47d2c-ec96-5b12-9c1f-3ff8bd37f8ad | note | Acceptance Criteria: Approved TMP and WASIN (where required)
2246883b-628a-5954-9d44-06ca2ab7effd | note | Reference Documents: Applicable TMP
6ca6a4a8-9696-535f-8d5a-a7c2a91ae057 | note | Inspection / Test Method: Document review & Site inspection
cadd008d-10e3-5c0a-856f-be02bb043616 | note | Record of conformity: Approved TMP
bf798040-569d-51a6-9694-5d7dfc3c8ec3 | note | *HP
9baaf27d-3cf5-5ae5-a1b7-457199f3a2dd | note | Responsibility: Site Engineer
be5612c2-a730-5757-9fb5-c15cd857eee5 | date | Date Completed:
| checkpoint | 1.4 - Survey set out works
51065493-00f0-5e0a-8e4e-8f5a5a3fbb2d | note | Frequency: Prior to Commencing Work
74f9294e-6639-51df-af61-571c4cf5a012 | note | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
7f8abf5b-367c-5ca5-bd5c-b920393dd2b2 | note | Reference Documents: IFC Project Drawings
683f11d8-22e2-5c60-9415-250d9e112da9 | note | Inspection / Test Method: Site inspection
e94c7dd9-1990-53b1-ac10-0450977906e2 | note | Record of conformity: Survey records & marks on the ground. This ITP Signed off.
5cb995cf-5902-57a1-bd2f-c9c5e3622db1 | note | *HP
7c49fe5e-9e3f-53af-8449-99f65231c471 | note | Responsibility: Site Engineer / Surveyor / Superintendent
8eeffb7c-0277-5ac5-9f52-05351cdb79ca | date | Date Completed:
| section | 2 - Material Conformance
| checkpoint | 2.1 - Water Pipes, Valves and fittings
be64df47-7139-55cc-9cc6-2e7c52bb62e2 | note | Frequency: Every batch of new material
5e9e0226-0f6b-5ea7-930d-78486d556bc4 | note | Acceptance Criteria: Fire Service pipe material to be free from defects and meet the following schedules
b3674d48-b2c5-5129-be21-f7f1bcc1e510 | note | ○ As per B.6.1 Fire Pipe Schedule and B.6.2 Valves and Fittings Schedule.
07c42b30-cb7c-5b68-b356-6f6281d0df40 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
63565097-6500-56f1-841c-e8a9e86bede9 | note | ○ B.6
382c7200-df3b-5d9d-9106-677d4f744ab2 | note | ○ C.6.9
c98b0a7a-6f48-50b0-bfc6-555a902004f7 | note | ○ C.6.10
0cdc05a1-2206-5265-8c89-975e4ff68048 | note | Inspection / Test Method: Verify
4b44253d-415a-5f24-8afa-454ebb4dc7ce | note | Record of conformity: ITP signed, Receival Inspection Checklist
18556bea-4e99-5db4-8099-f7de0c62c668 | note | IP
3aae03b7-80a8-5e34-95ac-33062e5a60e3 | note | Responsibility: Site Engineer
d1164b69-4e59-5031-8e56-0d15d9396ba7 | date | Date Completed:
| checkpoint | 2.2 - Correct embedment / backfill materials onsite
af011ab3-a8ac-59e7-9791-9826613fa5a1 | note | Frequency: Every batch of new material
4dc1ba5e-3438-5dbc-8822-076336e99d1f | note | Acceptance Criteria: Inspect bedding and backfill material to ensure suitability. If watermain is to be protected, use stabilised sand or concrete encasement
681bb129-98b0-57d3-b25f-088470acfc4c | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
ca02794e-a573-51de-9dda-64c28224e32a | note | ○ C.6.10.2,3,4,6,
ee459637-8803-5f41-8792-cf535029ec91 | note | ○ Drawing(s): EW-FP-DRW-00-0001
9b4ecf92-dd9f-569b-94b5-9ca617aebe92 | note | Inspection / Test Method: Verify
44d15a4f-f2a8-5606-9c4b-5f85fa2aec8b | note | Record of conformity: ITP signed, Receival Inspection Checklist
662c134e-cb54-5899-8d01-46e9e66833b7 | note | IP
080b226d-1d6a-5157-bae8-aded8fc048a8 | note | Responsibility: Site Engineer
e2c554bd-6d15-567e-a5e3-45ea17e5b174 | date | Date Completed:
| section | 3 - Excavation of trenches
| checkpoint | 3.1 - Trenching details
7db01806-c57c-57a4-970c-eb3ab508a737 | note | Frequency: Ongoing
5f6a74f9-c338-539e-8e6f-9c7c2453d903 | note | Acceptance Criteria: Trench's to be excavated to conform with IFC drawing details.
2bf23a61-9187-58d7-b6cd-11cfed426bd6 | note | ○ Ensure trench width and depth are within tolerance
18f1fdad-e2a3-570e-a479-80ab49a57471 | note | ○ Ensure trench foundation & wall firm, stiff & suitable
22c0a7c4-dafb-5025-850f-db9c2e6c7134 | note | ○ Provide minimum clear space of 100mm between pipe and trench face
6aebe822-0ca4-5e8f-9ae2-d70714166b23 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
9fb89825-d2e5-5ff9-9891-b0c77f8e98ee | note | ○ C.6.10.3
f98efb34-2db9-5665-97cf-3dbdc758f484 | note | ○ Drawing(s): EW-FP-DRW-00-0001
1cb7b107-3ec9-5402-9e42-990e58d20a5d | note | Inspection / Test Method: Verify
9580d0a3-93ff-5103-81b6-07f503678d39 | note | Record of conformity: ITP signed
456af881-cd78-5137-81ef-8dc5cf396014 | note | IP
7fe159de-6d9d-5321-8bb7-67329b687040 | note | Responsibility: Site Engineer
0e0bf588-25d1-5c66-b533-d4866da28779 | date | Date Completed:
| checkpoint | 3.2 - Benching & shielding (where required)
8fd98b77-6d49-5a63-b0d4-a6919d34ac06 | note | Frequency: As Required
203f6751-e104-500d-8ad4-9d7bbc21276c | note | Acceptance Criteria: Trench support is required where the trench is more than 1.5 metres, unless the trench has been assessed as safe by a geotechnical engineer and written confirmation provided as such.
e18220f4-8a9a-51cc-b720-b5f685fbb526 | note | Reference Documents: Work Procedure
74b6040f-77c5-5bce-87bd-77227c2c9cab | note | Inspection / Test Method: Verify
0363c114-0250-58fe-918c-056144b3d42b | note | Record of conformity: ITP signed
21c68861-fe5f-5572-a302-d127d3df55c0 | note | *HP
f69ea600-7fcc-5f90-9527-28a2c09d2913 | note | Responsibility: Site Engineer
ef496f1e-c7bc-581f-94e0-f96e24e05ae8 | date | Date Completed:
| section | 4 - Watermain Installation
| checkpoint | 4.01 - Bedding
6b2eb7aa-edcc-52a2-b75c-e330474f3443 | note | Frequency: Each Lot
67e8f83f-7144-5555-a43d-37500c732c47 | note | Acceptance Criteria: Bedding materials : 7mm single sized aggregate used
e682b094-f844-5e82-a8b3-1b34640e3d22 | note | ○ Bedding Depth: 75-100mm COMPACTED DEPTH, BEDDING MATERIAL INCREASED TO 150mm WHER EEXCAVATING IN ROCK
cf594eb6-ae9b-5cca-baab-857df422f02d | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
2f592918-ec44-59b1-8773-a5bf6b3923aa | note | ○ C.6.10.5
58ee087b-47b5-55a3-a4b0-376adf0d0e34 | note | ○ Drawing(s): EW-FP-DRW-00-0001
dc049500-eea2-528a-a1d9-92d8b6175014 | note | Inspection / Test Method: Verify
3b06adeb-83e3-5f39-8465-fdf9b54cdcf7 | note | Record of conformity: ITP signed
fc0d4f2c-4e4a-5acd-bb23-34734a21a8c8 | note | IP
3f3d1051-03f2-5ac2-861a-01dec0d8cb7f | note | Responsibility: Site Engineer
59968dc0-ee53-5db7-a622-bec296236019 | date | Date Completed:
| checkpoint | 4.02 - Pipe Joints
ee9e89b9-652a-539a-ac0a-c0cb753d1670 | note | Frequency: Each Lot
9fe08f65-9094-5f99-8a0c-c0c9fe381806 | note | Acceptance Criteria: Ensure pipe joint deflection is acceptable, as per drawings and product specifications. Ensure all Butt Fusion Welds are completed are correctly (butt fusion weld indicator showing).
e84af0da-cd9c-501e-8f7f-ae6574f4766a | note | ○ Prior to completing any works on existing infrastructure, ensure line is isolated.
96d1d11e-9fbe-5e42-8785-661b1211862e | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
c4aadf08-664a-5511-85d6-c3483ad61bdd | note | ○ B.6.1
119f4005-66c0-5b11-a3eb-b3148e5e416c | note | Inspection / Test Method: Verify
0c30de36-3f23-5f0e-9aaf-167d557cf48d | note | Record of conformity: ITP signed, photo of each joint
f362817c-f629-57cf-97cf-a09265ba7ba0 | note | IP
c9eb1956-9984-5c64-9e4d-af0906a5a92c | note | Responsibility: Site Engineer
dcba3858-b46a-56bb-b701-f78450c1bec9 | date | Date Completed:
| checkpoint | 4.03 - Pipe Embedment
c2680072-528f-5813-b64a-a8c5f05f8dc9 | note | Frequency: Each Lot
b0cbb252-a2a1-5408-8b25-27a30b640c55 | note | Acceptance Criteria: Horizontal alignment of a completed length of pipework is laid beneath areas of normal usage but where passing under areas of vehicular traffic must be subject to a minimum cover of 750mm or as otherwise directed
383589fd-18bb-5c26-82a4-a9c053deed81 | note | ○ A minimum cover of 450mm and 750 mm for pipework must be provided under unpaved and paved area respectively
9d44dbbc-3ce0-5eed-9661-f868ddfce84f | note | ○ 7mm Aggreate in Embedment layer.
7df5267b-3b8e-53ec-8404-bea89674a462 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
90f16944-6801-5b5a-b047-8b8b1e62a855 | note | ○ C.6.10.1,3
d6e61cc8-8ecb-571b-b416-251fc6f56cd0 | note | ○ Drawing(s): EW-FP-DRW-00-0001
5dd046b7-f827-5efc-8bac-7263646863ab | note | Inspection / Test Method: Verify
db471a76-7def-5ba8-914c-0c158764d7b5 | note | Record of conformity: ITP signed
8c8c77c5-81c5-5933-8722-90635b5b8060 | note | IP
1fbac24d-a48b-5ac8-8688-35cc65afe6ef | note | Responsibility: Site Engineer
33a0357b-1af8-5a9f-95a3-6af5084caa21 | date | Date Completed:
| checkpoint | 4.04 - Survey pickup of Services
14291f4a-4305-561b-82c6-6cc55e591c46 | note | Frequency: Each Lot prior to Backfill
a2d68b8b-aae5-54df-918b-707a014048de | note | Acceptance Criteria: Survey pick for As-built to be completed prior to Backfill
9eb93200-0c4d-584d-a814-44085ee03078 | note | Reference Documents: Work Procedure
660c7f1e-0082-5d48-91f6-5ad2b3bd5b04 | note | Inspection / Test Method: Verify
1b894ac2-3b4b-5730-b2ee-5efa877696f7 | note | Record of conformity: ITP Signed
26f24f5d-85c3-570f-ae91-0969fe217f1d | note | *HP
5d991b11-1137-5a1a-880f-a461f2dc4956 | note | Responsibility: Site Engineer
a31af065-0eaf-5a00-9d71-5e1ff8c117a0 | date | Date Completed:
| checkpoint | 4.05 - Pipe Backfill Material
d3762bb8-f686-54b9-a7a6-c40cf4c3cfeb | note | Frequency: Each Lot
9fbe1eef-a6a0-5ce2-82fc-8f2395e3fcc7 | note | Acceptance Criteria: A compacted sand bed of 75mm minimum thickness over earth or 150mm minimum thickness over rock must be provided. The pipework must be topped with 100mm minimum thickness of sand compacted carefully by watering and hard or light vibratory tamping to a dense tight state.
c6633423-f91e-5e64-861a-3b05e0697432 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
a442d1b6-c1b7-5ea1-8ab6-35e4da660f79 | note | ○ C.6.10.2,3,4,6,
744880a9-b17c-53d9-b2c0-cfec1c0d0aac | note | ○ Drawing(s): EW-FP-DRW-00-0001
24648b47-4e1d-5fce-9446-3e02775b0e02 | note | Inspection / Test Method: Verify
bafb2187-857d-51a6-982d-97f7dcba4458 | note | Record of conformity: ITP signed
3572af77-eac7-50ef-888e-1ab85b5bea59 | note | IP
11b084ee-4669-569e-99a2-e705db5fb088 | note | Responsibility: Site Engineer
1afa66f8-438d-52cc-9b17-fddbc798f77d | date | Date Completed:
| checkpoint | 4.06 - Pipe Backfill Compaction
4c10e041-f6d2-5a0c-9452-d0691d9be6b1 | note | Frequency: Subbase one test per 1000 sq.m
23f95f11-d482-5d93-a652-4c0526c7f607 | note | Acceptance Criteria: Backfill compacted in <= 250mm loose layers to achieve minimum density R_D 95% (MDDR = 95%).
5dcffef9-762b-5d2c-97e2-3a94920e3167 | note | Reference Documents: Drawing(s): EW-FP-DRW-00-0001
309772c4-1e2c-526f-9f61-3511bb2c9efe | note | Inspection / Test Method: Test report
d7ab43a6-a362-5713-b2a3-99973b3d2929 | note | Record of conformity: ITP signed
a04f7dce-87d3-5c68-9916-78a73e3cc572 | note | TP
80ae4a7c-da5f-5549-9a60-ab4659d76c63 | note | Responsibility: Site Engineer
8028613b-9f3b-5be2-835e-df35751f6992 | date | Date Completed:
| checkpoint | 4.07 - Marking Tape
221ccee7-c11d-5e55-a8eb-6c074056989b | note | Frequency: Each Lot
cc017398-2cdb-508e-960e-bfe0a8c76b65 | note | Acceptance Criteria: Tape widths must be as recommended by the manufacturer for the size of pipe to be covered but must be not less than 75mm wide for pipework up to 50mm dia.
4903aeb3-69d2-5821-8838-3d78891d90af | note | ○ DETECTABLE IDENTIFICATION -TAPE-300mm MINIMUM ABOVE PIPE.
e013c97c-6ec3-5785-8496-76f3a3237a29 | note | Reference Documents: Drawing(s): EW-FP-DRW-00-0001
d5521529-c0f0-5028-a9c7-f0dca0651fd5 | note | Inspection / Test Method: Verify
a52e6e65-20ce-5ed9-81b0-61471d8716df | note | Record of conformity: ITP signed
aa165d05-38cc-5ab4-bc71-4b394d2abdfd | note | IP
43700168-13ca-56df-8101-43d354c587c2 | note | Responsibility: Site Engineer
075c4c4f-606c-5aa2-97f2-f5bf3ba99a61 | date | Date Completed:
| checkpoint | 4.08 - Valves
f473a193-a740-55ce-a948-ec3f0c244fc0 | note | Frequency: Each Lot
9af55af0-e958-5c04-9a77-fa983567a4e3 | note | Acceptance Criteria: Install valves in the vertical position and provide surface fittings and valve markings in accordance with Drawings
b525cb12-d4a6-58ac-ab4c-8677cbdf07c3 | note | ○ Inspect the valve for damage. Repair any damage to the external coating in accordance with the manufacturer’s instructions
102cae0e-b08a-5986-95fe-4e0897f4bd79 | note | ○ Check the valve and off-take clamp flanges to ensure the sleeves fit in the bolt holes. Trim insulation sleeves such that they join inside one flange, and not at the flange joint.
9a8a36a4-d604-55d0-9fa0-4bc065e43f75 | note | ○ Ø150 U.P.V.C. (AS1477 CLASS 4.5) PIPE SLEEVE to be installed
fc253000-2664-593e-ad4a-5326cab4192e | note | Reference Documents: Drawing(s): EW-FP-DRW-00-0001, SLUICE VALVE DETAIL
e4e28ed6-457c-585f-9879-671b960d42ce | note | Inspection / Test Method: Verify
75db6a74-196c-51de-9157-cb4d78b213b4 | note | Record of conformity: ITP signed
65bfea2b-a3ab-57f5-92d2-227757804253 | note | WP
255db9ff-2b24-5002-9f5a-767c6d110c82 | note | Responsibility: Site Engineer
f10c0521-dc5c-56f6-82cf-5e389f91f324 | date | Date Completed:
| checkpoint | 4.9 - Hydrants and Valve Covers
2b2f53d8-0f09-5949-91ec-3630fb7a6965 | note | Frequency: Each Lot
94caf343-9492-5741-bc38-2d69f89406b4 | note | Acceptance Criteria: Ø100 HOT DIPPED GALVANIZED PIPE RISER (SINGLE PIPE RISER FROM P.E. PIPE.) to be installed.
15531548-7dea-5852-be30-9429dcd39fa9 | note | ○ 600mm x 600mm x 250mm CONCRETE PAD TO STABILIZE HYDRANT RISER. FINISH NOMINAL 25m ABOVE GROUND. Ø200 CAST IRON INSPECTION SHAFT COVER (Valves)
0f3b25cb-adce-55f0-b93d-cafc4af20264 | note | ○ Refer to Table B.6.1
f37d50a8-0c5e-5040-ac3d-8f39f4c15332 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
cf62093d-b99c-541f-8420-afd9c77d811d | note | ○ C.6.10.2,3,4,6,
d44cf574-1953-5b0b-ad1b-998659bcea33 | note | ○ Drawing(s): EW-FP-DRW-00-0001, EW-FP-DRW-20-0004, EW-FP-DRW-10-0001
57e5d433-f12d-54ca-b422-05f28c572b29 | note | Inspection / Test Method: Verify
e8caa3a1-9672-5753-92de-ba3a8ee84529 | note | Record of conformity: ITP signed
f68e4323-c999-5d2a-908a-afacb7bbd02c | note | WP
c76d6258-40da-5154-a9cb-7cd33d594cb6 | note | Responsibility: Site Engineer
58c5dbbe-ca9c-5fca-9091-ff7eb5f71951 | date | Date Completed:
| checkpoint | 4.10 - Thrust blocks
63d3bf48-afea-56d0-89e0-ec912b7eec04 | note | Frequency: Where required
d0e4e6e5-ea4e-5acf-b97c-3cb9e25bfcf1 | note | Acceptance Criteria: Thrust blocks must be installed in systems with unrestrained anchors.
deea68be-4819-5d7b-9ce8-118623d7b919 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
d84273ee-d7f2-5407-b406-30ea649c39c9 | note | ○ C.6.10.2,3,4,6,
9967dd49-5382-5e0e-abd8-3815e17da320 | note | ○ Drawing(s): EW-FP-DRW-00-0001
4869c6d8-04f5-5ea1-b208-c842fe99a25e | note | Inspection / Test Method: Verify
dc60e9e1-dda7-5e87-afbe-5e78770f194e | note | Record of conformity: ITP signed
71e084d8-883b-57fd-be93-ada9b658d3a4 | note | WP
8d9198aa-0151-522a-b771-158458efcbe5 | note | Responsibility: Site Engineer
2ca66e3c-5888-551d-9474-2730d4edf8cc | date | Date Completed:
| section | 5 - Testing
| checkpoint | 5.1 - Compaction Testing (when applicable)
bf59d84b-afc6-580a-958f-c15bb91cccc1 | note | Frequency: Completion of pipe installation & fittings.
049a654a-3761-5278-894c-3ad5b1585ebc | note | Acceptance Criteria: Undertake field density testing of trench fill in accordance with the methods specified within Specifcation and Drawings.
1d183f83-b0da-5961-b7aa-ff05cdfdb242 | note | ○ Testing not required where stablised sand is substitued for rock.
573fbbf5-4d9d-572b-93d8-8a15f7a86418 | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.)
301dcdc6-b769-5930-bfa4-2f74ff0d7809 | note | Inspection / Test Method: Compaction Testing
c6af9ba2-6e71-57b7-8c03-a0f0984447e1 | note | Record of conformity: ITP signed, Test Records
b5b4e03f-43c7-5a4d-ac61-bcdb585691c2 | note | WP
bae25f7d-3c6d-548b-81d3-4b889789eb93 | note | Responsibility: Site Engineer / Superintendent
9bfb6c1a-eea2-52f6-9ba1-a8b9e4f45fd7 | date | Date Completed:
| checkpoint | 5.2 - Pipeline Pressure Testing
46729fd7-5185-53c6-a748-8d9db0420ea4 | note | Frequency: Completion of pipe installation & fittings.
280da0e2-fe6e-5616-9d64-b0b6e295cd02 | note | Acceptance Criteria: Undertake pressure testing of pipelines in accordance with the methods specified in Specification: EW-FP-SPC-0000001(C.).
6a4d2863-2f35-54c4-8bce-68eaaeb008ca | note | ○ Refer to Table B.6.1 - Fire Pipe Schedule and AS2419 - Section 7 for test requirements.
073b3550-59b4-5b16-8bdb-ab1bb439a7ff | note | Reference Documents: Specification: EW-FP-SPC-0000001(C.), AS2419 - Section 7
6282c043-1d2c-5437-a56c-6500e02c53f0 | note | Inspection / Test Method: Pressure Testing
48f80279-d156-51fa-bf5f-f04093dad8f1 | note | Record of conformity: ITP signed, Test Records
68fcd8b6-af81-5ea4-ace7-e1f8961a7e53 | note | WP
ab3f89cb-b14d-5ae8-a66d-42136cbbfa35 | note | Responsibility: Site Engineer / Superintendent
72edf833-df2b-5c11-93a6-40177898fbe6 | date | Date Completed:
| section | 6 - Completion
| checkpoint | 6.1 - As constructed drawings
7594d5dd-6593-5a83-8098-558208ce9b6e | note | Frequency: Each Lot
385abf2c-37c5-5acf-98b4-bd210903d2d7 | note | Acceptance Criteria: Ensure all conduit deviations are captured on redline drawings for updating the IFC Drawings, and providing asbuilt data.
9ef241f1-a9a6-55bf-9ba8-04ed25d5a71b | note | Reference Documents: Drawing(s):
9c2ce22f-bfa0-50a4-a066-57371591c739 | note | ○ EW-FP-DRW-00-0001
288583fa-17c8-5f57-8150-e5005343cb59 | note | ○ EW-FP-DRW-20-0004
1bd782b6-d886-568d-abbe-9ee465dbd642 | note | ○ EW-FP-DRW-10-0001
cb7324e0-7963-5e7f-8dfe-267c2fec7e62 | note | ○ EW-FP-DRW-20-0001
4cbc0995-caa8-5cea-a80a-b965264aa8d0 | note | Inspection / Test Method: Verify
c6fc3a5a-d2a3-53b3-ad1f-3307f70be909 | note | Record of conformity: ITP signed
a13774f3-d027-5bbb-b292-f13a33fe9d56 | note | IP
838810fc-a38f-51a1-8b48-7e30f7a651bb | note | Responsibility: Site Engineer
805b145a-95f8-5d7d-8778-635abb23131b | date | Date Completed:
| checkpoint | Final Inspection
61e3e359-44e7-5485-a1cc-4e76f77fe4c7 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
eefe457a-f6da-5f8d-9b25-07efac89813f | textbox | Print Name:
b37f0829-c683-54ff-99a5-7a4acb81c628 | textbox | Position:
75410126-f1c0-586d-b2d8-645effbc2806 | date | Date:
| signoff | Sign ITP
| checklist | GT4-ITP-020 - Sewer Rising Main | itp | GT4-ITP-020 - Sewer Rising Main | 17ab8337-7ad6-46e2-affc-df83a95ff0ec
| section | 1 - Preliminary Works
| checkpoint | 1.1 - Check that current revision drawings are being used
a274e7a9-3712-5f09-84ea-1bf27cf1ea4d | note | Frequency: Prior to Commencing Work
16b8f2ff-5fff-542c-aa51-d1556b4bb84d | note | Acceptance Criteria: Issued For Construction (IFC) and latest available revision used
30f3c611-7bae-57e5-9ed0-a20aabe6af48 | note | Reference Documents: IFC Project Drawings/ Drawing Register
23c61706-4234-55d5-a1e6-43a70e9c5c7d | note | Inspection / Test Method: Document review
09c254bd-e9e7-5094-a39f-e5542fb49d1a | note | Record of conformity: Latest revision IFC drawings
fceb439c-f904-5df7-a865-9e0e1d6ce0e0 | note | *WP
96bc96a8-5d9d-5741-ad10-4e0e10ca8928 | note | Responsibility: Site Engineer
c815b887-40f3-5c0c-9872-cf0a02326283 | date | Date Completed:
| checkpoint | 1.2 - Confirm understanding of current EMP related to the work area and that all prescribed environmental controls are in place
b8776764-3b0d-5ec9-98ce-2734e18d1307 | note | Frequency: Prior to Commencing
7242fbf6-71d2-51ec-ab4e-2247b3a695eb | note | Acceptance Criteria: All environmental measures to be implemented as per current CEMP and local authorities. Sediment control measures to be installed and protected vegetation to be clearly identified
c7ade491-0379-501e-bfff-a96c68f4731e | note | Reference Documents: CEMP, Site induction
d3307ab8-6c4d-5f08-aee7-127e54a91d5b | note | Inspection / Test Method: Document review & Site inspection
52dbbab4-7878-5546-b80a-3cfd64069f1c | note | Record of conformity: ITP signed
e7bba101-af2b-56fd-85b3-861423de073f | note | *WP
cb918236-12e7-53de-803c-b8aef34dbbc4 | note | Responsibility: Site Engineer
53e7a295-75f9-591c-885f-c4bf722085c0 | date | Date Completed:
| checkpoint | 1.3 - Traffic Management (When required)
03d60e12-3b91-5c0c-bde9-60a8b520afd5 | note | Frequency: Prior to Commencing Work
6a2bd74c-0dd6-5186-bb07-3048844c1599 | note | Acceptance Criteria: Approved TMP and WASIN (where required)
9002db7c-461b-5bd7-9b99-105ce7bbc16a | note | Reference Documents: Applicable TMP
b5ea9461-0b41-5c5d-99bb-ea56d620f296 | note | Inspection / Test Method: Document review & Site inspection
8576e63e-5249-57e8-861b-189b675d4787 | note | Record of conformity: Approved TMP
a0a9d39e-9277-5f72-a431-000e8f8f1b9e | note | *HP
2523e6d6-dc35-5348-aa45-a29d75c1cba2 | note | Responsibility: Site Engineer
ab9715c2-5568-50f0-bc8b-78b95284a920 | date | Date Completed:
| checkpoint | 1.4 - Survey set out works
b9b22769-115e-5993-b573-ec1696d150b4 | note | Frequency: Prior to Commencing Work
e436736e-794f-5066-8ca3-a794f5dd61c4 | note | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
55e08f38-9535-5eee-aef9-01c7f1b33598 | note | Reference Documents: IFC Project Drawings
3c6c2f9e-524b-5a8c-87c5-8547331c0ec6 | note | Inspection / Test Method: Site inspection
5c7cac9a-5eee-5eeb-b7bc-bf176476ad85 | note | Record of conformity: Survey records & marks on the ground. This ITP Signed off.
da5fafd5-8b58-5a89-bfca-8e43a5e6d1b7 | note | HP
109f6404-8c37-5921-a468-4c953a92cd2e | note | Responsibility: Site Engineer / Surveyor / Superintendent
65a381af-4e2f-599e-99a4-d6aa5902531a | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 2 - Material Conformance
| checkpoint | 2.1 - Water Pipes and fittings
6ba8eb6e-3ceb-58fd-b767-7943123cd955 | note | Frequency: Every batch of new material
11f4bc69-eff2-513f-bcef-c0c79b70b1f1 | note | Acceptance Criteria: Sewer pipe material to be free from defects and be sized to the following:
12ca7d2a-4fe2-57dd-84ef-db0c93498c5d | note | ○ EW-CE-DRW-600-002- Schedule 1: New Pipe WSA-02-2014-3.1
e296c301-64a2-5f60-afca-0e03bc0bafbb | note | Reference Documents:
a2bba691-2a25-5744-ab8a-e48bc0d2e017 | note | ○ WSA-02-2014-3.1
0d8b8b64-f8c6-5700-b464-1b32fb2e7403 | note | ○ WSA PS 207
125dd349-aabb-58e9-a53b-66bed2a9e881 | note | ○ WSA PS-230
0b2a89ea-df7f-5195-8623-c3421cda6c2b | note | Drawing(s):
1b7656ff-e5ed-578a-884b-5430d39412e1 | note | ○ HB19198-C1271
6180fc42-f213-52d4-9590-41577e6aa981 | note | ○ HB19198-C1272
852474db-493f-576d-90b5-a6d0dded8806 | note | ○ HB19198-C1273
92550799-d786-5794-af72-ed71898cedb6 | note | ○ EW-CE-DRW-600-001
3f7c0a05-3266-5128-8ef8-df8af56229c1 | note | Inspection / Test Method: Verify
b47f5a32-6ac1-54dd-bcb5-4854ce7cca00 | note | Record of conformity: ITP signed, Receival Inspection Checklist
6cb0c150-2390-5e32-bb65-8232f255ef48 | note | IP
01165837-6903-5c54-9d1c-e7cc8dc42a6e | note | Responsibility: Site Engineer
df82984a-2bcc-5efd-879b-b05ddf1440b6 | date | Date Completed:
| checkpoint | 2.2 - Correct embedment / backfill materials onsite
ea87c7f8-1a01-57e5-8693-d4113e7a4b14 | note | Frequency: Every batch of new material
89660966-be11-5310-8bb6-4cb0d80f6c59 | note | Acceptance Criteria: Inspect bedding and backfill material to ensure suitability. If watermain is to be protected, use stabilised sand or concrete encasement
26fc6f73-5ec1-548f-9b7f-42fc28941772 | note | ○ TYPE R - REFER TO TRENCH DETAIL.
d966fa50-9259-5507-80f9-728ca2d2d6d8 | note | Reference Documents: MRWA-W-201 to 203, EW-CE-DRW-600-006
742f0058-b59a-5fe2-81b8-cb8829c2da3f | note | Inspection / Test Method: Verify
59a8d677-7b36-567d-89a0-a9619eb22f27 | note | Record of conformity: ITP signed, Receival Inspection Checklist
b30ca6a1-198d-56c5-9cf6-1bcb0765db84 | note | IP
4f874dea-352c-576c-8785-148675a478d9 | note | Responsibility: Site Engineer
8fb72061-1391-5fbb-ad59-275df8538aa0 | date | Date Completed:
| section | 3 - Excavation of trenches
| checkpoint | 3.1 - Trenching details
bbc0286e-70e6-59e0-ab76-d57fc9325d2b | note | Frequency: Ongoing
1f26fd6b-307a-5b28-aff5-012416c08536 | note | Acceptance Criteria: Trench's to be excavated to conform with IFC drawing details.
a287b99c-f3ce-5e1c-8b23-3499598cf8c3 | note | ○ Sides of excavation to be kept vertical to at least 150mm above the pipe.
3d5a129e-e2bb-5b42-95d6-80b92a6a2faa | note | ○ Ensure trench width and depth are within tolerance
38bc5228-5ef5-5b03-a3ca-d2ea9a941870 | note | ○ Ensure trench foundation & wall firm, stiff & suitable
486a3d6f-16b2-5b95-b92e-4ceac16e9340 | note | Reference Documents: Drawing(s): MRWA-W-2023, EW-CE-DRW-600-006
9bc83596-86d8-586c-96ed-649ed0f50bf2 | note | Inspection / Test Method: Verify
e791439b-0040-5930-b49c-c46d63ccfa5a | note | Record of conformity: ITP signed
9dfca2ca-85e6-5e01-ad9c-f4df459da90f | note | IP
d283a8aa-cfb5-5184-b2d9-b573ad90250a | note | Responsibility: Site Engineer
8ab9e7d2-4dee-5eaf-86ed-f0e856673840 | date | Date Completed:
| checkpoint | 3.2 - Benching & shielding (where required)
2e7e8871-6cad-548a-b560-e0ee2dcdb449 | note | Frequency: As Required
1763f747-260a-5a25-8578-e69e5bd78688 | note | Acceptance Criteria: Trench support is required where the trench is more than 1.5 metres, unless the trench has been assessed as safe by a geotechnical engineer and written confirmation provided as such.
468e3671-302b-5f2d-9354-c59e1b5c8b6a | note | Reference Documents: Work Procedures
875082f1-c1de-56a0-8c39-2e4e745f1e3d | note | Inspection / Test Method: Verify
b51fefbc-a3b7-57ac-9164-53584b6d883d | note | Record of conformity: ITP signed
413d3ff0-2304-5b40-8124-c309a4bbc4ff | note | *HP
34271537-88a4-5ddf-abf4-a20685b80409 | note | Responsibility: Site Engineer
d10c6714-c822-5017-9452-70a6077189c9 | date | Date Completed:
| checkpoint | 3.3 - Capping and grouting of abandoned mains
736531d8-0ac1-53d8-92ec-109fc7e9be16 | note | Frequency: Before bedding material is installed
97f91301-f1e1-5d34-bb31-47bac8dac3f2 | note | Acceptance Criteria: Where it is necessary to fill a redundant pipeline, low strength grout (<5 MPa), similar material or sand shall be used.
2eaaf072-662e-5861-8130-648a6c049e3f | note | Reference Documents: Drawing(s): WSA 03-2011 3.1, EW-CE-DRW-600-004
286fdcca-c270-54cf-b034-466327917d17 | note | Inspection / Test Method: Verify
6fcfb2a7-e3e1-548c-ba29-2fd6eac5114b | note | Record of conformity: Release of Hold Point
26895525-50f8-5596-9270-dcf66cea59f2 | note | WP
0a04cd6c-9177-589b-a82d-44e015b4238f | note | Responsibility: Site Engineer/Superindendant
6ff629f7-6367-575b-ac33-7f0bfe0a7e93 | date | Date Completed:
| section | 4 - Watermain Installation
| checkpoint | 4.1 - Bedding
3bf3bbb4-d4dd-5c67-ad57-6c5676644a78 | note | Frequency: Each Lot
c77bd12e-9983-5f42-9781-3c1abc814ecb | note | Acceptance Criteria: Bedding materials : 5 or 7mm single sized aggregate used
b6c62753-f15b-57a0-ac39-4eeb0ca7da00 | note | ○ Bedding depth: 75mm>x>150mm for 150dia pipe
39ea704e-1c99-5a67-abc1-47acc14ecf31 | note | Reference Documents: AS2053.1:2001, MRWA-W-201, EW-CE-DRW-600-006
87662fcf-f60b-5cfe-a765-afd0b4053feb | note | Inspection / Test Method: Verify
a933638b-0fca-5064-a0e1-cc5edeb58cec | note | Record of conformity: ITP signed
4fbc8b91-6a4d-57fd-8fde-7ee296edfab1 | note | IP
7bc839cf-0f5a-51b4-885f-476856ba8972 | note | Responsibility: Site Engineer
b1c2105c-63ff-5b9f-9c43-4d2eaa9f4579 | date | Date Completed:
| checkpoint | 4.2 - Pipe Joints
0973bb61-fb9b-5ef7-8da2-1d8f9c885136 | note | Frequency: Each Lot
512302fd-5732-5121-a668-ba3325385d61 | note | Acceptance Criteria: Ensure pipe joint deflection is acceptable, as per drawings and product specifications.
5e8121c6-0ca5-54fb-9ae8-c6a0013a213a | note | ○ ALL JOINTS SHALL BE BUTT WELDED. WHERE BUTT WELDING IS NOT POSSIBLE MECHANICAL
c351d8a1-2b20-5bde-bd17-360a59d9f262 | note | ○ JOINTS SHALL BE USED. ELECTROFUSION SHALL NOT BE USED UNLESS APPROVED PRIOR BY THE SUPERINTENDENT.
c05efb67-4148-5fc0-aa96-80672434998a | note | Reference Documents: MRWA-W-103
25f848f9-a753-5b7c-b9a6-e0a9d3cc4b7d | note | ○ Drawing(s): EW-CE-DRW-600-001
8ef166f5-224c-5244-8308-564a9a6c16ab | note | Inspection / Test Method: Verify
b509c191-9768-5c57-9c8b-e829db98823e | note | Record of conformity: ITP signed, photo of each joint
d52db969-502b-5c57-981c-26931c50ac5d | note | IP
a0d3c11c-c231-5351-8ece-d5a4a7697725 | note | Responsibility: Site Engineer
ca6905e3-a795-56c4-a206-3eed9cdcf5ad | date | Date Completed:
| checkpoint | 4.3 - Pipe Embedment
9866ad63-19b3-5b66-9613-d7361857d1bc | note | Frequency: Each Lot
b39a7689-79b9-5193-ae80-0620a467faf7 | note | Acceptance Criteria: Embedment Type R including 5/7mm single sized aggregate.
b89cf7e0-a8ad-5d41-8581-9ebe14795d1a | note | ○ Min Overlay: 300mm (Compaction with ride on equipment)
50014e70-45f6-5634-a009-d57e5c6d0e0f | note | ○ Side Support: 100mm>x>350mm
ead4ab25-ca7e-5cd0-b790-6f9be9e273e6 | note | ○ Embedment placed under haunches by shovel and worked around pipe to ensure all voids at haunches are filled
f9a7784b-99b4-521f-a926-265e394d11f6 | note | Reference Documents: Table 201-D, MRWA-W-201, MRWA-W-202, EW-CE-DRW-600-006
11ecb572-88f8-5312-bb0f-5a006920c619 | note | Inspection / Test Method: Verify
b92f1adb-5b0d-5acf-90b0-9f75d6901206 | note | Record of conformity: ITP signed
43900018-e47b-5190-9213-e8093545e93c | note | IP
4ee0ef08-9477-5baf-b368-41da622a2dd1 | note | Responsibility: Site Engineer
089e20c5-0b71-5000-961c-2b2682a44924 | date | Date Completed:
| checkpoint | 4.4 - Pipe Backfill Material
938ffecd-bbe7-5570-8b0b-d8b6174b83b1 | note | Frequency: Each Lot
63e2d7f8-e6db-503a-ace7-b37f0ccf6a68 | note | Acceptance Criteria: Backfill material (Type R):
9b81fbb7-d06a-58fe-b8f7-c6789d848898 | note | ○ Class 2 FCR (depth <1.5m)
909fc6e9-5df4-5e5e-a422-d7abb16f1fd1 | note | ○ Class 4 FCR (depth >1.5m)
32a14178-c6b8-5171-abbb-fc9ec1165f04 | note | Reference Documents: MRWA-W-201
2a612b82-feb7-5f41-aae2-16c0064846f6 | note | ○ Drawing(s): EW-CE-DRW-600-006
f329284e-f1bf-5886-abc8-c48022c7ca51 | note | Inspection / Test Method: Verify
e908a61d-3028-5aa7-bfee-7d04a6c4d777 | note | Record of conformity: ITP signed
0409ba78-7aa9-5157-8dbb-73b802115e8b | note | IP
05a2ecd3-b8aa-5b03-b35c-e082cd3b712a | note | Responsibility: Site Engineer
7211a825-c994-56e9-be1b-805d962987da | date | Date Completed:
| checkpoint | 4.5 - Pipe Backfill Compaction
d48e3221-7c9c-5429-890c-453a7c58dae0 | note | Frequency: Each Lot
41763cd8-d3a9-543d-9bdb-e27ed0aa2734 | note | Acceptance Criteria: Backfill compacted in <= 200mm loose layers to achieve minimum density R_D 95% (MDDR = 95%). Avoid compaction within 500mm of top of pipe
8778a4ed-ca72-5beb-8c8b-8a71d2c6aa12 | note | ○ Trafficable Areas: R_D 95% (MDDR = 95%)
2c1b3a2b-da1d-534a-9dea-38b13b2d25b8 | note | ○ Non-Trafficable Areas: Below 600mm = 90% MDDR, Above 600mm = 95% MDDR
9dc52d84-bf8c-5cac-a2a0-0a4dde9fbc78 | note | Reference Documents: MRWA-W-201, MRWA Specification No. 04-03.
0d6dc5a6-db1c-5dc0-af6c-851da1ec0d34 | note | Inspection / Test Method: Test report
302e6402-2b5f-5ef6-a801-754b1c4b4af6 | note | Record of conformity: ITP signed
b6505caf-b14d-50b4-884c-8bcdf4151bed | note | TP
4e864a48-91fc-538a-9ea2-20b39b688f43 | note | Responsibility: Site Engineer
84ba317d-0e87-56c0-bb93-ebb432078b25 | date | Date Completed:
| checkpoint | 4.6 - Marking Tape
c297621a-a97d-594a-9d4a-6b36383117f0 | note | Frequency: Each Lot
0d413326-359b-5608-9713-92f50ecd6dd8 | note | Acceptance Criteria: Marking tape to be laid along the route of the alignment ontop of first backfill layer
0d0abf7c-afc4-530c-af8d-4b8343b56679 | note | Reference Documents: MRWA-W-202
c5374edd-8235-5c93-8671-f88d534fd7a0 | note | Inspection / Test Method: Verify
2107cde0-e1ba-59f8-8254-30e03ef6729e | note | Record of conformity: ITP signed
fff1a111-f087-53e5-8e5b-c4309e9d1df9 | note | IP
ef39c5f4-b8eb-507e-a253-9033fb1dcfb4 | note | Responsibility: Site Engineer
73c4f223-c87c-5e67-90f0-37b3e83ba01a | date | Date Completed:
| checkpoint | 4.7 - Valves
2cc4e3bb-c866-5579-9488-d73923206547 | note | Frequency: Each Lot
d3780a24-869f-5174-ae91-94cbf581bb4d | note | Acceptance Criteria: Install valves in the vertical position and provide surface fittings and valve markings in accordance with Drawings
4b972e46-0a3e-542d-b596-4fe2e46e3260 | note | ○ Inspect the valve for damage. Repair any damage to the external coating in accordance with the manufacturer’s instructions
91c7e0c1-baa8-50fa-844c-e3fd3d126329 | note | ○ Check the valve and off-take clamp flanges to ensure the sleeves fit in the bolt holes. Trim insulation sleeves such that they join inside one flange, and not at the flange joint.
901f782d-0050-532c-94e6-46411904ad05 | note | ○ Lid on valve to be cenrally placed
69a0354f-de47-5fb6-b457-4b0d31740dc1 | note | Reference Documents: WSA 03-2011 3.1, MRWA-W-300, MRWA-W-301 and MRWA-W-302, EW-CE-DRW-600-004
7e00163a-70a0-5b6d-bb6a-1533addce0f3 | note | Inspection / Test Method: Verify
9d27e2b4-d1d0-5785-921f-981ded766045 | note | Record of conformity: ITP signed
f4679919-3be6-52dc-8dc7-3649884a3067 | note | *HP
46de2de0-2abe-5a3d-8a0d-3771fbbd2828 | note | Responsibility: Site Engineer
c81ffbaf-ecce-5e8f-bde7-72125fc64702 | date | Date Completed:
| checkpoint | 4.9 - Scour/Pump Out Points
1fcdaef1-2fee-531f-af87-dc0132fd7409 | note | Frequency: Each Lot
42a8ae30-5c81-5bb0-8a5e-c6bdb4a9d57b | note | Acceptance Criteria: DN100 SCOUR/PUMP OUT POINT IN A 1200 CONCRETE MH PIT to be installed where denoted on the drawings.
73d1d256-5a7c-545f-89b3-094f05a0c68a | note | ○ SEWER SCOUR OUTLETS TO BE IN ACCORDANCE WITH STANDARD DRAWINGS SPS-1602 AND SPS-1603
de0edd5e-947b-5ebb-b04a-b0fddd45deb8 | note | Reference Documents: EW-CE-DRW-600-004
df011109-5c31-5683-865a-18c08e091faf | note | Inspection / Test Method: Verify
c8f3d8b5-8779-55a8-ab5a-3f97e49bb8ea | note | Record of conformity: ITP signed
e0f698f5-cea2-5855-a51f-c01ea8ecb35a | note | *HP
a3774a51-d4cb-58b1-aa7c-3675ad5ffc4e | note | Responsibility: Site Engineer
5bd2d023-2129-5361-a9fd-9fde7e515155 | date | Date Completed:
| checkpoint | 4.10 - Thrust blocks
76915929-ad4c-5126-8151-0758081bd979 | note | Frequency: Where required
a7eeca9b-e6cb-5012-bc4c-75bdf1ff6f78 | note | Acceptance Criteria: CONNECTION TO THE EXISTING RISING MAIN MUST BE ANCHORED TO PREVENT MOVEMENT CAUSED BY THRUST IN ACCORDANCE WITH MRWA-W-205A. THRUST BLOCK AREA = 0.89m2
09a76e57-7034-5dca-aa9a-ee0e57fcb471 | note | Reference Documents: MRWA-W-205a, EW-CE-DRW-600-001
9d58e776-0919-5b59-bd06-400af155509b | note | Inspection / Test Method: Verify
edd9583e-3ee5-5bba-a7ce-ae3728da9233 | note | Record of conformity: ITP signed
f03835b8-a2ac-5577-9ecc-2db5f543473f | note | WP
15cdde4f-85f1-5f78-b2ab-1b2378dee3b9 | note | Responsibility: Site Engineer
998b5242-112a-5085-8a0d-98ef40531e03 | date | Date Completed:
| section | 5 - Testing
| checkpoint | 5.1 - Compaction Testing (when applicable)
b132ef2f-7ae8-5012-a997-75f1767b4fa9 | note | Frequency: Completion of pipe installation & fittings.
1f0fc339-ce97-5ed6-a04a-35d0118fe5be | note | Acceptance Criteria: Undertake field density testing of trench fill in accordance with the methods specified in WSA 02 - 2014-3.1
8a0d838f-e449-52c9-9e0a-1c9a981333b8 | note | Reference Documents: MRWA Backfill Spec 04-03.2, EW-CE-DRW-600-006
b7a3d8f3-cf1d-5ba6-ac12-f180a0813894 | note | Inspection / Test Method: Compaction Testing
ef682335-7f0a-547f-a66b-f62069a8c87d | note | Record of conformity: Test Report
2f5e6df2-a40f-5ed7-91df-636c195e24ad | note | WP
68431e79-d2b6-5ac9-b2c8-9af4d4e9bad3 | note | Responsibility: FH Engineer / Superintendent
0da18ff5-354b-5e1f-ad64-bea267710b6e | date | Date Completed:
| checkpoint | 5.2 - Pipeline Pressure Testing
f9fac129-e4b2-5450-9098-bbc466e4d365 | note | Frequency: Completion of pipe installation & fittings.
7af55dce-02ad-587a-94a8-eea88c663d04 | note | Acceptance Criteria: Undertake pressure testing of pipelines in accordance with the methods specified in WSA 02 - 2014-3.1 & WSA 03 - 2011-3.1.
19bb53e7-3326-5caa-ba5b-20e08b7dcd75 | note | ○ Gravity sewer to be tested for 28 Kpa for minimum 3 minutes and sewer rising main to be tested at 31m 1000 Kpa for minimum 2 hours.
0c1615da-f5d3-5bd3-bc82-babaa9011490 | note | Reference Documents: WSA 02 - 2014-3.1, WSA 03 - 2011-3.1, EW-CE-DRW-600-001
7498d455-e0a9-560a-b0da-dbb5254e5a60 | note | Inspection / Test Method: Pressure Testing
8561890a-cce5-5204-ae05-f5fed4007012 | note | Record of conformity: Completed CL-003- Pressure Testing Record & CL-003(A, B or C) -Pressure Testing
7459dcea-edaa-59be-806b-b9525c29a42b | note | HP
552b2134-3737-55a6-be13-74f81b3483c2 | note | Responsibility: FH Engineer / Superintendent
122a8489-b970-5da9-8724-d97d94a3efc8 | date | Date Completed:
| signoff | AUTHORITY HOLDPOINT
| section | 6 - Completion
| checkpoint | 6.1 - As constructed drawings
637c564c-47a5-5917-a69f-2952c26020dd | note | Frequency: Each Lot
5d88cd3c-2745-52aa-b490-33f291c40adb | note | Acceptance Criteria: Ensure all conduit deviations are captured on redline drawings for updating the IFC Drawings, and providing asbuilt data for AutoCAD
ec26cd93-e75b-509a-ab26-e408aa1fcbb8 | note | Reference Documents: EW-CE-DRW-600-004
601cc319-b2be-5089-b90e-8df821eb8253 | note | Inspection / Test Method: Verify
f0ddc819-13c2-540b-9c70-03e33e996e5e | note | Record of conformity: ITP signed
def40687-0bb4-509f-916b-fa2587145747 | note | IP
84d529ec-81f0-5b10-8498-0e109c6e4c8b | note | Responsibility: Site Engineer
7b800844-c498-5114-b5f4-ce2e68ebc189 | date | Date Completed:
| checkpoint | Final Inspection
0598fd7e-1637-5913-a72e-ef96e97e2049 | note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
ed1361bc-2f6c-5abb-8d50-4d2788c24d58 | textbox | Print Name:
73c9263b-9a25-55c0-b31c-f30e516921ba | textbox | Position:
51f821f1-cc39-5573-bbe2-5a3088ad1318 | date | Date:
| signoff | Sign ITP