## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | 001 - Pre Works |  |  |  |  | Yes | 001 - Pre Works | 1ec117d6-1fad-4a98-a3f2-af2da85a56ba
checkpoint-group |  |  | section | Site Inspection / Establishment & Isolation
checkpoint-status |  |  | checkpoint | Confirm address and delivery location
checkpoint-status |  |  | checkpoint | Make contact with Builder project Team and establish work hours etc
checkpoint-status |  |  | checkpoint | Create SWMs and issue to site team along with insurances
checkpoint-status |  |  | checkpoint | Confirm Premier site team and all tools have been organised ( Site box, ladders etc)
checkpoint-status |  |  | checkpoint | Once onsite review all documents and have a site walk to create any dilapidation report required for existing state of the site
checkpoint-status |  |  | checkpoint | Once dilapidation report has been completed begin make safe of existing Power, Lighting and Data as required
checkpoint-status |  |  | checkpoint | Issue the isolation Cert in next tab along with all documentation required to Builder team following make safe
checkpoint-group |  |  | section | Temp Power & Lighting
checkpoint-status |  |  | checkpoint | Discuss with Builder team for locations of proposed Temp DB and lighting across the site
checkpoint-status |  |  | checkpoint | Install Temp DB and Lighting to site as planned
checkpoint-status |  |  | checkpoint | Issue Builder team CCEW once temps have been installed with all information regarding the temp install for Breaker cascade
checkpoint-status |  |  | checkpoint | Assure all temp leads and DBs have been tested, Tagged and are in date.
checkpoint-status |  |  | checkpoint | Issue test and tag register to the builder
checkpoint-group |  |  | section | Conduits / Trenching & Underground Installation
checkpoint-status |  |  | checkpoint | Review all documents to assure that all runs have been accounted for
checkpoint-status |  |  | checkpoint | Conduit/ fitting size, type and locations correct
checkpoint-status |  |  | checkpoint | Conduit bends and radius satisfactory and ends sealed
checkpoint-status |  |  | checkpoint | Anchoring of conduit, accessories and all joints secure
checkpoint-status |  |  | checkpoint | Conduit labelled/ identified as latest AFC Drawing
checkpoint-status |  |  | checkpoint | Unfinished conduits labelled and ends taped in readiness for continuance in next section
checkpoint-status |  |  | checkpoint | Clearances to formwork and parallel steel sufficient
checkpoint-status |  |  | checkpoint | Draw wire installed
checkpoint-status |  |  | checkpoint | Expansion joints fitted correctly
checkpoint-status |  |  | checkpoint | Concrete pour witnessed
checkpoint-status |  |  | checkpoint | Conduits inspected afterwards to assure they are free from defects
checkpoint-status |  |  | checkpoint | Update As-builts if required to show any changes to conduit runs
checklist-sectioned |  |  | checklist | 010 - In-Slab Works Installation |  |  |  |  | Yes | 010 - In-Slab Works Installation | 2d9db6a8-3a52-4d46-a840-0a1f67156d3b
checkpoint-group |  |  | section | Coordination
checkpoint-status |  |  | checkpoint | Ensure that all new installations have been coordinated with other services, both new and existing
checkpoint-group |  |  | section | Metering / Setting Out
checkpoint-status |  |  | checkpoint | Ensure that the latest service drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure correct datum points are identified confirm datum points with building works supervisor. Use correct set out measurement tools and equipment
checkpoint-status |  |  | checkpoint | Engage certified surveyor for critical set out works
checkpoint-group |  |  | section | Conduit Selection
checkpoint-status |  |  | checkpoint | Identify circuit to be installed, confirm circuit cabling requirement. Select conduit size accordingly
checkpoint-group |  |  | section | Conduit Installation (General)
checkpoint-status |  |  | checkpoint | Conduit to be measured and cut using correct tools
checkpoint-status |  |  | checkpoint | All conduit bends to be sweeping using bending spring. Or large sweeping proprietary bends
checkpoint-status |  |  | checkpoint | All joins to be glued using PVC jointing cement
checkpoint-status |  |  | checkpoint | All conduit boxes to be correct type with correct number of entry points i.e. 2way, 3 way T, 4way
label | 1cd00d6c-5b94-567f-aee8-756f3122b26b |  | note | Do not use corrugated conduit in decks
checkpoint-group |  |  | section | Conduit Installation (Fixing)
checkpoint-status |  |  | checkpoint | Ensure entire conduit installation is fixed to steel work using tie wire
checkpoint-status |  |  | checkpoint | Conduit should be tied to bottom mat of steel
checkpoint-status |  |  | checkpoint | Ensure conduit installation is supported from deck over entire length
label | 52cfc916-b226-550b-b6c8-dbde69cdb977 |  | note | Where deck is post tension and steel support is minimal, use deck chairs and spare steel
checkpoint-group |  |  | section | Cast In Items
checkpoint-status |  |  | checkpoint | Ensure that the void/materials are fixed securely at its final location with the correct dimensions to allow the final equipment to be installed at FFL and Adjacent to walls, floor Boxes & Cast in Light's etc
checkpoint-group |  |  | section | Conduit Installation (Covering)
checkpoint-status |  |  | checkpoint | Ensure sufficient concrete cover can be achieved
checkpoint-group |  |  | section | Earthing
checkpoint-status |  |  | checkpoint | Ensure that if the slab may be used as a floor for showers and bathrooms have an equipotential bond to the steel reinforcement.
checkpoint-group |  |  | section | Concrete Pour
checkpoint-status |  |  | checkpoint | Observe concrete pour with particular attention to critical area
checklist-sectioned |  |  | checklist | 018 - Backbone Copper Cabling |  |  |  |  | Yes | 018 - Backbone Copper Cabling | 3a585098-ea71-43d6-bbbd-bff72352bf5e
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Ensure that the latest drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable has adequate support and does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-group |  |  | section | Installation of Distribution Boards
checkpoint-status |  |  | checkpoint | Ensure the distribution frame is fastened securely and at appropriate height for future maintenance and expansion
checkpoint-group |  |  | section | Termination
checkpoint-status |  |  | checkpoint | Ensure that all cores are punched down with the manufactures punch down tool and in the correct colour Sequence
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Test each pair on the disconnect module for correct wire mapping
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Cross check and verify that the As Built Drawings are Complete and Correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-sectioned |  |  | checklist | 005 - Power |  |  |  |  | Yes | 005 - Power | 3a79caff-5452-4f8d-b5a5-f316dea7ed48
checkpoint-group |  |  | section | Rough In
checkpoint-status |  |  | checkpoint | All fit off Accessories have been signed off for approval by the engineer, architect or consultant
checkpoint-status |  |  | checkpoint | Review drawings and create a list of any RFI's regarding the mounting or install of the Power fit off accessories that are not detailed in the drawings.
checkpoint-status |  |  | checkpoint | All Power circuits are adequately loaded and create a line diagram if required for the circuits.
checkpoint-status |  |  | checkpoint | Wire each zone per the plans. Assure each loom is tied back adequately with hits or on tray to the DB.
checkpoint-status |  |  | checkpoint | Update any changes of "P" numbers as you are roughing in.
checkpoint-status |  |  | checkpoint | Assure that plans have been completely highlighted as the circuits have been roughed in. Provide a photo of this to the Builder on completion
checkpoint-status |  |  | checkpoint | Power Drops have been dropped into place. Notify locations of the walls that can be closed. Assure that fit off sections for Lighting and Comms have also been completed.
checkpoint-group |  |  | section | Fit Off
checkpoint-status |  |  | checkpoint | Have a fresh copy of the plans to highlight as connections are terminated
checkpoint-status |  |  | checkpoint | Assure all terminals, connectors are securely tightened
checkpoint-status |  |  | checkpoint | After all GPO's within ceilings have been terminated. Notify the builder for locations of the ceiling that can be closed. Assure that all fit off of Lighting and Comms within the ceiling has also been completed.
checkpoint-status |  |  | checkpoint | Circuits have been run back to the indicated DB. Circuits have been tightly screwed into RCBO's and cabling neatly installed inside of the panel. Neutrals and earths are install per CB number.
checkpoint-status |  |  | checkpoint | GPO's and other fit off accessories have been installed to locations shown on the latest construction set of plans
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Installation complies with drawings
checkpoint-status |  |  | checkpoint | Complete the attached Power test results for all Power circuits and Sub Main supplies
checkpoint-status |  |  | checkpoint | All Power circuits have been labelled per "DB number - CB number" and affixed to a visible location
checkpoint-status |  |  | checkpoint | Update any changes to drawings and issue as "As-Built".
checklist-sectioned |  |  | checklist | 007 - Communication |  |  |  |  | Yes | 007 - Communication | 70a8739f-5f1a-4b3d-ade2-e76a5c3874c9
checkpoint-group |  |  | section | Rough In
checkpoint-status |  |  | checkpoint | Assure that you have all the relevant drawings onsite and printed to scale
checkpoint-status |  |  | checkpoint | Review all Communication Tech data sheets to assure that cable, jacks etc are being installed per specified
checkpoint-status |  |  | checkpoint | All Communications material has been signed off for approval by the engineer, architect or consultant
checkpoint-status |  |  | checkpoint | Review drawings and create a list of any RFI's regarding the mounting or install of the lights that are not detailed in the drawings.
checkpoint-status |  |  | checkpoint | Mark up Communication plans with the appropriate and approved labelling methodology.
checkpoint-status |  |  | checkpoint | Check that cabling is going to be within the allowed 90m tolerance for the longer runs shown on your drawing.
checkpoint-status |  |  | checkpoint | Update any changes of wire numbers as you are roughing in.
checkpoint-status |  |  | checkpoint | Assure that plans have been completely highlighted as the cables have been roughed in. Provide a photo of this to the Builder on completion
checkpoint-status |  |  | checkpoint | Data drops have been dropped into place. Notify locations of the walls that can be closed. Assure that fit off sections for power and Lighting have also been completed.
checkpoint-group |  |  | section | Fit Off
checkpoint-status |  |  | checkpoint | Have a fresh copy of the plans to highlight as Jacks are terminated
checkpoint-status |  |  | checkpoint | Assure all Jacks, connectors are securely terminated and installed into the corresponding plate or patch panel. Cable to be labelled within 300mm of termination.
checkpoint-status |  |  | checkpoint | After all jacks within ceilings have been terminated. Notify the builder for locations of the ceiling that can be closed. Assure that all fit off of Power and Lighting within the ceiling has also been completed.
checkpoint-status |  |  | checkpoint | Looms that have been run back to the indicated Comms room or Rack. Looms are in no more the 24 cables and have been velcroed every 2-3m. Assure that looms are not fastened via cable ties or Tape.
checkpoint-status |  |  | checkpoint | Cable, jacks and patch panels have been installed to manufacturer's specification
checkpoint-status |  |  | checkpoint | Data outlets have been installed to locations shown on the latest construction set of plans
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Installation complies with drawings
checkpoint-status |  |  | checkpoint | Complete the attached Communications test results for all Comms cables.
checkpoint-status |  |  | checkpoint | All data outlets have been affixed with a label on the plate and patch panel that relates to drawings.
checkpoint-status |  |  | checkpoint | Issue data results to the applicable manufacturer for the applicable warranty certificate.
checklist-flat |  |  | checklist | 014 - Cable Tray / Ladder |  |  |  |  | Yes | 014 - Cable Tray / Ladder | 872cfd43-d3a3-40bf-b269-8cea45825535
checkpoint-status |  |  | checkpoint | Support system suitability sized for expected load
text | b357e526-3b47-5ff5-ac21-e26c05263cff |  | textbox | Expected Load
text | 59f102e6-b80e-5c4e-bf0b-9a9c6fe48f02 |  | textbox | Seismic Restrained
text | 9c7238b7-db4a-5978-a3f3-6475bbde6b30 |  | textbox | Support Bracket is Suitable
checkpoint-status |  |  | checkpoint | Coordination & clearance from other services has been complete
checkpoint-status |  |  | checkpoint | Approx Meterage
checkpoint-status |  |  | checkpoint | Cable support system require equipotential bonding
checklist-flat |  |  | checklist | 013 - Testing and Commissioning |  |  |  |  | Yes | 013 - Testing and Commissioning | 8f33d5d8-9c7b-4408-845e-dcd2749a8176
checkpoint-status |  |  | checkpoint | Project Risk identification and management register.
checkpoint-status |  |  | checkpoint | Identify / acknowledge and manage risks involved with this task.
checkpoint-status |  |  | checkpoint | Correct test equipment to complete the task
checkpoint-status |  |  | checkpoint | The test equipment / multimeters etc must display current calibration information
checkpoint-status |  |  | checkpoint | Ensure the electrician who is to perform the works has been trained on correct operation of test equipment - multimeters
checkpoint-status |  |  | checkpoint | Ensure the electrician who is performing the works is familiar with the installation - If required walk them through the proposed work zone
checkpoint-status |  |  | checkpoint | Ensure the electrician performing the works has the latest redline marks up available and can easily identify circuit arrangements
checkpoint-status |  |  | checkpoint | Visual Inspection
checkpoint-status |  |  | checkpoint | Earth Continuity Resistance
checkpoint-status |  |  | checkpoint | Insulation Resistance
checkpoint-status |  |  | checkpoint | Polarity
checkpoint-status |  |  | checkpoint | Correct Circuit Connections
checkpoint-status |  |  | checkpoint | Earth Fault Loop Impedance
checkpoint-status |  |  | checkpoint | Upon completion of 'dead' testing present all documentation to Site supervisor for approval
checkpoint-status |  |  | checkpoint | Submit test results for review with site management
checkpoint-status |  |  | checkpoint | Test For Voltage
checkpoint-status |  |  | checkpoint | Phase rotation
checkpoint-status |  |  | checkpoint | Earth Fault Loop Impedance
checkpoint-status |  |  | checkpoint | Operation of Residual Current Devices
checkpoint-status |  |  | checkpoint | At works completion confirm all circuit schedules are complete & correct.
checkpoint-status |  |  | checkpoint | All circuit descriptions are clear & worded to be easily understood.
checkpoint-status |  |  | checkpoint | Any circuits not tested remain disconnected from circuit breaker & terminated in BP connected.
checkpoint-status |  |  | checkpoint | All equipment has been labelled in accordance with project requirements, and labelling aligns with as built drawings.
checklist-flat |  |  | checklist | 012 - Fit Off Power, Switches and Accessories |  |  |  |  | Yes | 012 - Fit Off Power, Switches and Accessories | 9a9163e9-5a44-42a4-a8f1-d1462943b998
checkpoint-status |  |  | checkpoint | Ensure the fitting is compliant with Australian standards
checkpoint-status |  |  | checkpoint | Install GPOs / Switches as per manufacturers recommendations
checkpoint-status |  |  | checkpoint | Ensure GPOS are installed using the correct fixings and brackets
checkpoint-status |  |  | checkpoint | Ensure the correct item is being installed at each location prior to fit off (Current rating and Phases required)
checkpoint-status |  |  | checkpoint | Use fire boxes, acoustic boxes etc. where required - if in doubt check with the site manager
checkpoint-status |  |  | checkpoint | Ensure correct weatherproof fittings are used where required
checkpoint-status |  |  | checkpoint | All switches and GPOs are installed in a tradesman like manner, e.g. level.
checkpoint-status |  |  | checkpoint | Ensure that all penetrations through the steel structure have been properly washed before fitting off item
checkpoint-status |  |  | checkpoint | Bushing installed is not able to fall off over time
checkpoint-status |  |  | checkpoint | Penetration is sealed to prevent ingress of vermin before fit off where required.
checkpoint-status |  |  | checkpoint | Visually inspect entire circuit for completeness.
checkpoint-status |  |  | checkpoint | Ensure fittings are protected if required
checklist-flat |  |  | checklist | 003 - Isolation Photos |  |  |  |  | Yes | 003 - Isolation Photos | 9c88d9c5-1891-493e-bc15-bb5988a85918
checkpoint-status |  |  | checkpoint | Attach any relevant documents and photos
checklist-flat |  |  | checklist | 009 - Communication Test Results |  |  |  |  | Yes | 009 - Communication Test Results | a60b99e8-1361-4044-8bd3-ab6e5543ba0a
checkpoint-status |  |  | checkpoint | Test Results - Add Comment
checkpoint-status |  |  | checkpoint | Re Tested
checklist-sectioned |  |  | checklist | 016 - Switchboard Delivery & Pre Energisation Inspections |  |  |  |  | Yes | 016 - Switchboard Delivery & Pre Energisation Inspections | b4e09d1d-e824-4ae3-a754-5750b21708a0
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Fixed Correctly into Position ¦ Fixing Type
text | eefc09b9-df3b-50cc-a7a3-144be9fe3bcb |  | textbox | Seismic Restrained
text | 2d4c0c6b-bb46-5972-9fb5-782eb74f2f04 |  | textbox | Type
checkpoint-group |  |  | section | Visual Checks
checkpoint-status |  |  | checkpoint | Take photos of any damage
checkpoint-status |  |  | checkpoint | Internal Clean
checkpoint-status |  |  | checkpoint | Internal Fixtures, Meter's, CB's etc. Secure
checkpoint-group |  |  | section | Tension Checks
checkpoint-status |  |  | checkpoint | Main switches
checkpoint-status |  |  | checkpoint | Circuit Breakers
checkpoint-status |  |  | checkpoint | Control
checkpoint-group |  |  | section | Isolation Checks Completed
checkpoint-status |  |  | checkpoint | Main switches
checkpoint-status |  |  | checkpoint | Main switches
checkpoint-status |  |  | checkpoint | Circuit Breakers
checkpoint-group |  |  | section | Check Trip Settings & Protective Device Ratings
checkpoint-status |  |  | checkpoint | Review switchboard as built SLD & engineers discrimination study
checkpoint-group |  |  | section | Correct Labelling Has Been Fixed
checkpoint-status |  |  | checkpoint | Review switchboard as built general arrangement and engineers reports
checkpoint-group |  |  | section | Signage
checkpoint-status |  |  | checkpoint | External Doors, Trench Covers & Schedules
checkpoint-group |  |  | section | Insulation & Continuity Test
checkpoint-status |  |  | checkpoint | Insulation & Continuity Test completed
checkpoint-group |  |  | section | Reinstate All Covers / Panels
checkpoint-status |  |  | checkpoint | Switchboard Covers Secured
checkpoint-status |  |  | checkpoint | Ready to Energise
checklist-sectioned |  |  | checklist | 011 - Mains & Sub Mains Installation |  |  |  |  | Yes | 011 - Mains & Sub Mains Installation | b60ec5a6-5733-437b-b3b0-4e52a23bfaa8
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Please attach marked up drawing - Please take photo of title block
checkpoint-status |  |  | checkpoint | All submains dressed in the formation specified on Fredon sub main installation check sheet.
checkpoint-status |  |  | checkpoint | Mechanical protection installed where required.
checkpoint-status |  |  | checkpoint | No cables to be tied to or supported by sprinkler / water pipes.
checkpoint-status |  |  | checkpoint | All submains have been kept clear of sharp edges during installation to avoid damage to insulation.
checkpoint-group |  |  | section | Visual Inspection of Rough In
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion
checkpoint-status |  |  | checkpoint | All relevant drawings checked to ensure that all services have been allowed for
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checklist-sectioned |  |  | checklist | 004 - Lighting |  |  |  |  | Yes | 004 - Lighting | bf55242d-df4f-4920-85b1-bc0a9b104fff
checkpoint-group |  |  | section | Rough In
checkpoint-status |  |  | checkpoint | Assure that you have all the relevant drawings onsite and printed to scale
checkpoint-status |  |  | checkpoint | Review all lighting Tech data sheets to assure that lights are being wired to control type (240v, dali, relay ETC)
checkpoint-status |  |  | checkpoint | All lights and control gear has been signed off for approval by the engineer, architect or consultant
checkpoint-status |  |  | checkpoint | Review drawings and create a list of any RFI's regarding the switching, mounting or install of the lights that are not detailed in the drawings.
checkpoint-status |  |  | checkpoint | All lighting circuits are adequately loaded and create any line diagrams if required for the zoning.
checkpoint-status |  |  | checkpoint | Wire each zone per the plans. Assure each loom is tied back adequately with hits or on tray to the DB
checkpoint-status |  |  | checkpoint | Update any changes of "L" numbers as you are roughing in.
checkpoint-status |  |  | checkpoint | Assure that plans have been completely highlighted as the circuits have been all roughed in. Provide a photo of this to the Builder on completion
checkpoint-status |  |  | checkpoint | Switch drops have been dropped into place. Notify locations of the walls that can be closed. Assure that fit off sections for Power and Comms have also been completed.
checkpoint-group |  |  | section | Fit Off
checkpoint-status |  |  | checkpoint | Have a fresh copy of the plans to highlight as connections are terminated
checkpoint-status |  |  | checkpoint | Assure all terminals, connectors are securely tightened
checkpoint-status |  |  | checkpoint | After all plug bases within ceilings have been terminated. Notify the builder for locations of the ceiling that can be closed. Assure that all fit off of Power and Data within the ceiling has also been completed.
checkpoint-status |  |  | checkpoint | Circuits have been run back to the indicated DB or lighting control panel. Circuits have been tightly screwed into RCBO's and cabling neatly installed inside of the panel. Neutrals and earths are install per CB number.
checkpoint-status |  |  | checkpoint | All light fittings have been checked to be defect free before install.
checkpoint-status |  |  | checkpoint | Lights have been installed to manufacturer's specifications
checkpoint-status |  |  | checkpoint | Lights have been installed to locations shown on the latest construction set of plans
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Installation complies with drawings
checkpoint-status |  |  | checkpoint | Complete the attached Power test results for all lighting circuits
checkpoint-status |  |  | checkpoint | All Lights and control gear is fully functional and set to client requirements
checklist-flat |  |  | checklist | 008 - Power Test Results |  |  |  |  | Yes | 008 - Power Test Results | c4407f29-8ff8-4808-a907-237cb98acc11
checkpoint-status |  |  | checkpoint | Attach any relevant documents and photos
text | 55cbe84c-de30-5f89-a7eb-fed64612dbb6 |  | textbox | RCBO/CB rating
text | 609182ec-afe6-5ad8-a118-77b3c9404c59 |  | textbox | Cable size
text | 0d313e35-4578-55f4-b98c-451137163d8a |  | textbox | Earth size
checkpoint-status |  |  | checkpoint | Visual Field Inspection
checkpoint-status |  |  | checkpoint | Connections Correct
checkpoint-status |  |  | checkpoint | Earth Core Continuity Verified
checkpoint-status |  |  | checkpoint | Insulation Resistance Active to Earth
text | 1a5b495c-54b5-5e6a-93f8-c7f0c58c4055 |  | textbox | MW
checkpoint-status |  |  | checkpoint | Polarity Checked
checkpoint-status |  |  | checkpoint | Fault Loop Impedance
checkpoint-status |  |  | checkpoint | RCD Operation
checklist-sectioned |  |  | checklist | 002 - Isolation Cert |  |  |  |  | Yes | 002 - Isolation Cert | d1b5e4eb-262f-4fb8-8eef-0ec58ff67d38
checkpoint-group |  |  | section | Equipment Details
checkpoint-status |  |  | checkpoint | Attach any relevant documents and photos
text | d9816eb2-6be1-5c56-b351-b81763e8a518 |  | textbox | Plant / Location
text | 4f383b6d-4db5-57ae-9e41-5e65b3e65e31 |  | textbox | Equipment to be isolated
text | 01437cf3-f545-51a9-9fb3-c257ade512e4 |  | textbox | Other equipment affected
checkpoint-group |  |  | section | Isolation Requirement
checkpoint-status |  |  | checkpoint | Attach any relevant documents and photos
text | cb434ee3-bb90-5916-8355-86d84f584ca4 |  | textbox | Switchroom
text | fc017150-51b2-5c7b-b1ac-64e323bc6bfb |  | textbox | Panel / Cubicle
text | 4a0b9704-b17c-59f1-a1fe-7a9cb21c76bc |  | textbox | CB
checkpoint-group |  |  | section | Details of Location
checkpoint-status |  |  | checkpoint | Fuses removed
checkpoint-status |  |  | checkpoint | Isolator off & locked
checkpoint-status |  |  | checkpoint | MCB off & locked
checkpoint-status |  |  | checkpoint | Feeds removed
checkpoint-status |  |  | checkpoint | Lock dog installed on CB's
checkpoint-status |  |  | checkpoint | Tags Fitted
checkpoint-status |  |  | checkpoint | Padlocks fitted
checkpoint-status |  |  | checkpoint | Other
checkpoint-group |  |  | section | Handover of services
checkpoint-status |  |  | checkpoint | Isolations have been installed and proved dead test has been carried out by an ELECTRICALLY AUTHORISED PERSON
checkpoint-group |  |  | section | Point of work prove dead test
checkpoint-status |  |  | checkpoint | A point of work that a ELECTRICALLY COMPETENT PERSON has proven that all circuits/ DB is DEAD
checkpoint-group |  |  | section | Return to service
checkpoint-status |  |  | checkpoint | All work has been completed and isolations have been removed. To be completed by an ELECTRICALLY AUTHORISED PERSON
checklist-sectioned |  |  | checklist | 006 - Switchboard |  |  |  |  | Yes | 006 - Switchboard | d4bf7b20-e27b-426e-a3e4-0a7134ee5e8c
checkpoint-group |  |  | section | Rough In & Fit Off
checkpoint-status |  |  | checkpoint | Switchboard has been signed off for approval by the engineer, architect or consultant
checkpoint-status |  |  | checkpoint | Cable tray and brackets have been installed to allow the install of the New DB.
checkpoint-status |  |  | checkpoint | All Power & Lighting circuit looms are tied back adequately on tray to within the DB.
checkpoint-status |  |  | checkpoint | If Breakers have not be Preloaded, assure that the breakers are installed and are loaded to suit the circuit requirements.
checkpoint-status |  |  | checkpoint | Update any changes of "P" & "L" numbers as you are installing into CB's. Have a template of the DB schedule to update onto as you install.
checkpoint-status |  |  | checkpoint | Assure all terminals, connectors are securely tightened
checkpoint-status |  |  | checkpoint | Installation complies with drawings & standards.
checkpoint-status |  |  | checkpoint | Complete the below testing
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Attach any relevant documents and photos
text | 41858001-f2f0-5749-8d0a-505d2ae42d5b |  | textbox | Test and record phase - phase voltages R-W (L1-L2)
text | d3190fe1-3f33-5588-a9e4-46a202aab775 |  | textbox | Test and record phase - phase voltages R-B (L1-L3)
text | 88158267-cf70-5536-9199-829fbb98084d |  | textbox | Test and record phase - phase voltages B-W (L3-L2)
text | 54a86d78-a397-5860-b1fb-3097411dd1e5 |  | textbox | Test and record phase - neutral voltages R-N (L1-N)
text | 2fe1080b-6712-544f-817d-5ff7a9417283 |  | textbox | Test and record phase - neutral voltages W-N (L2-N)
text | 78d9e32b-f241-5e2b-9635-5eeb8b86c159 |  | textbox | Test and record phase - neutral voltages B-N (L3-N)
text | 69b90a56-f1c8-5da7-b739-87b3ec30afa2 |  | textbox | Test and record phase - earth voltages R-E (L1-E)
text | b6202bd2-a399-530b-a685-67928e954d03 |  | textbox | Test and record phase - earth voltages W-E (L2-E)
text | c536ffa1-a9b7-5e1e-a2ed-09ddabf5faf3 |  | textbox | Test and record phase - earth voltages B-E (L3-E)
checkpoint-status |  |  | checkpoint | Ensure phase rotation is correct (anti-clockwise)
checkpoint-status |  |  | checkpoint | Verify test supplies are functional
checkpoint-status |  |  | checkpoint | Settings per data sheet
checkpoint-status |  |  | checkpoint | All configuration data recorded
checkpoint-status |  |  | checkpoint | Ensure all temporary bridges are removed and isolations reinstated, locked out
checkpoint-status |  |  | checkpoint | Protection settings
checkpoint-status |  |  | checkpoint | Fuse type/ circuit protection ratings recorded
checkpoint-status |  |  | checkpoint | Test certificates
checklist-sectioned |  |  | checklist | 017 - Fibre Optic Cable |  |  |  |  | Yes | 017 - Fibre Optic Cable | dee5c118-22d7-4807-95cf-007c71d0ee2a
checkpoint-group |  |  | section | Cable Installation
checkpoint-status |  |  | checkpoint | Ensure that the latest services and coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Ensure the cable pulling strength is not exceeded as per manufacturer's recommendations
checkpoint-status |  |  | checkpoint | Ensure the cable been loomed in neatly along cable pathway and has adequate service loop's at both origin and destination
checkpoint-group |  |  | section | Termination
checkpoint-status |  |  | checkpoint | Ensure the area for splicing has the appropriate workstation and is in a dust free environment
checkpoint-status |  |  | checkpoint | Cut the last 2 meters of the fibre and remove it to avoid any dirt, or damage from the hauling that may have taken place.
checkpoint-status |  |  | checkpoint | Ensure the cable is stripped using the specialised tools and remove all Gel using telstra wipes if applicable and secure kevlar rope
checkpoint-status |  |  | checkpoint | Ensure all equipment (cleaver and splicer) has been visually inspected, self checked, cleaned and regular servicing has been maintained
checkpoint-status |  |  | checkpoint | Ensure all splicing follows the correct sequence and any cut off shards are accounted for and disposed of correctly
checkpoint-status |  |  | checkpoint | Ensure fobot is securely placed inside enclosure and dust caps installed
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Ensure that OTDR Testing is taken from both directions and at multiple wavelengths and all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-status |  |  | checkpoint | Ensure that Light Source Testing has the correct parameters as per manufacturer and client requirements all results are recorded with their core/cable no as per label on cabinet and latest revision drawings
checkpoint-group |  |  | section | Test Results Recording
checkpoint-status |  |  | checkpoint | Ensure all test results are downloaded and stored in both their native format and as PDF's or safe keeping
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all testing are complete and collate records
checklist-sectioned |  |  | checklist | 01 5 - Horizontal Cabling |  |  |  |  | Yes | 01 5 - Horizontal Cabling | f4dcdc4f-6475-471a-8b60-51c227f96e9f
checkpoint-group |  |  | section | Horizontal Cabling Rough-in
checkpoint-status |  |  | checkpoint | Ensure that the latest services and coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure that the latest coordinated drawings are being referenced
checkpoint-status |  |  | checkpoint | Ensure the cable does need exceed manufactures bending radius and is segregated to other services as per AS S2009:2013
checkpoint-status |  |  | checkpoint | Ensure the cable has adequate support and the pathway is less than 90 m including service loops & goose necks before drops
checkpoint-group |  |  | section | Visual Inspection of Rough In
checkpoint-status |  |  | checkpoint | Visual inspection of rough in carried out to ensure completion.
checkpoint-group |  |  | section | Cabinet
checkpoint-status |  |  | checkpoint | Ensure Cabinet Layouts are installed to the latest drawing layouts with door swing and clearances considered
checkpoint-status |  |  | checkpoint | Ensure cabinet is secured and and all accessories, panels and management installed correctly to latest RU Layout Drawings
checkpoint-status |  |  | checkpoint | Ensure all shielded equipment is earthed and the electrical contractor has supplied an earth with a maximum resistance of 0.5Ω
checkpoint-group |  |  | section | Horizontal Cabling Fit-off
checkpoint-status |  |  | checkpoint | Ensure that cables are bunched into their final looms and dressed throughout the communications room to individual patch panels
checkpoint-status |  |  | checkpoint | Ensure that all cabling is terminated according to communications rack lay out drawings
checkpoint-status |  |  | checkpoint | Ensure that all cabling is terminated has been labelled
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | Cross check and verify that the as built drawings are complete and correct
checkpoint-status |  |  | checkpoint | Verify all inspections are complete and collate records
checkpoint-status |  |  | checkpoint | Verify all testing are complete and collate records