## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Appia Group - Inspection Test Plan - Structural Concrete |  |  |  |  | Yes | Appia Group - Inspection Test Plan - Structural Concrete | 191a8065-b8e6-4ed6-936f-aa3703e023e9
checkpoint-group |  |  | section | 1. Preparation/Sub Base
checkpoint-no-status |  |  | checkpoint | Location of pour
label | 257be722-7a07-5095-8d47-969b1d2a1148 |  | note | Attach markup of pour location
text | 5c784c85-df3e-5150-837b-2b34adbfc659 |  | textbox | Grid Reference / Area
checkpoint-status |  |  | checkpoint | Check works are constructed off the latest revision drawing received
text | df1555fe-6338-5a6a-a4a8-9e1b8eb3ef21 |  | textbox | Confirm drawing number & revision:
checkpoint-status |  |  | checkpoint | Confirm set out as per current drawing
checkpoint-status |  |  | checkpoint | Foundation Preparation Complete
text | 09f5f58c-5516-57de-ae9e-899443dcbed0 |  | textbox | Confirm kPa required:
text | 8a9ab4d3-1cce-52b0-9e64-b5169a427f3e |  | textbox | Geotechnical Engineer Inspection complete
checkpoint-status |  |  | checkpoint | Is blinding required?
text | 1598bc47-cd28-546a-859d-9cef2da40ad1 |  | textbox | Thickness required:
checkpoint-status |  |  | checkpoint | Scabbling/surface required and completed
label | 12b9c5af-fd35-51cb-b535-b6a2a25905f4 |  | note | Photo (if required)
checkpoint-group |  |  | section | 2. Formwork
checkpoint-status |  |  | checkpoint | Bracing/ties are secure and adequately support form structure
checkpoint-status |  |  | checkpoint | Chamfer/fillets required and in place
checkpoint-status |  |  | checkpoint | Set out dimensions as per drawing
checkpoint-status |  |  | checkpoint | Formwork design required?
text | 842299cc-df5f-5f00-b24f-204fb8961f77 |  | textbox | Formwork design drawing No.
checkpoint-status |  |  | checkpoint | Engineer Inspection & sign off complete
label | 73bc09c8-b29c-5fe7-bf55-975c605f9fa5 |  | note | Show Engineers inspection/sign off
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request Kapitol Group and/or Engineer signature
checkpoint-status |  |  | checkpoint | Release oil applied
checkpoint-status |  |  | checkpoint | Formwork clean and clear of debris
label | e2c3f05f-4a6b-5579-be67-4d06e086270f |  | note | Photo to confirm clen
checkpoint-status |  |  | checkpoint | Confirm line and level as per current drawing
checkpoint-status |  |  | checkpoint | Formwork is sufficiently restrained as per approved formwork design to prevent deformation and leaking of grout during concrete placement
checkpoint-group |  |  | section | 3. Reinforcement
checkpoint-status |  |  | checkpoint | Nominal cover of 50mm achieved unless noted otherwise
text | 903eb683-9e6e-5e38-ad72-27f3870c8460 |  | textbox | Confirm cover requirements as per drawings and concrete specification
checkpoint-status |  |  | checkpoint | Bar size and spacing correct as per current drawing
checkpoint-status |  |  | checkpoint | Reinforcement is adequately tied and supported to prevent movement during pour
checkpoint-status |  |  | checkpoint | Bar splice length and location as per current drawing
checkpoint-status |  |  | checkpoint | Starter bar caps installed to exposed bars
checkpoint-status |  |  | checkpoint | Visual check reinforcement installed as per current drawing
label | 84a9f18b-ba57-55a0-8fa3-1531cc36d30e |  | note | Add photos to show reinforcement installed
text | 122bc7c8-4c49-51dc-a0df-3ac0990e41c4 |  | textbox | Add comment (is applicable)
checkpoint-status |  |  | checkpoint | Engineer & Main Contractor inspection complete
label | e15776b7-b003-5fcb-a524-02e33ce2481b |  | note | Upload inspection report
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request Kapitol Group and/or Engineer signature
checkpoint-group |  |  | section | 4. Falsework
checkpoint-status |  |  | checkpoint | Size/Spacing of falsework installed as per current drawing
text | d8d90d6f-30b7-5343-8b8f-22635d193d57 |  | textbox | Reference Drawing No. if applicable
checkpoint-status |  |  | checkpoint | Temporary works design available for falsework and independently verified
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request Kapitol Group and/or Independant verifier signature
checkpoint-status |  |  | checkpoint | Onsite Inspection completed prior to pouring
label | a4352afc-6e7d-51db-8835-7b1ef160cb0b |  | note | Upload inspection report
checkpoint-group |  |  | section | 5. Embedment Items
checkpoint-status |  |  | checkpoint | Water stop/hydrotite installed as per current drawings and manufacturers guidelines
label | 5b02bf40-621d-5c37-9072-629937daa8aa |  | note | Upload photo (If applicable)
checkpoint-status |  |  | checkpoint | Drainage and conduits installed as per current drawings
label | 0cea0b1f-5c2f-5075-bb2e-fdc11509e230 |  | note | Upload photo (If applicable)
checkpoint-status |  |  | checkpoint | Metalwork/Dowels installed as per current drawings
label | 36ff1302-7a73-53b7-81d0-b66ec09568ff |  | note | Upload photo (If applicable)
checkpoint-status |  |  | checkpoint | Block-outs installed as per current drawings
label | 0a138cf3-2bba-56dc-b8da-5a3f2745d71d |  | note | Upload photo (If applicable)
checkpoint-status |  |  | checkpoint | Crack control detail installed as per current drawings
label | 9b23b922-e026-5014-8e4b-ef74cc40e9d5 |  | note | Upload photo (If applicable)
checkpoint-group |  |  | section | 6. H.D Bolts/precast grout tubes/cast in plates
checkpoint-status |  |  | checkpoint | Set out drawing provided
text | 3b78e586-c89f-5ae4-ab0e-b1627e96576b |  | textbox | Reference current drawing number:
checkpoint-status |  |  | checkpoint | Surveyor attended site and completed initial set out
checkpoint-status |  |  | checkpoint | Surveyor has attended site and checked installed bolts/dowels/plates. No wet setting of H.D bolts/rag bolts/grout bars or cast in plates
checkpoint-status |  |  | checkpoint | Surveyor must attend site to confirm items have been installed to correct locations
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request Kapitol Group and/or surveyor signature
checkpoint-group |  |  | section | 7. Final Check
checkpoint-status |  |  | checkpoint | Complete pre-pour inspection items 1 - 6 prior to pour
text | e0d73786-9a92-53f2-bd75-74c718a3210f |  | textbox | Concrete Mix:
text | fff2eda5-0b66-507d-9ac2-783f96b33bb7 |  | textbox | Supplier:
text | 2d51aaaa-a375-52c7-b2b9-1233f4dddbd5 |  | textbox | mPa Required:
text | daa6c409-4fd8-50b3-a1c0-b9bbccee22e5 |  | textbox | Pour Method:
text | 84a4194a-bf03-5c4c-82f9-d39bac62b6be |  | textbox | Comments:
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request Kapitol Group signature
checkpoint-group |  |  | section | Pour Sign Off
checkpoint-status |  |  | checkpoint | Appia Group Foreman and Kapitol Group Representative name entered and signature attached below
holdpoint |  | Multiple signoffs are not allowed | signoff | HOLDPOINT - Click here to add Appia Group Foreman signature
holdpoint |  | Multiple signoffs are not allowed | signoff | HOLDPOINT - Click here to add/request Kapitol Group Representative signature
checkpoint-group |  |  | section | 8. Post Pour Inspection
checkpoint-status |  |  | checkpoint | Curing carried out as per current drawing/concrete specification
checkpoint-status |  |  | checkpoint | Formwork stripped in accordance with specified times on current drawings/concrete specification
checkpoint-status |  |  | checkpoint | All surface defects repaired immediately
label | d00423a8-4dac-5422-a990-a2dddd1ba88c |  | note | Add photo of repair (If applicable)
checkpoint-status |  |  | checkpoint | All areas cleaned and clear of slurry and debris
checkpoint-status |  |  | checkpoint | Surveyor check of H.D bolts/precast grout tubes/dowels/cast in items install
checkpoint-group |  |  | section | 9. Concrete Test Results
checkpoint-status |  |  | checkpoint | Concrete has reached design strength
text | 348030d0-52be-5a76-ba73-b73fc636dc4b |  | textbox | Strength at 7 Days (mPa)
label | d43a824a-1f98-5d33-b95e-6c72533ef4e5 |  | note | Upload test result
text | f7636a20-3e5b-5327-bbcb-01b374b3db5c |  | textbox | Strength at 28 Days (mPa)
label | 6a1adf60-878e-5f85-b325-c890aa78869b |  | note | Upload test result
checklist-sectioned |  |  | checklist | ITP0005 – PT02 FULL DEPTH ASPHALT WORKS | itp |  |  |  | Yes | ITP0005 – PT02 Full Depth Asphalt Works | 53b0cf51-67f8-4733-9d11-af50385d5ec6
checkpoint-group |  |  | section | Subgrade
checkpoint-status |  |  | checkpoint | 1.1 - Test roll subgrade
label | 4fa09423-0e5c-5bb9-a04b-d0273284f297 |  | note | METHOD - T
label | f221a5d2-6d50-539c-9968-4c1fdcdc1373 |  | note | REFERENCE - KAPITOL
label | 2a4a88cb-2bde-55c6-abfd-499245ad1e39 |  | note | CRITERIA - Subgrade to withstand test rolling by the specified plant without visible deformation or springing
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.2 - Testing of subgrade leve
label | ff9abc00-dff4-5b10-ab50-bf07ef1045b2 |  | note | METHOD - T
label | 453c3261-67ff-53e7-bd63-a6814671167b |  | note | REFERENCE - M3-CI-01-8501- [B]
label | 47b7ba05-8de1-59af-be80-1499b7d47c57 |  | note | CRITERIA - Subgrade compacted to 2% CBR Test Details:
label | 98acd160-09bc-5774-b7b2-7856e82b9eef |  | note | VALUE - 2% CBR , Subgrade material – crushed rock / clay
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.3 - Level of sub-grade
label | 32e2a5f1-91c9-5788-adb6-30c3393daf4f |  | note | METHOD - M
label | 18966639-14de-518f-ae74-78c39ecdb30d |  | note | REFERENCE - M3-CI-01-8501- [B]
label | f3ea5e8a-3fe0-5cf7-9afa-c6a051eaaf33 |  | note | CRITERIA - Earthworks shall be finished to conform to the levels, lines, grades and cross-sections specified or shown on the drawings Test Details:
label | 19c7e467-a6ba-56f9-a667-4d1852552198 |  | note | Earthworks shall be finished to conform to the levels, lines, grades and cross-sections specified or shown on the drawings Test Details:
label | fcc314d9-51b1-56a7-bd2f-4e028a845b8c |  | note | Level: mean deviation from design no more than +15 to -30mm, max. below the specified level
label | 34b574f4-78d2-5c41-8969-d5115048f090 |  | note | Thickness: Not more than 15mm less than the specified thickness
label | 2e490e1e-d11d-5da0-b40a-a0f655119883 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
label | 4da50705-bf99-5604-a787-036fcad8ceae |  | note | VALUE - {Value}
checkpoint-group |  |  | section | Filling Works
checkpoint-status |  |  | checkpoint | 2.1 - Fill Layer Thickness (if required)
label | 91d64f38-191e-5d08-87e2-e1c9c0dd09ca |  | note | METHOD - M
label | d557c0f5-e212-5c1d-a12e-14da86c302d5 |  | note | REFERENCE - M3-CI-01-8501- [B]
label | 6bc9a091-c30d-55bf-896b-8ab661fe6469 |  | note | CRITERIA - Spread and compacted in layers not exceeding compacted thickness. Material:
label | a8917173-c091-532e-bdb4-036afefab38e |  | note | Material:
checkpoint-status |  |  | checkpoint | 2.2 - Fill layer Compaction (if required)
label | 4d90a063-3070-5980-8772-80e7b6f31288 |  | note | METHOD - T
label | f3cfe489-6cf7-5ad9-9b21-1bc70364e5d9 |  | note | REFERENCE - M3-CI-01-8501- [B]
label | 61ec3024-ee7a-5d15-ab8d-cde347cb0ab6 |  | note | CRITERIA - The minimum characteristic value of density ratio.
label | b9799def-e9b4-56d3-b7b7-2b33d497fabf |  | note | Material:
label | 0f075eea-50db-5ce4-b49c-53cb4e421eca |  | note | Test Details:
label | 57a6cbc8-f9da-5611-8c1b-ba5cfd3be4e7 |  | note | VALUE - 98% STANDARD COMPACTION
checkpoint-group |  |  | section | Capping Layer – Proposal To Use Class 4 Crushed Rock
checkpoint-status |  |  | checkpoint | 3.1 - Compaction
label | b6895336-8596-50b0-9882-d9d364cd311f |  | note | METHOD - T
label | 13565063-54f3-580a-a3c3-bb0906de12dd |  | note | REFERENCE - M3-CI-01-8501 - [C]
label | 1d326a3c-a7e6-536d-8dc4-123beac96268 |  | note | CRITERIA - Compaction for sub-base layer will not be less than the required characteristic density ratio. 98% standard compaction
label | a1ef877b-7c97-538f-9f9f-a10d9a693d05 |  | note | Test Details:
label | a0e03db6-b03e-5c23-beaf-b13b720bbe6d |  | note | Calculation of density ratio used is Choose an item.
label | e60fc2d9-009a-5a4d-acba-b9d1d4d76c4a |  | note | VALUE - 300mm Thick Class 420mm crushed concrete 150mm
checkpoint-status |  |  | checkpoint | 3.2 - Conformity with drawings
label | bcdcca4d-26db-5244-9f45-8409f42ea643 |  | note | METHOD - V
label | e703ffe1-f144-5307-9c9c-e448603f8fe9 |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 977f0d4d-9709-5c19-972d-e7d129d799e6 |  | note | CRITERIA - Material: 300MM THICK CLASS 4 20MM CRUSHED CONCRETE
label | 67f16592-a52e-56dc-aa4d-e092adbc0e12 |  | note | Thickness: Not more or less than the specified thickness. 300MM
label | dacdb53a-fd25-5901-a723-fb1ec91f6c44 |  | note | Width: +/- 50mm from right angles to the design line.
label | 05d443a2-11f9-52ca-8ea0-e5ef57ea6acb |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | 84c2e112-6749-5a30-8c37-7e475e343a79 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
label | ca5abac8-9442-571a-b4d6-7c784f9f7a50 |  | note | VALUE - {Value}
checkpoint-group |  |  | section | Kerb & Channel
checkpoint-status |  |  | checkpoint | 4.1 - Set out/alignment inspection
label | 5684041c-01da-5f3a-b932-1916a30bcd97 |  | note | METHOD - V
label | e3e471b1-3e19-5def-b408-0e185c0788c8 |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 1933dcc0-6f1c-5680-a876-d50238d0e479 |  | note | CRITERIA - Kerb and channel to be inspected prior to pour
label | 8d9bcaa9-89df-5f38-9f3f-d6164d10a068 |  | note | VALUE - {Value}
checkpoint-status |  |  | checkpoint | 4.2 - Base
label | f8791200-f13b-5225-aa1b-c04d506bc4c3 |  | note | METHOD - V
label | ad6b5d23-978f-50a9-8845-d6905301a947 |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 43947c75-cee7-5651-8c91-22470de87be4 |  | note | CRITERIA - Install kerb and channel in accordance with drawings and requirements AS 2876 and per as Construction Drawing
label | 133ce8e3-858e-5b54-ac51-5b7cc63badec |  | note | Preparation to be minimum 150mm Class 4, 20mm
label | 58b3d92b-afe1-5c14-98db-e829c227c327 |  | note | VALUE - {Value}
checkpoint-status |  |  | checkpoint | 4.3 - Delivery
label | 7c17473a-e9d1-590a-a45a-10bb7c9ae882 |  | note | METHOD - V
label | 1edfdbb6-3003-5035-86b5-1f1d29032e5e |  | note | REFERENCE - M3-CI-01-8501- [C]
label | b41a8bb6-95b7-5374-b6b7-61dd6b2bcc78 |  | note | CRITERIA - Kerb & channel concrete type: 320 kg of cementitious material per cubic meter of concrete – No colour.
label | dc91b0dd-8879-560f-8e24-16f1a56d2f15 |  | note | VALUE - {Value}
checkpoint-group |  |  | section | Sub-base Layer
checkpoint-status |  |  | checkpoint | 5.1 - Compaction
label | 168b2b27-469b-5133-aee6-097e2f973f89 |  | note | METHOD - T
label | 17095423-4ab4-577f-a3f7-a39103a6556d |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 491af33a-4c59-5815-a6ba-128a2818bd8e |  | note | CRITERIA - Compaction for sub-base layer will not be less than the required characteristic density ratio. 98% standard compaction
label | 18a0a9ba-cf15-512e-89d2-99d948cf8992 |  | note | Test Details:
label | a0b07cb5-7c70-518a-8e72-2cd866c48682 |  | note | Calculation of density ratio used is Choose an item.
label | 3a67de75-c0c7-5762-aab2-f2d72ba27a20 |  | note | VALUE - 98% MODIFIED COMPACTION
checkpoint-status |  |  | checkpoint | 5.2 - Conformity with drawings
label | 165b1dba-92b6-5a24-9880-874c3707769d |  | note | METHOD - V
label | 42c1a030-9c3c-524e-b74e-7f6aa581ee7b |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 2958b14e-1408-53e3-9550-c5039e699484 |  | note | CRITERIA - Material: 200mm THICK CLASS 4 20MM FINE CRUSHED CONCRETE
label | 1c14dc69-22a3-58d6-8bb9-d1d5a60aa048 |  | note | Thickness: Not more or less than the specified thickness. 200mm
label | fa5ecef9-082a-579f-a844-810148d66b60 |  | note | Width: +/- 50mm from right angles to the design line.
label | c900dd6e-80db-5d08-8763-bf76708ce73d |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | 6fccd60b-757c-550b-b637-3a855e1bca1c |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
label | 04a93098-ca97-5908-b347-56e1143e5f68 |  | note | VALUE - 200mm Thick Class 420mm crushed concrete 150mm
checkpoint-group |  |  | section | Asphalt Base Coarse
checkpoint-status |  |  | checkpoint | 6.1 - Compaction
label | b99314c0-b0e5-5a3b-bed7-0eb6a4d6ecb2 |  | note | METHOD - V
label | afbf1c7b-72e6-5d77-861e-cfdf77336aeb |  | note | REFERENCE - M3-CI-01-8501- [C]
label | fa4d9610-c14e-51d5-bd16-2221477f122f |  | note | CRITERIA - Material: 65mm THICK COMPACTED ASPHALT TYPE SI – (20MM NOM. MIX)
label | 0d70f479-2e3e-56c5-931a-1e9605e04d9f |  | note | Thickness: Not more or less than the specified thickness. 65MM
label | 30004bd8-b835-5ff0-a380-41c184e4d486 |  | note | VALUE - 65mm THICK COMPACTED SI-SiZE 20mm
checkpoint-status |  |  | checkpoint | 6.2 - Conformity with drawings
label | 7e3ba4da-e6eb-5105-81ce-33367f8a04f3 |  | note | METHOD - V
label | 1f372191-37af-5928-8bb4-f9702eb2bc37 |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 5930ebf7-74c6-57b1-b1b8-a0bf9da59a05 |  | note | CRITERIA - Width: +/- 50mm from right angles to the design line.
label | 809c934b-2bfd-54d6-bd7b-5dcc710b26d7 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | 9fc5df45-584e-54b2-886c-6eff3d8d103a |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm
label | 5ed39fa0-e226-5067-845f-4d4db0bdc4ca |  | note | from a 3m straight edge or 10mm from a 6m straight edge.
label | b7e3442d-ad9d-54aa-822b-bff9d87d5b46 |  | note | VALUE - {Value}
checkpoint-group |  |  | section | Asphalt Intermediate Coarse
checkpoint-status |  |  | checkpoint | 7.1 - Compaction
label | 7ed3aea4-a715-5461-8742-db141ab2184c |  | note | METHOD - V
label | b17884e2-7d97-56cd-a444-09597df0b20d |  | note | REFERENCE - M3-CI-01-8501- [C]
label | f07a4026-60fd-5b01-aa25-d781f63cefec |  | note | CRITERIA - Material: 60mm THICK COMPACTED ASPHALT TYPE SI – (20MM NOM. MIX)
label | 7399433f-3d3a-53aa-a50d-946f31578543 |  | note | Thickness: Not more or less than the specified thickness. 60MM
label | f7326535-484a-5624-8a84-eeae7e9586eb |  | note | VALUE - 60mm THICK COMPACTED H-SiZE 20mm
checkpoint-status |  |  | checkpoint | 7.2 - Conformity with drawings
label | 2553c6c8-7ddf-503e-8351-2850ff16f459 |  | note | METHOD - V
label | 4ae84973-53c4-5ca4-83eb-b4a4a23e85da |  | note | REFERENCE - M3-CI-01-8501- [C]
label | ef0daa8c-e3b1-5c53-9a66-bbd5fce7c8e5 |  | note | CRITERIA - Width: +/- 50mm from right angles to the design line.
label | 8e8dbb57-970c-5230-8a6a-85209bcb3a0c |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | b7360cd7-54bc-5f1c-8d0d-c1bd19aafa80 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
label | 447072f6-6b26-51ae-b3b5-1da0995c7e1e |  | note | VALUE - {Value}
checkpoint-group |  |  | section | Asphalt Wearing Coarse
checkpoint-status |  |  | checkpoint | 8.1 - Compaction
label | be68f45a-fe99-5ebc-854b-2db9bcb2f485 |  | note | METHOD - V
label | b360a226-aabb-5168-ad97-f82a4dff61ed |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 5a73a2be-3e64-53c7-a65a-ea853f2d00a7 |  | note | CRITERIA - Material: 40mm THICK COMPACTED ASPHALT TYPE H – (14MM NOM. MIX)
label | f40b5c1f-f593-5baa-929b-a10276be1c69 |  | note | Thickness: Not more or less than the specified thickness. 40MM
label | 947c1075-6591-56c1-bc89-4c27653745a1 |  | note | VALUE - 40MM THICK COMPACTED H-SiZE 14mm
checkpoint-status |  |  | checkpoint | 8.2 - Conformity with drawing
label | f8cff087-185d-50fe-828a-6bf52d5df63c |  | note | METHOD - V
label | 522a5ce0-f594-52d2-bb23-1eaa3479a585 |  | note | REFERENCE - M3-CI-01-8501- [C]
label | 3a4e4ce9-49b1-5a8d-b0b6-aba4d81507d9 |  | note | CRITERIA - Width: +/- 50mm from right angles to the design line.
label | 91b3c7ca-9732-5f0b-8c23-446b58dc32df |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | cca0e0ce-c876-5a7c-8a6f-2c26aee0cc2a |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
label | 525276bd-5b0e-5187-b7ab-64caaa9df2b1 |  | note | VALUE - {Value}
checkpoint-status |  |  | checkpoint | Final Sign Off
text | 825c6b94-54ed-575a-b1b0-10ed872f1e2c |  | textbox | Person:
text | 255bb755-e556-5c3f-af99-02b72fa92e80 |  | textbox | Print Name:
text | 00961200-64d5-5ef2-9e5b-3e7c37c1b4ac |  | textbox | Date Completed:
holdpoint |  |  | signoff | Add Signature:
checkpoint-status |  |  | checkpoint | Final Sign Off
text | eef24fb4-0ea6-53d8-aa79-42139aa123ab |  | textbox | Person:
text | 2574df1a-f59c-56a3-8a31-288f2411b615 |  | textbox | Print Name:
text | f27ba1f3-b79a-516e-af8d-d92daf854cee |  | textbox | Date Completed:
holdpoint |  |  | signoff | Add Signature:
checklist-sectioned |  |  | checklist | Appia Group - Inspection Test Plan - Concrete Pavement |  |  |  |  | Yes | Appia Group - Inspection Test Plan - Concrete Pavement | 8b7b0dd6-bb1b-4ce3-85c2-f73158bf4c9a
checkpoint-group |  |  | section | 1. Subgrade
checkpoint-no-status |  |  | checkpoint | Location of pour
label | 52b76c55-ce29-51ed-9464-9cb12f5d48b0 |  | note | Attach markup of pour location
text | f363f935-699d-58ce-9cad-e77dfeb3c30e |  | textbox | Grid Reference / Area
checkpoint-status |  |  | checkpoint | Test roll subgrade complete
label | d22912e2-43a3-5032-9dbd-7532995d4454 |  | note | Subgrade able to withstand test rolling by the specified plant without visible deformation or springing
text | 54c26a9f-27fc-5f1a-a7ae-0309d7f2769e |  | textbox | Test roll result
checkpoint-status |  |  | checkpoint | Compaction testing of subgrade level to 98% modified compaction
text | e3e45cdd-b7d4-534b-a73d-16abd201ff63 |  | textbox | Compaction test result
checkpoint-status |  |  | checkpoint | Subgrade level Earthworks shall be finished to conform to the levels, lines, grades and cross-sections specified or shown on the drawings
checkpoint-status |  |  | checkpoint | Width: +/- 50mm from right angles to the design line
checkpoint-status |  |  | checkpoint | Level: mean deviation from design no more than +15mm to -30mm, max below the specified level
checkpoint-status |  |  | checkpoint | Thickness: Not more than 15mm less than the specified thickness
checkpoint-status |  |  | checkpoint | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge
checkpoint-group |  |  | section | 2. Filling Works
checkpoint-status |  |  | checkpoint | Thickness: Spread and compacted in layers not exceeding compacted thickness
checkpoint-status |  |  | checkpoint | Compaction: The minimum characteristic value of density ratio achieved
text | bd99e5b6-ce0c-5c68-9782-849df38fc3e4 |  | textbox | Material:
text | 84841921-61f8-5691-8501-08ee1f330255 |  | textbox | Test Details
checkpoint-group |  |  | section | 3. Sub-Base Layer
checkpoint-status |  |  | checkpoint | Compaction for sub-base layer will not be less than the required characteristic density ratio. 98% standard compaction
text | 2cf8b43d-031e-57d7-be61-6c25cff7daf8 |  | textbox | Test Details:
checkpoint-status |  |  | checkpoint | Material Conforms to drawings: 150mm thick class 4 20mm fine crushed rock
checkpoint-status |  |  | checkpoint | Thickness: not more or less than the specified thickness 150mm
checkpoint-status |  |  | checkpoint | Width: +/- 50mm from right angles to the design line
checkpoint-status |  |  | checkpoint | Level: mean deviation from design no more than +15mm to -30mm, max below the specified level
checkpoint-status |  |  | checkpoint | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge
checkpoint-group |  |  | section | 4. Kerb & Channel
checkpoint-status |  |  | checkpoint | Set Out & Alignment: Kerb & Channel inspected prior to pour
checkpoint-status |  |  | checkpoint | Base: Install kerb & channel in accordance with drawing requirements and AS2876 and per construction drawings
label | 3cd2586c-cc08-5fe0-9c1b-6c4e4f7c822c |  | note | Preparation to be minimum 150mm class 4, 20mm
checkpoint-status |  |  | checkpoint | Kerb & Channel concrete type: 320kg of cementitious material per cubic metre of concrete
checkpoint-group |  |  | section | 5. Base Layer
checkpoint-status |  |  | checkpoint | Compaction for base layer will not be less than the required characteristic density ratio. 98% standard compaction
text | 34d05288-9c97-5053-8b11-c4fba757daa5 |  | textbox | Test Detail:
checkpoint-status |  |  | checkpoint | Material Conforms to drawings: 150mm thick class 3, 20mm fine crushed rock, 3% cement treated.
checkpoint-status |  |  | checkpoint | Thickness: not more or less than the specified thickness 150mm
checkpoint-status |  |  | checkpoint | Width: +/- 50mm from right angles to the design line
checkpoint-status |  |  | checkpoint | Level: mean deviation from design no more than +15mm to -30mm, max below the specified level
checkpoint-status |  |  | checkpoint | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge
checkpoint-group |  |  | section | 6.Formwork
checkpoint-status |  |  | checkpoint | Bracing/ties secure and adequately supporting form structure
checkpoint-status |  |  | checkpoint | Chamfer and fillets installed as per drawing requirements
text | e820815e-b669-590a-a379-75151130d493 |  | textbox | Drawing No:
checkpoint-status |  |  | checkpoint | Dimensions as per drawing requirements
text | 77e3fd9f-2c1f-5bd3-a5a1-2118aba63945 |  | textbox | Drawing No:
checkpoint-status |  |  | checkpoint | Formwork over 2m required Engineered design
checkpoint-status |  |  | checkpoint | Formworks constructed in accordance with engineered design
text | 61a7b94d-2a5d-55ae-b914-ace86fa27651 |  | textbox | Drawing No:
checkpoint-status |  |  | checkpoint | Engineer inspection and sign off completed
label | 76816af2-5349-5eb8-9b9c-fd0fc6e8217d |  | note | Engineers inspection/approval
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request Kapitol Group and/or Engineer signature
checkpoint-status |  |  | checkpoint | Release Oil: Formork coated as nominated with approved non-toxic oil
checkpoint-status |  |  | checkpoint | Formwork clean and free of debris
label | ba952395-a562-5685-b38c-fa00a20dae8a |  | note | Attach photos
checkpoint-status |  |  | checkpoint | Line/Level as per IFC drawings and as per concrete specification
checkpoint-status |  |  | checkpoint | Formwork is sufficiently restrained as per approved formwork design to prevent deformation and leaking of grout during concrete placement
checkpoint-group |  |  | section | 7. Reinforcement
checkpoint-status |  |  | checkpoint | Nominal cover of 50mm unless noted otherwise
label | fa8b0aff-a9b2-5060-a895-961fd2b60636 |  | note | Check cover requirements as per IFC drawings and concrete specification
checkpoint-status |  |  | checkpoint | Size, spacing and location as per IFC drawings
checkpoint-status |  |  | checkpoint | Reinforcement is adequately tied to prevent movement during pouring. Fixing to be as per standard.
checkpoint-status |  |  | checkpoint | Splice location/length as per drawings and notes
label | d7c820da-db7a-5480-9bb6-1c5c05a67a53 |  | note | As per IFC drawing or minimum 40mm x bar diameter
checkpoint-status |  |  | checkpoint | Starter bar caps installed to all exposed bars
checkpoint-status |  |  | checkpoint | Visual check to confirm installation as per drawings
label | 7a40c5e7-295c-5e14-b1bb-2fde22a3850a |  | note | Attach photos
checkpoint-status |  |  | checkpoint | Changes due to RFI's/superseded drawings
text | aded4045-981e-50ac-b776-5f5fe83d1f02 |  | textbox | RFI No:/Drawing No:
checkpoint-status |  |  | checkpoint | Client/consultant inspection complete
label | b5cf89e6-2d49-54b0-9da6-e17f9b483a43 |  | note | Attached consultant inspection report
holdpoint |  |  | signoff | HOLDPOINT - Click here to add/request client/consultant signature
checkpoint-group |  |  | section | 8. Concrete
checkpoint-no-status |  |  | checkpoint | Concrete details
text | 267ace04-cd4b-5451-be2d-37a1ddd23c2e |  | textbox | Concrete Mix:
text | c8141610-8aaf-5c96-ab87-0d7817f5fe22 |  | textbox | Supplier:
checkpoint-status |  |  | checkpoint | Testing Required to AS1379
text | 841a768b-d118-51dc-ada4-72b28edc1497 |  | textbox | Concrete Specification Document:
checkpoint-status |  |  | checkpoint | Mix design approved?
select | 361af934-a65c-50d6-947b-b8efbb1596b6 |  | dropdown | Method of Pour? | Line Pump,Boom Pump,Kibble,Chute,Tremie
checkpoint-group |  |  | section | 9. Final Sign Off
checkpoint-status |  |  | checkpoint | Appia Group Foreman and Kapitol Group Representative name entered and signature attached below
holdpoint |  | Multiple signoffs are not allowed | signoff | HOLDPOINT - Click here to add Appia Group Foreman signature
holdpoint |  | Multiple signoffs are not allowed | signoff | HOLDPOINT - Click here to add/request Kapitol Group Representative signature
checkpoint-group |  |  | section | 10. Post Pour
checkpoint-status |  |  | checkpoint | Curing carried out as per IFC drawings/concrete specification
checkpoint-status |  |  | checkpoint | Formwork stripped in accordance with times specified on drawings/concrete specification
checkpoint-status |  |  | checkpoint | Surface defect repairs: Repair grout to be higher strength than substrate concrete
checkpoint-status |  |  | checkpoint | All areas free from slurry, surfaces cleaned after pour if required
checkpoint-status |  |  | checkpoint | Surveyor to complete as-built of cast in items: HD Bolts/precast dowels/cast in plates etc.
checkpoint-group |  |  | section | 11. Concrete Test Results
checkpoint-status |  |  | checkpoint | Concrete has reached its indicated strength?
text | 068747da-8f49-5b66-b840-8fe76c80adfd |  | textbox | Strength achieved at 7 days (mPa):
text | c9f137e6-fd26-5c87-aecb-b1adcca27671 |  | textbox | Strength achieved at 28 days (mPa):
label | c1b8d987-cf01-5738-afb9-066b3752f1bd |  | note | Concrete test report:
checkpoint-status |  |  | checkpoint | 56 Day shrinkage test is within limits of concrete specification
label | c41f08c5-a400-5971-9b4c-5247b1b3ffc2 |  | note | Appia Group Foreman and Kapitol Group Representative name entered and signature attached below
holdpoint |  | Multiple signoffs are not allowed | signoff | HOLDPOINT - Click here to add Appia Group Foreman signature
holdpoint |  | Multiple signoffs are not allowed | signoff | HOLDPOINT - Click here to add/request Kapitol Group Representative signature
checklist-sectioned |  |  | checklist | ITP002 - Asphalt Pavement Works |  |  |  |  | Yes | ITP002 - Asphalt Pavement Works | 9a07999c-7971-497e-9437-2e85e94eaff8
checkpoint-group |  |  | section | Subgrade
checkpoint-status |  |  | checkpoint | 1.1 Test roll subgrade
label | 0258011b-14a4-5b05-ae4c-f9b9c5ee1f02 |  | note | Subgrade to withstand test rolling by the specified plant without visible deformation or springing.
holdpoint |  |  | signoff | Holdpoint - click to add signature
checkpoint-status |  |  | checkpoint | 1.2.Testing of subgrade level
label | 5728dca9-10a8-5dea-8eeb-5faca3ae751e |  | note | Subgrade compacted to 98% modified
text | aa08191f-983b-592b-b9a7-b0b6abc0cfc7 |  | textbox | Test Details:
holdpoint |  |  | signoff | Holdpoint - click to add signature
checkpoint-status |  |  | checkpoint | 1.3 Level of sub-grade
label | 11903bac-933e-54a2-835d-357fe889783b |  | note | Earthworks shall be finished to conform to the levels, lines, grades and cross-sections specified or shown on the drawings
text | f99ed8a5-9f43-5c06-b6ec-247be0ddf00c |  | textbox | Test Details:
label | b8308ab9-d593-5adb-afc6-93c3431def07 |  | note | Width: ± 50mm from right angles to the design line.
label | 945f6f3b-1d65-5348-bb57-7063a2381558 |  | note | Level: mean deviation from design no more than +15 to -30mm, max. below the specified level
label | e521fe22-cffc-5946-a2fb-86dae6590ee5 |  | note | Thickness: Not more than 15mm less than the specified thickness.
label | 1f0fffbe-5813-5ff3-a7c2-373a89d5965f |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | Filling Works
checkpoint-status |  |  | checkpoint | 2.1 Thickness
label | ade481bc-6068-59ad-b53f-6d229064310e |  | note | spread and compacted in layers not exceeding compacted thickness.
text | 156eedbb-919d-55e6-b740-ec446c8fb0b3 |  | textbox | Material:
checkpoint-status |  |  | checkpoint | 2.2. Compaction
label | 9800f4eb-d63a-5ac6-8820-dd5bb48767c9 |  | note | The minimum characteristic value of density ratio.
text | 141a2996-d35b-5872-bd94-110fd701e72d |  | textbox | Material:
text | 3624a11a-030e-5caa-afbd-2b5f3f339225 |  | textbox | Test Details
checkpoint-group |  |  | section | Sub-base Layer
checkpoint-status |  |  | checkpoint | 3.1 Compaction
label | 5b1c5946-c626-59ea-90ef-fb75afe51b20 |  | note | Compaction for sub-base layer will not be less than the required characteristic density ratio. 98% standard compaction
text | 628b2fbc-a59b-59c0-9e8d-62370a59d202 |  | textbox | Test Details:
select | c29fb1d7-1d89-5493-adf2-f570e496140d |  | dropdown | Calculation of density ratio used is | P =4Rm-284,P =4Rm-292,P =4R-284,No modification
checkpoint-status |  |  | checkpoint | 3.2 Conformity with drawings -
label | 66587483-5ffd-5fc5-9806-a2b31d5b4509 |  | note | Material: 200MM THICK CLASS 2 20MM CEMENT TREATED FINE CRUSHED ROCK
label | 69ac2971-2c23-516e-846d-d48e1c68f746 |  | note | Thickness: Not more or less than the specified thickness. 200MM
label | 77945c01-8d1b-526e-8fe4-c578cc8ddff8 |  | note | Width: +/- 50mm from right angles to the design line.
label | 1f374d99-1338-5707-babb-b766ba22ace6 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | e5b30a8a-5e50-554c-99d2-023c816a6bf2 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | Kerb & Channel
checkpoint-status |  |  | checkpoint | 4.1 Set out/alignment inspection
label | 4a5031c7-bf37-5186-a2f9-ef0b3f55e364 |  | note | Kerb and channel to be inspected prior to pour
checkpoint-status |  |  | checkpoint | 4.2 Base
label | 84039310-0beb-5722-8cff-4afe283def17 |  | note | Install kerb and channel in accordance with drawings and requirements AS 2876 and per as Construction Drawing
label | c0e05af5-cf03-5137-bc5e-931f0fc82d39 |  | note | Preparation to be minimum 150mm Class 4, 20mm
checkpoint-status |  |  | checkpoint | 4.3 Delivery
label | 1ecc8c24-3402-5d61-b4c4-94a0b4bbac5d |  | note | Kerb & channel concrete type: 320 kg of cementitious material per cubic meter of concrete.
checkpoint-group |  |  | section | Base Layer
checkpoint-status |  |  | checkpoint | 5.1 Compaction
label | 1b54d0f5-f279-5ffb-85cc-15c20fafd2c6 |  | note | Compaction for sub-base layer will not be less than the required characteristic density ratio. 100% standard compaction
text | 59d112c1-2d7b-520f-8f6a-256d839e0201 |  | textbox | Test Details:
select | b2da8c1d-7c38-5525-a5b3-11f6f56732e2 |  | dropdown | Calculation of density ratio used is | P =4Rm-284,P =4Rm-292,P =4R-284,No modification
checkpoint-status |  |  | checkpoint | 5.2 Conformity with drawings -
label | 85a5b4a0-afbf-5046-b591-047713b1004b |  | note | Material: 200mm THICK CLASS 2 20MM FINE CRUSHED ROCK
label | fc7427b8-2852-5f07-b1fc-de6d5eb697f2 |  | note | Thickness: Not more or less than the specified thickness. 200mm
label | 30803bf7-2675-5e5d-868d-1669402dec0b |  | note | Width: +/- 50mm from right angles to the design line.
label | dc258d3f-42a0-5347-a8c9-18224c2e6bc6 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | 1c298951-3543-5f35-a963-06b6eff2d95b |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | Asphalt Wearing Coarse
checkpoint-status |  |  | checkpoint | 6.1 Conformity with drawings -
label | daefc76c-0207-5c2f-bb61-8c30a1a2a26c |  | note | Material: 50mm THICK COMPACTED ASPHALT TYPE H – (14MM NOM. MIX)
label | b7cfa906-2fb8-53ef-a777-09b3f74f0456 |  | note | Thickness: Not more or less than the specified thickness. 50MM
checkpoint-status |  |  | checkpoint | 6.2 Conformity with drawings -
label | 7611b40e-71e1-5af6-9041-3fdc1af53379 |  | note | Width: +/- 50mm from right angles to the design line.
label | 6c30144b-0956-5f3d-8ccb-536af67de507 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | 42b47a82-639f-5841-ac2c-0729fa32a9b4 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checklist-sectioned |  |  | checklist | ITP003 - Light Duty Asphalt Pavement Works |  |  |  |  | Yes | ITP003 - Light Duty Asphalt Pavement Works | c89d45ea-9db1-45d6-b5d2-9f11a0a79849
checkpoint-group |  |  | section | Subgrade
checkpoint-status |  |  | checkpoint | 1.1 Test Roll Subgrade
label | 41fc95f5-2f95-58ad-a587-463fe90d23d4 |  | note | Subgrade to withstand test rolling by the specified plant without visible deformation or springing.
holdpoint |  |  | signoff | Holdpoint - click to add signature
checkpoint-status |  |  | checkpoint | 1.2 Testing of subgrade level
label | 56f1da72-f528-5722-8135-d98561bba0a9 |  | note | Subgrade compacted to 98% modified
text | 20d2b9b8-0fea-548b-a005-8cc10653394f |  | textbox | Test Details:
holdpoint |  |  | signoff | Holdpoint - click to add signature
checkpoint-status |  |  | checkpoint | 1.3 Level of sub-grade
label | 2ae83ee5-4b46-51b0-a4bd-6c19e8ee5509 |  | note | Earthworks shall be finished to conform to the levels, lines, grades and cross-sections specified or shown on the drawings
text | 03daf706-fb75-5091-88e3-3f9eda501912 |  | textbox | Test Details:
label | 061e2ff2-3911-5b46-a809-95b7094277b5 |  | note | Width: ± 50mm from right angles to the design line.
label | 7c5eed39-64c2-5c56-9a84-2d9bbaa3b95e |  | note | Level: mean deviation from design no more than +15 to -30mm, max. below the specified level
label | 770bd968-aff9-5744-863b-2a4185902a83 |  | note | Thickness: Not more than 15mm less than the specified thickness.
label | fcbdcef7-5822-56a7-b8fe-3543225d1ea4 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | Filling Works
checkpoint-status |  |  | checkpoint | 2.1 Thickness
label | ee9f725e-d06a-52ae-8f90-3803175bb4c4 |  | note | spread and compacted in layers not exceeding compacted thickness.
text | 3a722e0d-b2f4-56f0-be49-a144d9befa82 |  | textbox | Material:
checkpoint-status |  |  | checkpoint | 2.2 Compaction
label | c8951d8a-e55d-5d43-8f36-c6145d1b6d36 |  | note | The minimum characteristic value of density ratio.
text | 751a1256-b774-5e68-ad08-55d82a614fb6 |  | textbox | Material:
text | d26c501f-07e0-57a4-bc59-a44f3d42bbbb |  | textbox | Test Details:
checkpoint-group |  |  | section | Sub-base Layer
checkpoint-status |  |  | checkpoint | 3.1 Compaction
label | f002813d-bda4-5898-adea-4c1e92419a36 |  | note | Compaction for sub-base layer will not be less than the required characteristic density ratio. 96% standard compaction
text | 411fb071-15cd-543c-9523-29d9e99d6f36 |  | textbox | Test Details:
select | 847b8073-c669-539c-b10e-1d0f72768f33 |  | dropdown | Calculation of density ratio used is: | P =4Rm-284,P =4Rm-292,P =4R-284,No modification
checkpoint-status |  |  | checkpoint | 3.2 Conformity with drawings -
label | 7fd8f385-58d4-533d-a44f-34480e1e8fa7 |  | note | Material: 100MM THICK CLASS 3 20MM FINE CRUSHED ROCK
label | 3d898b46-5f64-582e-a4d8-88e013ead1c5 |  | note | Thickness: Not more or less than the specified thickness. 100MM
label | cb5fd1a7-44fa-5def-b50e-17bffef383f1 |  | note | Width: +/- 50mm from right angles to the design line.
label | 5a038fbb-6ce2-5fff-b38e-bba61924f8f4 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | fcafeebc-ca05-52ec-83ed-d42446bf806a |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | Kerb & Channel
checkpoint-status |  |  | checkpoint | 4.1 Set out/alignment inspection
label | 470766a8-b0bc-562c-aa85-924d026d3534 |  | note | Kerb and channel to be inspected prior to pour
checkpoint-status |  |  | checkpoint | 4.2 Base
label | f8c47762-84e8-5365-978a-2cfe3b1afa53 |  | note | Install kerb and channel in accordance with drawings and requirements AS 2876 and per as Construction Drawing
label | a67e219a-1a7e-59da-9c79-92a210c5f256 |  | note | Preparation to be minimum 150mm Class 4, 20mm
checkpoint-status |  |  | checkpoint | 4.3 Delivery
label | f9495cb2-d471-5898-8ff7-f9d6c62fc253 |  | note | Kerb & channel concrete type: 320 kg of cementitious material per cubic meter of concrete.
checkpoint-group |  |  | section | Base Layer
checkpoint-status |  |  | checkpoint | 5.1 Compaction
label | 94a065e3-aa99-58b9-a95b-e4d93205c0d3 |  | note | Compaction for sub-base layer will not be less than the required characteristic density ratio. 98% standard compaction
text | 1a2160ad-3aae-549f-a332-b392733d2155 |  | textbox | Test Details:
select | 9ada988d-63c2-5551-b48c-65543dfd9723 |  | dropdown | Calculation of density ratio used is | P =4Rm-284,P =4Rm-292,P =4R-284,No modification
checkpoint-status |  |  | checkpoint | 5.1 Conformity with drawings -
label | a1d3e722-5c2f-567d-b71b-f7bb01219a81 |  | note | Material: 100MM THICK CLASS 2 20MM FINE CRUSHED ROCK
label | 5778fceb-d8c9-5302-8e7a-dcedf314925a |  | note | Thickness: Not more or less than the specified thickness. 100MM
label | d27e237d-1240-5896-b324-722292a92f9e |  | note | Width: +/- 50mm from right angles to the design line.
label | 964e025f-bc29-536a-ae85-bf67799d854c |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | 2cd794ad-cee1-51a0-88c2-fd6d76529f25 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | Asphalt Wearing Coarse
checkpoint-status |  |  | checkpoint | 6.1 Conformity with drawings -
label | 373e34dc-15fc-5858-8583-5bd24037b6d2 |  | note | Material: 50mm THICK COMPACTED ASPHALT TYPE N – (10MM NOM. MIX) – CLASS 170 BINDER – WITH PRIMER
label | 0f3e81ef-6031-5bd9-8955-590d1f45c31f |  | note | Thickness: Not more or less than the specified thickness. 30MM
checkpoint-status |  |  | checkpoint | 6.2 Conformity with drawings -
label | 954f00af-0e65-5007-ab52-98806989b47c |  | note | Width: +/- 50mm from right angles to the design line.
label | 61df80ea-f299-525e-9752-3bd9b9ec10a4 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | b24dcaad-150b-56e6-a67e-b368de46c316 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checklist-sectioned |  |  | checklist | ITP004 - Civil Works Type 1 Concrete Pavements |  |  |  |  | Yes | ITP004 - Civil Works Type 1 Concrete Pavements | e8c0d35f-6226-4f44-b135-63c886a101a0
checkpoint-group |  |  | section | Subgrade
checkpoint-status |  |  | checkpoint | 1.1. Test roll subgrade
label | d6e49728-883c-5093-9dff-7ea210246029 |  | note | Subgrade to withstand test rolling by the specified plant without visible deformation or springing.
holdpoint |  |  | signoff | Holdpoint - click to add signature
checkpoint-status |  |  | checkpoint | 1.2.Testing of subgrade level
label | 46b477fc-387c-5459-aff2-74f4c6ba906d |  | note | Subgrade compacted to 98% STANDARD COMPACTION
text | ef0629d1-0863-53f7-b0f0-ad572af66e4e |  | textbox | Test Details:
holdpoint |  |  | signoff | Holdpoint - click to add signature
checkpoint-status |  |  | checkpoint | 1.3. Level of sub-grade
label | 98c8df8c-8d79-56bc-beeb-72b5886a5ba4 |  | note | Earthworks shall be finished to conform to the levels, lines, grades and cross-sections specified or shown on the drawings
text | 2d739c97-1346-5b5e-b43b-401a08ab58c8 |  | textbox | Test Details:
label | 09cfa192-4331-5fa9-844d-bae2a5fd87ff |  | note | Width: ± 50mm from right angles to the design line.
label | 18972a5f-5f89-57a5-ad54-2620f3209f03 |  | note | Level: mean deviation from design no more than +15 to -30mm, max. below the specified level
label | 154a485d-3e54-5d9c-a294-66dbd0c9fd94 |  | note | Thickness: Not more than 15mm less than the specified thickness.
label | c1cfb361-90a4-5b0e-a53f-9b476b13a8c9 |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | 2. Base Layer
checkpoint-status |  |  | checkpoint | 2.1. Compaction
checkpoint-status |  |  | checkpoint | Compaction for sub-base layer will not be less than the required characteristic density ratio. 98% standard compaction
text | f9594698-78f1-541a-9fbb-e9530af31fe9 |  | textbox | Test Details:
select | 126f14c7-0e13-5dfc-af26-b6b201371275 |  | dropdown | Calculation of density ratio used is | P =4Rm-284,P =4Rm-292,P =4R-284,No modification
checkpoint-status |  |  | checkpoint | 2.2. Conformity with drawings
label | ce4cf714-7ad6-5090-8988-7f95b61d6de4 |  | note | Material: 150MM THICK CLASS 2 20MM FINE CRUSHED ROCK
label | 6ea14a79-6d24-5193-bf99-cb243f0e985a |  | note | Thickness: Not more or less than the specified thickness. 150MM
label | 57e9ae5b-498d-53b9-b317-d3470706d57e |  | note | Width: +/- 50mm from right angles to the design line.
label | 7c4dc679-51e3-5d5e-a254-78795719beb3 |  | note | Level: Mean deviation from design no more than +6 to -10mm, max. standard deviation 10.
label | e4d8f027-e9d1-5743-a7a4-209b6fe427af |  | note | Shape: No point on the surface of the pavement layer shall vary by more than 8mm from a 3m straight edge or 10mm from a 6m straight edge.
checkpoint-group |  |  | section | 3. Base Layer
checkpoint-status |  |  | checkpoint | 3.1. Concrete Pour
label | 6ef7f388-b226-5e83-87dc-bddd42083e2a |  | note | Concrete pour 25Mpa 14mm aggregate 80mm slump – 100mm thick, with dowelled expansion joints every 12 meter max centres. Saw cut / tools joints every 1.5 max centres each way
checkpoint-group |  |  | section | Reinforcement
checkpoint-status |  |  | checkpoint | 1.1. Nominal cover of 50mm unless noted otherwise
label | b1839f3b-abb8-575f-badc-7d842a937722 |  | note | Check cover requirements as per IFC drawings & concrete specification document.
checkpoint-status |  |  | checkpoint | 1.2. Size, spacing & location
label | ab1d71f0-77dc-5407-b7d6-3aabbd28e2b3 |  | note | SL62 central
checkpoint-status |  |  | checkpoint | 1.3. Rigidity
label | db19c928-233f-555b-9996-fbfe626f11e0 |  | note | Reinforcement is adequately tied to prevent movement during pouring. Fixing to be as per standard.
checkpoint-status |  |  | checkpoint | 1.4. Visual check
label | c0823e5a-a2a8-5935-bf07-5c7d00a4b252 |  | note | Reinforcement as per IFC drawings
checkpoint-group |  |  | section | Concrete properties
checkpoint-status |  |  | checkpoint | Concrete properties:
text | ee9ea782-9ad0-5865-8f6f-232780ffa0d4 |  | textbox | Concrete mix:
text | 291af7c3-0636-51f0-857b-3c5bb0b142b6 |  | textbox | Supplier:
select | e7f102e0-dd2d-56fc-ac1e-5890b7771034 |  | dropdown | Testing required to AS1379 | Yes,No,N/A
select | 467ab9a0-9a47-537a-b6eb-932ed5bade37 |  | dropdown | Mix Design Approved | Yes,No,N/A
text | 4f444831-e042-5632-b7f6-5fc17d5534ba |  | textbox | Approved By:
select | 951540fa-81c6-5f21-97d5-d1b6550327ff |  | dropdown | Method of Pour: | Line Pump,Boom Pump,Kibble,Chute,Tremie
checkpoint-group |  |  | section | Post pour
checkpoint-status |  |  | checkpoint | 4.1. Curing
label | fa15bcd6-6da0-58e0-90be-7d2b1e0ed10d |  | note | Curing carried out as per IFC drawings / concrete specification
checkpoint-status |  |  | checkpoint | 4.2. Formwork stripped
label | a937468a-7d72-53a6-a959-9ba4a841408d |  | note | Formwork stripped in accordance with specified times on IFC drawings / specifications
checkpoint-status |  |  | checkpoint | 4.3. Surface defect repair
label | bc08fab4-c813-5075-935f-8b385e662c6e |  | note | Repair grout to be higher strength than substrate concrete
checkpoint-status |  |  | checkpoint | 4.4. All areas are clean from slurry
label | aa90fd26-476e-5a07-9a56-4af4e827198d |  | note | Surfaces to be cleaned after pour if required