## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Colphene Uni NG Riser Pit (ITC)
section | Details
checkpoint | Substrate - To Pile Base
button | All surfaces dry, clean, smooth and free from sharp objects, laitance, oils, grease or any foreign materials which may inhibit or reduce adhesion. | Yes,No
button | Commencement of installation shall be taken as acceptance of the substrate by the Applicator | Yes,No
checkpoint | Colphene BSW UNI NG - To Raft Slab
button | Confirm rolls stored upright, with the selvedge side on top. If the product is stored outdoors confirm covered with an protective cover | Yes,No
button | Check COLPHENE BSW UNI NG thickness is 4mm | Yes,No
button | Apply COLPHENE BSW UNI NG loose laid on blinding concrete | Yes,No
button | Confirm minimum 100 mm side overlap | Yes,No
button | Confirm minimum 150 mm end lap between each strip | Yes,No
button | Confirm end laps are staggered by at least 300 mm | Yes,No
button | Confirm laps avoid excessive layering | Yes,No
button | Visual inspection of joint welds at cross laps | Yes,No
button | Confirm no laps at capping beam construction joint | Yes,No
button | Confirm all side laps are sealed and end laps by heat-welding the selvedge with a propane torch and minimum 3-8mm bleed | Yes,No
button | Confirm all angle changes (inside and outside corners) are reinforced by heat-welding on additional 300 mm piece of COLPHENE BSW UNI NG centered on the angle | Yes,No
checkpoint | Colphene BSW UNI NG Reiforcement Strip - Floor/Wall Junction and Existing Wall Upturn
button | Confirm rolls stored upright, with the selvedge side on top. If the product is stored outdoors confirm covered with an protective cover | Yes,No
button | Check COLPHENE BSW UNI NG thickness is 4mm | Yes,No
button | Confirm minimum 100 mm side overlap | Yes,No
button | Confirm minimum 150 mm end lap between each strip | Yes,No
button | Confirm end laps are staggered by at least 300 mm | Yes,No
button | Confirm laps avoid excessive layering | Yes,No
button | Visual inspection of joint welds at cross laps | Yes,No
button | Confirm no laps at capping beam construction joint | Yes,No
button | Confirm all side laps are sealed and end laps by heat-welding the selvedge with a propane torch and minimum 3-8mm bleed | Yes,No
checkpoint | WPA Injection System - To Insitu Wall Junctions with Slab, Existing Wall and Itself
button | Verify all components for installation are in the kit | Yes,No
button | Verify kit is not damaged | Yes,No
button | Install and fix hose to construction joins | Yes,No
button | Install Injection box(es) in agreed locations | Yes,No
button | Feed hoses into injection boxes | Yes,No
button | Clip and cap hoses | Yes,No
checkpoint | Colphene BSW UNI NG - To Insitu Walls
button | ANTIROCK PRIMER can be applied with a brush or roller on clean, dry substrates free of any residue that may hinder adherence. Shake well before using. | Yes,No
button | It must be thoroughly dry before applying the waterproofing membrane. Drying time will vary depending on air and surface temperature and humidity. | Yes,No
button | Confirm rolls stored upright, with the selvedge side on top. If the product is stored outdoors confirm covered with an protective cover | Yes,No
button | Check COLPHENE BSW UNI NG thickness is 4mm | Yes,No
button | Confirm minimum 100 mm side overlap | Yes,No
button | Confirm minimum 150 mm end lap between each strip | Yes,No
button | Confirm end laps are staggered by at least 300 mm | Yes,No
button | Confirm laps avoid excessive layering | Yes,No
button | Visual inspection of joint welds at cross laps | Yes,No
button | Confirm no laps at capping beam construction joint | Yes,No
button | Confirm all side laps are sealed and end laps by heat-welding the selvedge with a propane torch and minimum 3-8mm bleed | Yes,No
button | Confirm all angle changes (inside and outside corners) are reinforced by heat-welding on additional 300 mm piece of COLPHENE BSW UNI NG centered on the angle | Yes,No
checkpoint | Sopradrain 20 - To Insitu Walls
button | The substrate must be firm, even, clean and free from loose materials or any construction debris on the surface. | Yes,No
button | Install SOPRADRAIN 20 with the geotextile facing the backfill. | Yes,No
button | Join by simply butting edge to edge and overlapping the geotextile overhang and securing with reinforced canvastape | Yes,No
button | Terminate SOPRADRAIN 20 by nailing pressure bar at required height | Yes,No
checkpoint | WPA 100 - To Top of Raft Slab
button | Mix well the product before use | Yes,No
button | WPA100 is applied with a with a brush or a roller in two (2) layers. Application must be a minimum of 2 coats @ >= 1.2kg/m2 per coat to achieve a dry film thickness not less than 2mm as per the technical data sheet. | Yes,No
button | Ready to recoat after 2 hours. Dry: 24 hours (remains tacky to touch). | Yes,No
button | Store WPA 100 in chemical bunds provided by Delta | Yes,No
checkpoint | CHECKLIST COMPLETE AND SIGNED
button | ITC completed | Yes,No
checklist | Colphene Uni NG Riser Pit ITP
section | Details
checkpoint | CAPPING BEAM WATERPROOFING ITP
button | Sample Submissions Approved | Yes,No
button | Shop Drawings Approved | Yes,No
button | Colphene BSW UNI NG Installed - To Raft Slab Blinding | Yes,No
button | Colphene BSW UNI NG Upturn to Installed - Existing Wall | Yes,No
button | Colphene BSW UNI NG Reiforcement Strip Installed - Floor/Wall Junction | Yes,No
button | Injection System Installed - To Insitu Walls | Yes,No
button | Primer Installed - To Insitu Walls | Yes,No
button | Colphene BSW UNI NG Installed - To Insitu Walls | Yes,No
button | Sopradrain Installed - To Insitu Walls | Yes,No
button | WPA 100 Installed - To Top of Raft Slab | Yes,No