## F-S Rev02
CIVIL INSPECTION & TEST PLAN
T3084984 - Wiri RAP Interface Returns - ITP |  |  |  |  | Rev: | Originator | Date | Approved | Date
[5 empty] | 0 | Cameron Hinge | 2024-06-14
| H - HOLD |  | CR - Contractor Representative |  | 1
| P - PERFORM |  | CTS - Channel Representative Signoff
| W - WITNESS |  | CTS CI - Channel Civil Inspector
R - REVIEW
ITEM | TASK | SPECIFICATION REFERENCE | ACCEPTANCE CRITERIA | DATE/SIGN |  |  | COMMENTS
1 | Issued For Construction Drawings | IFC Drawings Issued by Client/Engineer | Issued For Construction Drawings Available | Contractor Rep - H
2 | Underground Services Confirmation | CTS Permit to Work | Underground Services Drawings to accompany permit and marked out onsite where excavation is to be undertaken | Contractor Rep - P CTS Civil Inspector - R
3 | Survey & Setout | IFC Drawings CTS General Civil Construction Spec CTS Excavation Works Spec | Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing. | Contractor Rep - P
4 | Waste Management & Disposal | CTS General Civil Construction Spec CTS Excavation Works Spec CTS Contaminated Environmental Ground Soil Managenet Plan RW-231 | Waste management plan prepared and followed. Supporting documents available on request | Contractor Rep - P CTS Civil Inspector - R
P1185A
5A | Demolition | IFC Drawings | Existing pedestal removed at ground level Concrete removed to approved landfill | Contractor Rep - P CTS Civil Inspector - R
5B | Position of Pump Pedestal Setout | IFC Drawings | Setout as per IFC Drawings | Contractor Rep - P CTS Civil Inspector - R
5C | Pump pedestal location Cleaned & Scabbled | IFC Drawings | Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour | Contractor Rep - P CTS Civil Inspector - R
5D | Cast in Items - Bolts & Nuts | IFC Drawings CTS General Civil Construction Specification CTS Epoxy Grouting of Anchor Bolts Manufacturers Documentation Inspection Records | If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings Drilled holes for Anchors shall be inspected Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings | Contractor Rep - P CTS Civil Inspector - R
5E | Formwork, Reinforcing & Concrete | IFC Drawings CTS General Civil Construction Specification NZS3109/3112 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing and formwork to comply with IFC drawings Concrete to be min 30MPa at 28 days Testing of concrete per CTS Specifications Prepour Inspection Record Filled out Prior to Concrete | Contractor Rep - P CTS Civil Inspector - H
5F | Grouting of Baseplate | IFC Drawings CTS General Civil Construction Specification Manufacturers Documentation | Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings | Contractor Rep - P CTS Civil Inspector - W
P1158B
6A | Demolition | IFC Drawings | Existing pedestal removed at ground level | Contractor Rep - P CTS Civil Inspector - R
6B | Position of Pump Pedestal Setout | IFC Drawings | Setout as per drawings | Contractor Rep - P CTS Civil Inspector - R
6C | Pump Pedestal Location Cleaned & Scabbled | IFC Drawings | Foundation area cleaned and free from contamination and dust/oil or grease, surface roughened to accept further concrete pour | Contractor Rep - P CTS Civil Inspector - R
6D | Cast in Items - Bolts & Nuts | IFC Drawings CTS General Civil Construction Specification CTS Epoxy Grouting of Anchor Bolts Manufacturers Documentation Inspection Records | If drilled in, Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings Drilled holes for Anchors shall be inspected Cast in anchor bolts shall be set to spec in IFC drawings and positioned with template to design measurenments in IFC drawings | Contractor Rep - P CTS Civil Inspector - R
6E | Formwork, Reinforcing & Concrete | IFC Drawings CTS General Civil Construction Specification NZS3109/3112 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing and formwork to comply with IFC drawings Concrete to be min 30MPa at 28 days Testing of concrete per CTS Specifications Prepour Inspection Record Filled out Prior to Concrete | Contractor Rep - P CTS Civil Inspector - H
6F | Grouting of Baseplate | IFC Drawings CTS General Civil Construction Specification Manufacturers Documentation | Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings | Contractor Rep - P CTS Civil Inspector - W
PSS3259 - F1 Pipe Foundation
7A | Setout of Pipe Sleeper | IFC Drawings | Comply with setout in drawings | Contractor Rep - P CTS Civil Inspector - R
7B | Excavation & Foundation Preparation inc Site Concrete | IFC Drawings CTS Excavation Works Specification CTS General Civil Construction Specification | Excavated as per IFC drawings to line and levels shown Foundation compaction Inspection Record completed | Contractor Rep - P CTS Civil Inspector - W
7C | Formwork, Reinforcing & Concrete | IFC Drawings CTS General Civil Construction Specification NZS3109/3112 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing and formwork to comply with IFC drawings Concrete to be min 30MPa at 28 days Testing of concrete per CTS Specifications Prepour Inspection Record Filled out Prior to Concrete | Contractor Rep - P CTS Civil Inspector - H
PSS3263 - F1 Pipe Foundation
8A | Position of Pump Pedestal Setout | IFC Drawings | Setout as per drawings | Contractor Rep - P CTS Civil Inspector - R
8B | Excavation & Foundation Preparation inc Site Concrete | IFC Drawings CTS Excavation Works Specification CTS General Civil Construction Specification | Excavated as per IFC drawings to line and levels shown Foundation compaction Inspection Record completed | Contractor Rep - P CTS Civil Inspector - W
8C | Formwork, Reinforcing & Concrete | IFC Drawings CTS General Civil Construction Specification NZS3109/3112 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing and formwork to comply with IFC drawings Concrete to be min 30MPa at 28 days Testing of concrete per CTS Specifications Prepour Inspection Record Filled out Prior to Concrete | Contractor Rep - P CTS Civil Inspector - H
P1185A/B Slab Extension
9A | Position of Slab Extension Setout | IFC Drawings | Setout as per drawings | Contractor Rep - P CTS Civil Inspector - R
9B | Excavation & Foundation Preparation inc Site Concrete | IFC Drawings CTS Excavation Works Specification CTS General Civil Construction Specification | Excavated as per IFC drawings to line and levels shown Foundation compaction Inspection Record completed | Contractor Rep - P CTS Civil Inspector - W
9C | Formwork, Reinforcing & Concrete | IFC Drawings CTS General Civil Construction Specification NZS3109/3112 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing and formwork to comply with IFC drawings Concrete to be min 30MPa at 28 days Testing of concrete per CTS Specifications Prepour Inspection Record Filled out Prior to Concrete | Contractor Rep - P CTS Civil Inspector - H
PSS3272/3273 Slab Extension
10A | Position of Slab Extension Setout | IFC Drawings | Setout as per drawings | Contractor Rep - P CTS Civil Inspector - R
10B | Excavation & Foundation Preparation inc Site Concrete | IFC Drawings CTS Excavation Works Specification CTS General Civil Construction Specification | Excavated as per IFC drawings to line and levels shown Foundation compaction Inspection Record completed | Contractor Rep - P CTS Civil Inspector - W
10C | Formwork, Reinforcing & Concrete | IFC Drawings CTS General Civil Construction Specification NZS3109/3112 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing and formwork to comply with IFC drawings Concrete to be min 30MPa at 28 days Testing of concrete per CTS Specifications Prepour Inspection Record Filled out Prior to Concrete | Contractor Rep - P CTS Civil Inspector - H
11 | Complete final Civil Inspection and close off ITP | IFC Drawings CTS General Civil Construction Specification Manufacturers Specification | ITP/QC has been completed; all steps & hold points signed byrelevant party. All work completed as per work pack, and any field instructions issued during construction compiled | Contractor Rep - P CTS Civil Inspector - H
12 | Non-Conformance Reporting | UCC Internal NCR and or Lucidity event NCR QC Requirements for Civil Works | All Non-Conformance reports and Investigations are attached and closed out | Contractor Rep - R
13 | As Built & Final Design Documentation |  | Confirmation From Engineer on as built records & redline mark ups | Contractor Rep - P
14 | Reference Info, Specifications |  | All Reference Information and relevant Product Specifications
15 | Punch Listing | CTS QC Requirments for Civil Work | All punch list items are closed out in the relevant timeframe to the required standard | Contractor Rep - P Project/Construction Engineer - R
16 | Compilation of ITP |  | ITP Completed and Signed off | Contractor Rep - H Project/Construction Engineer - H