## Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | ZENT-ITP-7039 - ITP - Electrical - Substation L2 |  | ZENT-ITP-7039 - ITP - Electrical - Substation L2 |  | 244c8c7d-159d-4885-a206-be783550f853
| section | SECTION 1 - GENERAL
| checkpoint | General
cd12fa75-dd46-5b7e-be1a-045612531231 | note | ITP Template No.: ZENT-ITP-7039
e9436eb0-2a2b-5ff5-aff2-af265dd9cabc | note | Revision: A
4696fa56-7457-5b96-9b87-1f7867f99513 | note | Prepared By: Brendan King
4393ba64-a113-54d6-9e3a-43ee7d88648c | note | Prepared Date: 19/12/2023
f34d61ad-5257-5b9d-b0d6-e434d9f7ac3a | note | Approved By: Brendan Hile
bd1fafc3-b844-5cbd-8527-7bc10fc0e626 | note | Discipline: Electrical
e0c981cf-328c-59d1-9b58-67aa92eaa041 | note | Component: ITP - Electrical - Substation L2
| section | SECTION 2 - CLOSE OUT SIGNATURE (ZENVIRON ONLY)
| checkpoint | Close Out Signature
1633aa03-5c9e-5471-8b1c-af85e7bfe3bd | textbox | Name:
4afe97f2-4267-5fb5-ba80-cd5893d2d486 | textbox | Position:
68182205-2f04-5573-85fb-a99c8589401e | date | Date:
| signoff | Signature:
| section | SECTION 4 - Level 2 - Pre-commissioning/Secondary System Tests
| checkpoint | 4.1 - Earthing System Tests
b2771fdd-06c8-5953-a831-680fad4386dd | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Injection tests on earthing system to measure transfer of potential, continuity, step & touch voltages.
2099afad-eca9-5e0c-a6b9-df61e8c073c8 | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
71ee7f91-32c7-5ad4-bc8d-3750e1dc3f44 | note | VERIFYING DOCUMENT: Substation Earthing Commissioning Report ZX115-REP-7901
470353d7-8118-5759-bb39-96a620d4d77d | note | SUPERVISION TYPE: N/A
| checkpoint | 4.2 - 330/33kV Main Transformer
7b0329a7-40f0-5e35-bf1f-ca88bacf3d7e | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Post assembly inspections of main power transformer
51e6569f-48e2-5faf-938e-242fb363f2f3 | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
0b68c588-b3c9-5a19-bdb0-3751963f905f | note | VERIFYING DOCUMENT: Subcontractor/OEM Documentation 1 Per Item
88fdaf7d-8bb6-5934-bf6e-6902c1944c17 | note | SUPERVISION TYPE: N/A
| checkpoint | 4.3 - 330kV Circuit Breaker
12898e79-8544-5728-892a-d3be63947cba | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of 330kV Circuit Breakers Incl
f5dbec5f-6346-5282-ae35-5af3fe91e345 | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
0aa28c7b-3407-5724-a0ea-24734ec0b0e5 | note | VERIFYING DOCUMENT: ZX115-ITR-7361 Outdoor Circuit Breaker and/or Subcontractor/OEM Documentation 1 Per Item
f5ceb2f5-ce4b-5ef0-b1cc-47c4b125b941 | note | SUPERVISION TYPE: N/A
| checkpoint | 4.4 - 330kV Disconnector / Earth Switch
2d8da91c-e2a9-5823-89ea-86aa66505076 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of 330kV Disconnector/EarthSwitch(s)
90fe1067-f749-5b99-9565-2b65769052dc | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
c5d7a609-9911-5b7a-8146-3bb53a11ad00 | note | VERIFYING DOCUMENT: ZX115-ITR-7362 Outdoor Disconnector and/or Subcontractor/OEM Documentation 1 Per Item
2cd0bad1-b471-5c44-8a47-0c1691d4633c | note | SUPERVISION TYPE: N/A
| checkpoint | 4.5 - 330kV Voltage Transformer
f7f01fba-ab92-54db-aae0-231a727a8c4b | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of the Voltage Transformer(s)
2c0bbcc6-1c31-5c2f-945f-9c91ea909bb0 | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
a885015c-708e-557e-a23d-e95f071d9e64 | note | VERIFYING DOCUMENT: ZX115-ITR-7379 Outdoor Voltage Transformer 1 Per item
bf288893-8988-580b-a598-c1acff778a1f | note | SUPERVISION TYPE: N/A
| checkpoint | 4.6 - 330kV Current Transformer
d4dbde08-df0e-5303-b3be-e1ddcd65152e | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of the Current Transformer(s)
a9554c36-21d5-5f04-95c7-07981a34fadb | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
57715020-90fd-5e82-a424-3c251749af9f | note | VERIFYING DOCUMENT: ZX115-ITR-7364 Outdoor Current Transformer 1 Per item
b8fd7e86-251e-5594-9c88-148557dbcc01 | note | SUPERVISION TYPE: N/A
| checkpoint | 4.7 - 330kV Overhead Busbar and Flexible Conductor
556f53ea-a0fd-585f-b330-12f18cfd3951 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Ductor and insulation resistance testing of 330kV Overhead Busbar and Flexible Conductor
e4f5fad4-627e-5b77-925c-a1579376658d | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
927e7443-e0d5-5e2d-a56f-c494916cb1b0 | note | VERIFYING DOCUMENT: ZX115-ITR-7368 Level 2 ITR Overhead Rigid Busbar/Flexible Conductor 1 Per Bay or Section (Or replaced by equivalent Subcontractor Documentation)
412ec2a6-ac05-5c24-93ea-604902ba18a0 | note | SUPERVISION TYPE: N/A
| checkpoint | 4.8 - Neutral Earthing Resistor
1444dbe3-ad4c-5d63-a8f9-d0017bbbf52a | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of the Neutral Earthing Resistor
6740b401-a9c4-5c5d-bc3c-d3f877a15eec | note | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
4e65f49b-1f8b-5752-8574-5936dab3a826 | note | VERIFYING DOCUMENT: ZX115-ITR-7380 Neutral Earthing Resistor and/or Subcontractor/OEM Documentation 1 Per Item
2bfe699d-223f-50af-9fed-79445ab4b46b | note | SUPERVISION TYPE: N/A
| section | SECTION 5 - Level 2 - Completion
| checkpoint | 5.1 - Redline markup of Construction Drawings
ae9f29dd-342a-5bab-8563-bbb7f1326750 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Redline markup of relevent Construction Drawings in Master Drawing Folder
3e8ac50e-8292-54fc-8642-ad885228f0b6 | note | ACCEPTANCE CRITERIA: In line with ZX115-REP-0201 Earthworks, Roads and Drainage Specification and BMS- WIN-1024 - Document Red-Line Markup
e70c7b4a-3a5b-5bcb-b68c-f987f07c8736 | note | VERIFYING DOCUMENT: Redline Markup in Master Drawing Folder
408f9ce1-9984-5779-bdd0-432e52564590 | note | SUPERVISION TYPE: N/A
| checkpoint | 5.2 - Generate Punch List
851566ca-ff95-59aa-be41-962be4484b7d | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Subcontractor walk-down inspection
7f6c5663-6894-509a-80f4-70edd6c512fa | note | ACCEPTANCE CRITERIA: Generate specific area/scope Punch List and transfer the open items to the Punch List Master Register
11738bc2-5f98-536d-8d52-bd4ef51e87b7 | note | VERIFYING DOCUMENT: BMS-TMP-0044 Punch List record
8182996e-116f-5258-9599-6248f46ae620 | note | SUPERVISION TYPE: N/A
| checklist | ZENT-ITR-7550 - Outdoor Circuit Breaker - L2 |  | ZENT-ITR-7550 - Outdoor Circuit Breaker - L2 |  | 79ec035d-0c1a-4d40-9d52-f4b077dfc43d
| section | 1. GENERAL
| checkpoint | General
d519fb83-56ce-5af4-83c0-4ae38469c90e | textbox | Project Name:
ddf79230-02b8-5e02-8a86-8fe2ac2a7756 | textbox | Project No.:
f0b80abf-7840-59dd-9690-0f503a7e2372 | note | ITR Description: Outdoor Circuit Breaker - L2
3ef031ad-b67e-57c9-b57c-59cf8c8660d2 | note | ITR Template No.: ZENT-ITR-7550
c2ce3117-290c-570c-8232-18ad5a67650d | note | Rev.: 0
f6844734-bd4e-508b-a5b3-eaeb9aabe6a2 | note | ITR Level: Level 2
| section | 2. SUBCONTRACTOR
| checkpoint | Subcontractor
6b7050f2-9152-5d80-911d-a93c9843eea6 | textbox | Company:
3f5ea2a6-995e-5fbd-94e0-16fefbd2df54 | textbox | Supervisor:
8ec6a087-628d-54d4-a0f5-63be13798fc8 | textbox | Scope of Work:
ed3ed806-ce81-5365-9c42-54c56db45775 | textbox | Contract No.:
| section | 3. INSPECTION AND TEST DETAILS
| checkpoint | Inspection and Test Details
7d967ef0-4071-546b-b9d6-e4a00306c5e7 | radio | Is HOLD POINT applicable? | Yes,No
f944b1a7-2c0c-5ce5-a70c-9f3cbcc8df50 | radio | Is WITNESS applicable? | Yes,No
7f9cb5f7-c61d-5ba1-add9-2b5992b4b207 | textbox | ITP Reference: |  |  | Choose an item
812f41e8-a0f5-5c50-b1a2-3e28decb9be7 | textbox | Location:
92380a97-9067-5239-a79e-d875ba8265c1 | textbox | Drawings Ref.:
8e2f6f15-040c-5fe6-a058-499c25af779f | textbox | Specification Ref.: |  |  | Choose an item
| section | 4. EQUIPMENT DETAILS
| checkpoint | Equipment Details
13ef1a68-2b11-53b1-a69c-e3f291d5c557 | textbox | Description:
2899f265-c95c-54cd-8010-f13da35a85ef | textbox | Model Number:
1985c0a5-0b1a-51b8-9210-aef45e9ee35f | textbox | Manufacturer:
615711d7-3a7f-5c81-8eac-6f95c4d3f9fd | textbox | Serial Number:
| section | 5. TEST EQUIPMENT: ***WARNING - Always ensure circuits are de-energised before connecting test equipment***
| checkpoint | Insulation resistance Tester
2e31ce53-f850-5294-b849-1de2d9fe7744 | textbox | Make / Model
9c10a36b-009f-5c51-a174-1cd95daff63d | textbox | Serial Number
dbe0a295-744b-52f4-b028-2c9244518cec | date | Calibration Due Date
| checkpoint | Ductor Tester
8df0c528-b66c-5810-954c-61ec99f08b14 | textbox | Make / Model
466cb77e-766f-54e4-a364-4a59f0f55388 | textbox | Serial Number
5eb50de4-9068-581f-8b3c-8855f5919c37 | date | Calibration Due Date
| section | 6. INSPECTION POINTS: Insulation Test Result - Main contacts closed
| checkpoint | Aa - BbCcE
286a9aed-aab8-52dd-91eb-36147a682ba4 | textbox | IR Test: Voltage (V)
c58b7c1a-b4b9-5575-b562-bd755033785a | textbox | IR Test: Duration (s)
df1ccc05-d0ff-5ee6-8dbe-c246ef80205f | date | IR Test: Resistance (GΩ)
| checkpoint | Bb - AaCcE
16ab0ece-4bdb-5be0-b07b-0eeeee90d6fd | textbox | IR Test: Voltage (V)
cefcb82c-978e-5906-8b37-2f3f9d5717f0 | textbox | IR Test: Duration (s)
f3402cd0-6407-5413-88a0-33820e956bbe | date | IR Test: Resistance (GΩ)
| checkpoint | Cc - AaBbE
88a86409-b79f-5271-bcb8-932f541c9873 | textbox | IR Test: Voltage (V)
105c930d-b34f-5cb7-bed2-c084fd92bb16 | textbox | IR Test: Duration (s)
003730e4-33e3-5a56-9141-15c9487dac73 | date | IR Test: Resistance (GΩ)
| section | 6. INSPECTION POINTS: Insulation Test Result - Main contacts open
| checkpoint | A - aBbCcE
db60bd6b-cea3-5e44-a5a7-636944d52f79 | textbox | IR Test: Voltage (V)
df25a99a-8ef8-5a44-9b8f-c6134cbb0951 | textbox | IR Test: Duration (s)
738d6d59-1ea0-58f3-9664-09c0b1b72886 | date | IR Test: Resistance (GΩ)
| checkpoint | B - aAbcCE
ab84616f-61ec-555b-811f-c9260893104f | textbox | IR Test: Voltage (V)
01765b99-4eb1-5722-86cf-dcf5c8a2c4a0 | textbox | IR Test: Duration (s)
3a7589bd-69bb-546f-8a88-435185ddd141 | date | IR Test: Resistance (GΩ)
| checkpoint | C - aAbBcE
a084aef0-a7be-57a8-808d-afb139631239 | textbox | IR Test: Voltage (V)
35a482e0-49f6-50e0-8e16-502bfa535eb9 | textbox | IR Test: Duration (s)
16039cb2-443e-5fce-9921-714220cd9270 | date | IR Test: Resistance (GΩ)
| checkpoint | a - ABbCcE
9c4d03b2-4281-5448-b306-0942173e2874 | textbox | IR Test: Voltage (V)
e410d17f-2659-5bc0-bab1-09dd4f61a658 | textbox | IR Test: Duration (s)
5585a50a-3f8b-5d9c-a3a0-92d8dd843460 | date | IR Test: Resistance (GΩ)
| checkpoint | b - aABcCE
aab6b6cd-492b-5a4b-b70f-761ee55a438e | textbox | IR Test: Voltage (V)
1d6779ee-ba79-5f04-8dfe-db7ee3f24419 | textbox | IR Test: Duration (s)
c6fbe36b-2689-5be6-863c-485a1e74e51d | date | IR Test: Resistance (GΩ)
| checkpoint | c - aAbBCE
d54e4816-b7e2-5e63-855b-0637b93a75e4 | textbox | IR Test: Voltage (V)
057b23bd-f9d0-5d8e-bf2e-a9f3971baaee | textbox | IR Test: Duration (s)
deba1008-4f2f-5eaf-a234-7a98e6de5aa1 | date | IR Test: Resistance (GΩ)
| section | 6. INSPECTION POINTS: Circuit Breaker - Main contacts closed - Resistance μΩ
| checkpoint | Red
88c40d84-2f0f-5901-ab03-00af737b15b3 | textbox | Ductor (A)
c9623b59-3e63-59a6-82fe-d3521287f1b2 | textbox | Resistance μΩ:
| checkpoint | White
ead81a0b-3cf3-5fb3-a2e3-60a90d091012 | textbox | Ductor (A)
5aa9f445-1709-58ee-958a-b6325c0a993a | textbox | Resistance μΩ:
| checkpoint | Blue
093d8048-7f7e-5086-984b-fafc705b2f8e | textbox | Ductor (A)
cdaf2319-3555-52e8-8f50-8b5e853a6740 | textbox | Resistance μΩ:
| section | 6. INSPECTION POINTS: Auxiliary Readings
| checkpoint | Auxiliary Readings
fb567ee8-f78f-51cf-8605-8d4c33ec0371 | textbox | Trip Supply (Vdc)
68187f11-e6e6-517d-812e-3cdf3224dcf3 | textbox | Trip Coil 1 (Ω)
f99574e5-2c09-5b8d-a3d9-a023a6222bdf | textbox | Motor Overload (A)
613a51ff-07c3-56ed-8fba-7811ce56f0d5 | textbox | Close Supply (Vdc)
c8c5994c-2690-5aee-a386-f5ff84b0eb2c | textbox | Trip Coil 2 (Ω)
1c223897-052b-590f-9556-7b00af70d906 | textbox | Heater thermostat ºC
f01269fe-4d26-5741-a98b-3befd78c7040 | textbox | Charging Motor Supply (Vdc)
553bfec6-ef6b-5518-96ca-fb7b14731879 | textbox | Closing Coil (Ω)
fd35f230-5d22-521f-a897-e42f09adaccc | textbox | Counter reading
| section | 7. INSPECTION POINTS (Functional Tests & Completion)
| checkpoint | 1 - Auxiliary Supply Voltage and Polarity correct
| checkpoint | 2 - Protection operates both trip coils
| checkpoint | 3 - Wiring to control panels correct as per schematic
| checkpoint | 4 - CB operates correctly when done manually
| checkpoint | 5 - Indicators read correctly in open and close position
| checkpoint | 6 - Spring charge works automatically
| checkpoint | 7 - Apply trip while close is maintained (anti pump)
| checkpoint | 8 - Anti-condensation heaters operational, tong tested
| checkpoint | 9 - Gas pressure Lockout/Trip functional
| checkpoint | 10 - CB cannot be operated with ES on
| checkpoint | 11 - Close and opening timing tests complete, test report attached
| checkpoint | 12 - Area left clean and tidy
| checkpoint | 13 - Drawings updated and marked as 'As-Built'
| checkpoint | Operation Type:
014fd91b-0fec-5307-80e8-fc5eeff3cf2d | textbox | Local
269a9d5e-b350-56ec-ad3b-38e5e533cafe | textbox | Remote (Relay)
dac9529e-c124-5908-8a15-ee646c282336 | textbox | Remote (HMI)
d2319fb9-cd37-556d-8a78-907849c9da1e | textbox | Remote (Offsite)
| checkpoint | Open Operation
ac4146d4-c1f5-5b8f-9995-f379b22ec64f | textbox | Local
12b279b2-3063-54c7-89d6-37df2bac67e4 | textbox | Remote (Relay)
e36f2ba6-85fa-506b-831c-1c76babafbde | textbox | Remote (HMI)
db071316-595d-5fdf-a103-d13278c641c6 | textbox | Remote (Offsite)
| section | 8. INSPECTION AND TEST RESULT
| checkpoint-no-value | ACTION Details or Inspection Comments:
| checkpoint | Works to go and/or punch list items registered?
| section | 9. SUBCONTRACTOR SIGN OFF
| checkpoint | Subcontractor Sign Off
8040d6ed-8b60-5f4a-beb8-aac874e78a82 | textbox | Name:
979b0080-8a2f-5474-99b5-1fca358a2cb4 | textbox | Position:
f2bfbc01-c7cc-582f-a63e-66a9c231bd74 | textbox | Date:
| signoff | Signature:
| section | 10. ZENVIRON WITNESS OR HOLD POINT SIGN OFF (if considered applicable in Section 3)
| checkpoint | Subcontractor Sign Off
2f697fc1-10b0-57ad-889d-debec2b492a1 | textbox | Name:
9473f737-b569-5628-adeb-30e4d7e0c744 | textbox | Position:
6e3f1593-2c15-556e-acac-7e975121e8f1 | textbox | Date:
fb6fd249-01bb-5ba7-aebc-b1753dc44631 | note | Disclaimer: A signed Company witness shall not remove or relieve the subcontractor of the responsibility to supply or construct in full compliance with the Purchase Order/ Contract # requirements and terms. Zenviron reserved the right to reject goods or products not supplied or manufactured in accordance with Company requirements.
| signoff | Signature:
| checklist | ZX118-ITP-7020-1(0) - ITP - Civil - Access Track |  | ZX118-ITP-7020-1(0) - ITP - Civil - Access Track |  | 0cff6815-61d3-49fc-9558-9eea6958ca1f
| section | SECTION 1 - GENERAL
| checkpoint | General
464b0e2a-3836-5b40-8769-b63472d96841 | note | ITP Template No.: ZX118-ITP-7020-1
233ec6e2-2ce1-5e26-b3dd-6eb30a28a84d | note | Revision: 0
eb9c792b-23fd-558d-b3ad-baa84aa8a803 | note | Prepared By: L.Blazevic
35c20f51-835f-53b9-b36c-d68522bdc715 | note | Prepared Date: 11/01/2024
e9cbdae4-0655-572f-99c2-7dd5073f60e0 | note | Approved By: R.Burke
d16c174e-01ac-5199-81dc-f89273df5245 | note | Approved Date: 11/01/2024
5abe2d5d-7400-5754-a3ba-e37debc77f4a | note | Client: Fluence
ce428685-a967-51b4-a02c-36e35f50f6ba | note | Asset: LV BESS
61b56bbe-d83b-5798-9dca-6e75a8af735c | note | Project Name: Latrobe Valley BESS
04451b6a-513a-5956-8355-6fc976ab91eb | note | Area: Access Track
1b750089-1b97-59d5-bdae-281971442089 | note | Project Number: ZX118
2fa1f211-4146-5c1a-9c29-22db30cd63c2 | note | Discipline: Civil
4379483d-20dd-53e6-a899-340556f4676a | note | Component: Access Track
| section | SECTION 2 - CLOSE OUT SIGNATURE (ZENVIRON ONLY)
| checkpoint | Close Out Signature
b090303f-8e12-5503-a223-509d3db762ae | textbox | Name:
8eaaa73e-29c4-574e-a815-da5dc0daac92 | textbox | Position:
d55536b7-5668-5356-894e-cd174a56fb26 | date | Date:
| signoff | Signature:
| section | SECTION 4 - PRELIMINARY
| checkpoint | 4.1 - Design drawings, project specifications.
98feaae3-5ff0-5d16-8e1b-651eb9547cdc | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Design drawing revision status issued for construction, Project Specification and current controlled model issued.
663f4c2b-85c2-5bf1-91dd-a8f8c903eda1 | note | ACCEPTANCE CRITERIA: Documents controlled through document management system.
c4b4ee04-1a76-5b3e-ae6d-984f11cdd339 | note | VERIFYING DOCUMENT: N/A
d0b4dd4d-b947-5603-96bb-35e60f928ff7 | note | SUPERVISION TYPE: WITNESS
| checkpoint | 4.2 - Survey and Setout.
48d75b65-7594-5799-87a9-7ed3d9fc35e7 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): ZX118-REP-0173 Civil Specification Report Survey and inspection of Control Points.
565e946f-62d6-509f-b57a-d66899a13fef | note | ACCEPTANCE CRITERIA: Control point survey. Visual inspection of control point/s. Survey equipment spot checked for calibration.
941d5468-713e-5af8-a54a-800bcfb02bd6 | note | VERIFYING DOCUMENT: N/A
59861aad-72a5-5894-ab3a-ee7824b61ab7 | note | SUPERVISION TYPE: WITNESS
| section | SECTION 5 - MATERIAL APPROVALS
| checkpoint | 5.1 - Subgrade Material Conformance - Import Fill
42bc3f97-1744-532e-8fc6-480b333ba838 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of material to: ZX118-REP-0173 Civil Specification Report As per ZX118-DWG-3702 Typical Access Track Details As outlined in AS 1289
61b42dab-01c6-5d51-ab46-12c1eea482dd | note | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report Testing as per AS 1289.5.1, Designer Approval prior to placement Low Reactivity Granular CBR>15%
145af4f0-7b20-50ca-9435-b177f4ec116e | note | VERIFYING DOCUMENT: NATA Test Reports
7b5519e5-086a-5e55-a374-4d9e142b4791 | note | SUPERVISION TYPE: REVIEW
| checkpoint | 5.2 - Base Course Material Conformance
67ff1059-9caa-5de1-bdf6-2aa06a6da7eb | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of material to: ZX118-REP-0173 Civil Specification Report, Austroads Guide to Pavement Design - Part 4A, and ZX118-DWG-3702 Typical Access Track Details
95724a8b-1e0d-5f7f-a5e0-8645e9b88775 | note | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report; Testing as per AS 1289.5.1
1d7f1351-b29d-5e4b-9e76-d3587e2921a8 | note | – Particle Size Distribution - in line with Class 3 according to Austroads Guide to Pavement Design - Part 4A
7d71d6e2-9f5d-56c7-9edf-7d3540889e93 | note | – CBR >45%
5ea8a18a-3568-57f1-9fdf-9b64c0046c85 | note | – Atterberg Limits targeting PI 9% +/-2% OMC
35699285-1a00-50f0-b532-b140dac5e784 | note | – Wet/Dry Strength Variation ≥50kN
0ca59477-d77e-5ee0-bcb0-1937b8704519 | note | VERIFYING DOCUMENT: NATA Test Reports
24bd4955-9381-56cf-b929-7464aa15b189 | note | SUPERVISION TYPE: REVIEW
| checkpoint | 5.3 - Drainage Backfill
fded329c-8dcd-50fa-ab52-74cf71d926be | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of pipe bedding and backfill material to: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3703 Typical Stormwater Details
4e67e9c6-e6f8-5a4d-91d3-e8310022d7af | note | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report Design Drawings
936d2b48-e5d2-5a34-b9c8-b70b2b4cde5c | note | – Bedding - Evenly graded Class 2 FCR with 20mm nominal size or other designer approved material
cbe4d72e-d6aa-5c29-a6f9-02c38976b6cf | note | – Backfill - Class 3 FCR with 30mm nominal sizing or other design approved material
151ae83c-e14a-513a-8533-80c0e42789e2 | note | VERIFYING DOCUMENT: NATA Test Reports
3849116a-b6f0-5782-bce9-fce9e956fc7f | note | SUPERVISION TYPE: REVIEW
| checkpoint | 5.4 - Drainage Elements
2b45df78-eb79-559b-b0b4-e5ab9193e6c1 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of pipes and headwall to: ZX118-REP-0173 Civil Specification Report
6b835b71-59a1-5942-8bd2-53e61c2282d8 | note | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report RCP compliance to AS/NZS 4058 and/or polypropylene to AS/NZS 5065
248ed202-a151-53e5-a7e7-112653e0fb5f | note | VERIFYING DOCUMENT: Material Data Sheets
2d25981f-190d-5643-b2b9-f782e20e1e6e | note | SUPERVISION TYPE: REVIEW
| section | SECTION 6 - CONSTRUCTION PROCESS - ACCESS TRACK STRIP SOIL
| checkpoint | 6.1 - Clear and Grub
c352d83f-d77d-52ff-b3a4-d62293060022 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify area has been cleared and grubbed.
addbd523-1709-5fd2-adf3-05b94d627fdd | note | ACCEPTANCE CRITERIA: Area cleared of all refuse, artificial and deleterious materials. Consult with landowner prior to removing any fencing or gates. Ensure CEMP is adhered to.
aa1103c3-4f4f-5c60-9f06-2d2a6be32a6d | note | VERIFYING DOCUMENT: N/A
0a4ed9ba-7f37-5965-b9c1-74ad2c7ea401 | note | SUPERVISION TYPE: WITNESS
| checkpoint | 6.2 - Topsoil Stripping
ce5a7503-9ace-5eba-843e-ed8e523b37c3 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Confirm top soil removed and stockpiled adeqautely
d40d9b56-9cea-5df3-a21f-3dd357dc6946 | note | ACCEPTANCE CRITERIA: Strip topsoil to a depth required to remove all topsoil from the footprint area. Ensure the area is self draining Ensure CEMP is adhered to. Temporary ERSED controls in place as required.
9bf7271d-e4fe-5fb4-a479-ae9e118568ff | note | VERIFYING DOCUMENT: N/A
947af98f-5733-5cf3-9234-1143ef1b3cb9 | note | SUPERVISION TYPE: WITNESS
| section | SECTION 7 - CONSTRUCTION PROCESS - SUBGRADE AND CONDITIONING
| checkpoint | 7.1 - Earthworks Foundation
7d0b02e2-1ee7-50a5-800b-33a7f2e2f64d | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Earthworks on subgrade treatment to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, and ZX118-DWG-3701 General Notes
288865ef-a20d-5c96-be8a-e53085807e7f | note | ACCEPTANCE CRITERIA: Test results on founding layer compliant to ZX118-REP-0173 Civil Specification Report
62b370e8-57b7-5c35-afa4-5708030adb60 | note | – Proof Roll using fully loaded 10000L water truck or other approved vehicle
b7b62629-6f75-53ac-9212-cc2764a0fb70 | note | – DCP - 1 test per 50lm
e6bef1e1-5cec-5b39-b821-d3ceb6ecaca7 | note | VERIFYING DOCUMENT: ZX118-ITR-7209 - Proof Roll Inspection DCP Field Results / NATA Test Report ZX118-ITR-7210 (Where applicable) - including Location plan of soft, wet or unsuitable material including replacement methodology.
1147c847-31d9-5a40-87c0-0e2b159d8a8b | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 7.2 - Structural Fill/ Rock Fill Embankment (Where Required)
351c50a2-4a9d-597e-ba8b-4138df48f9ed | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Earthworks on structural fill/ rock fill embankments to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, ZX118-DWG-3701 General Notes and AS 1289
89650bc8-8abe-5331-95f1-99ee88f85bae | note | ACCEPTANCE CRITERIA: Test results and/ or proof roll records obtained for the fill layers compliant to ZX118-REP-0173 Civil Specification Report
dcba0a68-5d33-531a-b3f4-b3686ea14376 | note | – Compaction to 98% SMDD at ±2% OMC
221c9e73-2d12-5c95-af5b-67a25ecd11fb | note | – Frequency of 1 test every 300m and every second layer within 1000mm of finished subgrade level
0322c110-26d0-5117-aba1-8bab07d24d2c | note | VERIFYING DOCUMENT: NATA Test Report (Where Required) ZX118-ITR-7209 - Proof Roll Inspection
5e1e6867-27b6-5358-8797-2a3d8a2ec4d6 | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 7.3 - Rock Subgrade (Where Required)
5fb21177-c582-599a-ae4d-70892fdd6d11 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Rock Subgrade compromising of reasonable strength rock to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report
20c23234-0605-5532-bd19-862046fab920 | note | ACCEPTANCE CRITERIA: Proof roll records obtained
364dcd52-927a-5f8d-9369-c5eda66d8ca3 | note | – Fully loaded 10000L water truck or other approved vehicle2
d5b3004d-aebb-531e-823a-1c0d6816ed7b | note | VERIFYING DOCUMENT: ZX118-ITR-7209 - Proof Roll Inspection If applicable Include; Location plan of soft, wet or unsuitable materialand the applied replacement methodology.
3bb4d1b5-c166-5bd0-8223-7db4fec1f0b6 | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 7.4 - Finished Subgrade
4dc97711-dbac-53f5-9c59-cd3f9577f3e5 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Test results obtained for the finished subgrade layer compliant to: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track, Details, ZX118-DWG-3701 General Notes, and AS 1289
a1ea2a4d-176f-560d-92e1-c45763eadb04 | note | ACCEPTANCE CRITERIA: Test results and proof roll records obtained for the finished layer compliant to ZX118- REP-0173 Civil Specification Report
beca4494-d666-56a7-856e-1ea8d4aa48b5 | note | – Compaction to 98% SMDD at ±2% OMC
0ea1ca78-f355-50e0-80e0-6f9ea90b59dc | note | – Frequency of 1 test every 300lm
2f024a72-f4e8-54af-a7f5-ce3373d22593 | note | – Proof Roll using fully loaded 10000L water truck or other approved vehicle
689a0355-a9ce-55fa-90f2-b7f7138436c1 | note | VERIFYING DOCUMENT: NATA Test Report ZX118-ITR-7209 - Proof Roll Inspection
34741b71-3cb7-5152-825e-fc2f320b293c | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| section | SECTION 8 - CONSTRUCTION PROCESS - ACCESS TRACK BASE COURSE PLACEMENT
| checkpoint | 8.1 - Base Course Pavement Placement
e58c0df5-4cc5-5a67-b543-3933b73229fd | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Material placement compliance test results in accordance with: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, and AS1289
3b7419af-31ce-5630-86d4-2d38a2771a66 | note | ACCEPTANCE CRITERIA: Material placement compliance test results in accordance with: ZX118-REP-0173 Civil Specification Report
e9e8d98f-cd1a-5eb2-83fd-e37f0c91f085 | note | – Compaction to 98% SMDD at ±2% OMC
0c3eb628-93fb-576b-976a-886d675086a8 | note | – Frequency of 1 test every 300lm
fbe0bb17-730d-5cb5-a79c-ad8148aa2afb | note | – Proof roll using fully loaded 10000L water truck or other approved vehicle
a0d4c847-4d35-5718-855a-82a9be40ece5 | note | VERIFYING DOCUMENT: NATA Test Report ZX118-ITR-7209 - Proof Roll Inspection
2d30ca8b-9208-5b54-a0b1-17cac6280c54 | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| section | SECTION 9 - CONSTRUCTION PROCESS - LONGITUDINAL DRAINAGE
| checkpoint | 9.1 - Excavation
87b9c94a-c634-58f0-8057-49421d6cd3e2 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Ponding monitored and made free draining
8b44277d-39cf-5273-91d5-ef6d87dbe7d0 | note | ACCEPTANCE CRITERIA: Visual Inspection
0d61c5c3-f806-5748-9077-c5a98b0bbe79 | note | VERIFYING DOCUMENT: N/A
a75ebbcc-8dfe-5194-ad86-cb8910e70fa5 | note | SUPERVISION TYPE: WITNESS
| checkpoint | 9.2 - Erosion Controls
5c1709de-9f39-5929-b283-7b49b89e2be7 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Erosion controls in line with: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3717 Erosion & Sediment controls
6edc0698-3e97-511f-83b9-5b80fa49d46f | note | ACCEPTANCE CRITERIA: Visual Inspection
28cf5bc3-3a12-5a01-9b4d-62155a828319 | note | VERIFYING DOCUMENT: N/A
186e1440-09bd-5e45-a0ba-0b3873ff4d80 | note | SUPERVISION TYPE: WITNESS
| section | SECTION 10 - CONSTRUCTION PROCESS - CULVERTS
| checkpoint | 10.1 - Culvert Foundation
b7201642-cff5-5c39-8700-592df4b83c24 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Floor of excavation is sound and no presence of soft or under yeilding material
570365e6-c71d-587e-a7d7-8fd98b1418f0 | note | ACCEPTANCE CRITERIA: Visual Inspection
72f18cd4-7575-54e2-a325-b1d1ae25d23c | note | VERIFYING DOCUMENT: If applicable Include; Location plan of soft, wet or unsuitable materialand the applied replacement methodology.
4aa100a3-2074-591e-ae50-0a0ff5945c99 | note | SUPERVISION TYPE: WITNESS
| checkpoint | 10.2 - Bedding
03c6c247-a273-5148-b7db-e045bf0be3d2 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Placed via hand ramming to a minimum 100mm compacted thickness
d2be43a3-9c08-5f79-81d1-6db741bbdf05 | note | ACCEPTANCE CRITERIA: Visual Inspection
defb0f2b-c6e1-5ccd-aaae-49cfccc307ea | note | VERIFYING DOCUMENT: N/A
d0279769-74b7-51b1-8388-611f77a14b96 | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 10.3 - Pipe Placement
488e4311-d194-5a13-b739-f2ce3b23e764 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Location to be confirmed on-site. Grade and RL as per Design requirements.
93042bd2-1639-5f74-8621-20b85cac5ac7 | note | ACCEPTANCE CRITERIA: Visual Inspection. Confirm pipe flows in the correct direction, barrel of the pipe is laying evenly on the full length of the bedding material and all sockets face upstream.
511136f0-2374-5c5b-94b3-dd136f6224a7 | note | VERIFYING DOCUMENT: N/A
6085c0d6-42e2-5f3d-94b5-a6c7a20f05b7 | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 10.4 - Haunching and Backfill
17b3d2fe-e02d-5bda-929c-e84538ad72b7 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Earthworks on backfill to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3703 Typical Stormwater Details
07dbc8b0-2f5e-5f1a-b21f-ba941f5b69cf | note | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report ZX118-DWG-3703 Typical Stormwater Details
c9954fed-712f-52f9-a97e-c8ba5d06a557 | note | – Compaction & Density 98% SMDD at ±3% OMC
038f89a6-51ca-53ef-af7d-4e3e88296240 | note | – 1 test per drainage line
e6853a22-5ab0-5a93-bc9c-e678540c4992 | note | VERIFYING DOCUMENT: NATA Test Report
1dd7935d-5a0a-5ad2-90db-17896aa26bbe | note | SUPERVISION TYPE: HOLD POINT
| signoff | AUTHORITY HOLDPOINT
| checkpoint | 10.5 - Erosion Controls - Rock Armouring
db44b524-357b-5feb-8ce7-44e8895c9b0b | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Permanent ERSED Controls in place in line with ZX118-DWG-3717 Erosion & Sediment controls
60ecb521-24ad-5e0a-a765-b0f1524c26a1 | note | ACCEPTANCE CRITERIA: Visual Inspection of scour protection for compliance to: ZX118-REP-0173 Civil Specification Report
3329a0c1-a8d7-5324-97fa-43ea08be433c | note | VERIFYING DOCUMENT: ZX118-ITR-7217 Culvert Installation Checklist
f7f125d2-d794-5a99-9316-aa0ec2d57fff | note | SUPERVISION TYPE: WITNESS
| section | SECTION 11 - COMPLETION AND HANDOVER
| checkpoint | 11.1 - Redline markup of Construction Drawings
cd9c0565-4848-5579-b52e-5fa597604f26 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Redline markup of relevent Construction Drawings in Master Drawing Folder
1a2be2b1-3821-5911-9498-7434b4d855b8 | note | ACCEPTANCE CRITERIA: In line with: ZX118-REP-0173 Civil Specification Report
944ee1de-faea-5010-a77b-d27390439b07 | note | VERIFYING DOCUMENT: Redline Markup in Master Drawing Folder
c3174709-4955-52d8-9579-caa080f7409b | note | SUPERVISION TYPE: N/A
| checkpoint | 11.2 - Generate Punch List
e373b2f5-bbb1-54fd-85dd-45ff1f9b30c3 | note | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Subcontractor walk-down inspection
f7fddc77-7a2c-5a87-ab6b-216e9adf412f | note | ACCEPTANCE CRITERIA: Generate specific area/scope Punch List and transfer the open items to the Punch List Master Register
377a7c5d-6aef-5232-9516-16d0a73319c7 | note | VERIFYING DOCUMENT: BMS-FRM-1033 Punch List Sheet record
9405c3c0-956d-58ba-a783-46625672bb3e | note | SUPERVISION TYPE: N/A
| checklist | ZX118-ITR-7217(0) - Culvert Installation Inspection |  | ZX118-ITR-7217(0) - Culvert Installation Inspection |  | ecb1ba92-62c6-4b53-a86b-9c32f0d260ed
| section | 1. GENERAL
| checkpoint | General
e32e064e-1bac-58be-9902-b21a4f06de6c | textbox | Project Name:
c1172f4f-714f-5879-9280-8a1e5a5fc997 | textbox | Project No.:
d6d3937b-da2e-513c-b88e-d1900a6e6d54 | note | ITR Description: Culvert Installation Inspection
48b2a96e-1ed1-54a0-87f9-52ff4e007793 | note | ITR Template No.: ZX118-ITR-7217
c86a6ecd-a310-5d5c-bdf3-d4d4bdc10df6 | note | Rev.: 0
c3446fad-9c16-5dab-ab11-4d6dd3e67efa | note | ITR Level: 1
| section | 2. SUBCONTRACTOR
| checkpoint | Subcontractor
54dd8bfb-f28a-5cf7-829b-472893884d14 | textbox | Company:
5c23c3b4-ab38-58e0-8409-50389ad4f0d5 | textbox | Supervisor:
40e2ff47-9843-5351-93f6-25d946f529c5 | textbox | Scope of Work:
c2742fc7-5351-5fb9-86cb-5ecfe077a0fc | textbox | Contract No.:
| section | 3. INSPECTION AND TEST DETAILS
| checkpoint | Inspection and Test Details
c4efa985-d7f6-534a-a784-095ce40cf521 | radio | Is HOLD POINT applicable? | Yes,No
13c7a12c-b57c-52d0-a259-3cba615e7ee9 | radio | Is WITNESS applicable? | Yes,No
661f5505-8647-53ff-8dfd-8f727b9444f5 | textbox | ITP Reference: |  |  | Choose an item
06cebb70-98bd-5222-b58b-ae90355cc5cc | textbox | Location:
f124e846-18c1-57bb-a7c3-d77de7a867fc | textbox | Drawings Ref.:
291173cb-77e1-55a7-b87e-8774b7c125cd | textbox | Specification Ref.: |  |  | Choose an item
| section | 4. INSPECTION DETAILS
| checkpoint | Inspection Details
e5f6acfb-85d6-5b8d-8daf-becdc456f32b | textbox | Type of Pipe:
3792ddcd-a8b4-5e70-9ba5-a79756989f9c | textbox | Class:
cf3f0503-c5cc-5ab4-86f8-6d1d352a4d64 | textbox | Number of Cells:
4e79e1f4-a136-5fc4-9039-a5e53ecbe026 | radio | Concrete Encasement: | Yes,No
| section | 5. INSPECTION POINTS
| checkpoint | A. Alignment
| checkpoint | B. Foundation Inspection
| checkpoint | C. Laying Inspection
| checkpoint | D. Backfill Inspection
| checkpoint | E. Erosion Controls
| section | 6. INSPECTION AND TEST RESULT
| checkpoint-no-value | ACTION Details or Inspection Comments:
| checkpoint | Works to go and/or punch list items registered?
| section | 7. SUBCONTRACTOR SIGN OFF
| checkpoint | Subcontractor Sign Off
ad4289cc-b34f-5fab-9a0d-0f4066559bab | textbox | Name:
0d7539c1-3064-5f15-9113-cbc5cd229397 | textbox | Position:
ef77ba77-eaee-50a1-ba87-3143cf9f855e | textbox | Date:
| signoff | Signature:
| section | 8. ZENVIRON WITNESS OR HOLD POINT SIGN OFF (if considered applicable in Section 3)
| checkpoint | Subcontractor Sign Off
89da4c35-a5c6-542e-a81d-efcf0130b39e | textbox | Name:
baf7295a-aa33-50e9-90f5-e6539d59f533 | textbox | Position:
a098621c-0cae-5e00-9095-83435d90d11f | textbox | Date:
6fc9c4c9-0965-5fc8-8d9b-0801e3766d29 | note | Disclaimer: A signed Company witness shall not remove or relieve the subcontractor of the responsibility to supply or construct in full compliance with the Purchase Order/ Contract # requirements and terms. Zenviron reserved the right to reject goods or products not supplied or manufactured in accordance with Company requirements.
| signoff | Signature: