## Resources
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Headstocks Checklist |  | Headstocks Checklist | 0b60add9-b282-4024-adfa-614d13624a5a
| section | Pre-Pour Checklist
| checkpoint-no-value | Pre-Pour
0cd57cab-8fa7-548d-b9de-16387f93a80b | textbox | Cast Number
14a813d4-dfe1-52dc-b77c-241de30d055c | textbox | Headstock Number
| checkpoint | Shop Drawings approved for Works
| checkpoint | Mould Dimensions are within Shop Drawings Tolerance
854f45db-a23a-5c05-9591-8d70751f3852 | note | Length
239d6d63-f5bb-5890-a895-dfd3b4e9d67f | note | Width
d91e5513-0d54-52cb-a8b9-f9f6b6a4b5c4 | note | Height
0491ae4b-4c2c-5ec2-928d-ffd3595034bf | note | Straightness
ad9ea5d9-3760-5428-928f-2ecb4547f937 | note | Cross-section
| checkpoint | Mould Surface Checked (HOLD POINT FOR PERMACAST TO SIGN OFF)
debf7e04-3212-5dca-9c59-2e99172a8e36 | note | Cleaned
e8cce6d3-6af3-5d13-9d63-cde41ac17903 | note | Sealed
daae5147-0969-5b07-83dc-5f1bf0f97075 | note | Rubbers in Place
ba321736-4c30-566e-80c7-33dd2326b77d | note | Oiled
efc54a3f-168e-5b17-866c-3cddb2a15ef0 | note | Chamfers in Place
4cd46cb1-4bbe-526b-a9ad-5452216f36f2 | note | Check angle for shutter
| checkpoint | Reinforcement in Accordance with Drawings
c1c57d89-9342-53d7-9ed9-69f8f1289ec4 | note | Reinforcement size
a1782bb2-dd9d-5419-85d3-ecb72ce94a28 | note | Lap Length
1b923b0c-7339-51f6-a190-fc9ba945741b | note | Splicing
e0d3a23a-bfce-5c01-9706-2100f6bf2065 | note | Bar Chairs
| checkpoint | Cover maintained and within tolerance
| checkpoint | All Stainless Items are installed in accordance with Drawings
7b4a7d07-afd3-58fe-8a63-ee2b0c771f8c | textbox | Specify
| checkpoint | All PT ducts are installed in accordance with Drawings
01d487da-45f9-5d87-b45c-be0c683afa24 | textbox | Stressbar layout type
68dd529a-d5ba-5ded-936b-4b1649a656d4 | textbox | No of stress bar ducts
5499df35-ec48-52aa-88ff-04eefa35e382 | textbox | Duct locators
| checkpoint | All Lifting Inserts are installed in accordance with Drawings approved by the client (HOLD POINT FOR PERMACAST TO SIGN OFF)
7d7679eb-3622-5248-8184-39f4417578ce | note | Lifting drawing name
44f05c5c-cd3c-5fab-b1d3-be91bb93dadd | textbox | 20T Lifters for (4x CA20200)
| checkpoint | Cast-in Items and Ferrules
4d0e3ffe-2822-51e9-a995-53e2edb0cfc8 | textbox | M20 Ferrules - Stability Bracket Ferrules on top face
c199eabd-4a9d-517c-9f05-4975f56a149a | textbox | M16 Ferrules - Temporary formwork Ferrules on outside face
95da8278-9a59-5fb7-990d-9f849fed4e1f | textbox | CA20255 Cone Lifters
fee1cb0e-8346-5666-8895-95f50c55e0c2 | textbox | Ferrules (Other type, specify)
f3899ea9-8d91-5690-815b-24b9180a2ecf | textbox | All Couplers are installed in accordance with drawings
b616293a-8167-5ce2-8e80-8293ee03ee69 | textbox | All ferrules are installed in accordande with drawings
7634352c-8001-500e-894a-09e1d40c9574 | note | Number of couplers
| checkpoint | Earthing and Bonding is installed in accordance with Drawings (HOLD POINT FOR PERMACAST TO SIGN OFF)
94077a9c-6975-5c8b-9060-806b99a7d90b | textbox | Earthing Terminals (FDB-16)
32967a6c-d977-5edd-af37-a2afc1d5ce3b | textbox | Flexi cables
55fa2857-7eb0-5241-ae61-329d82c19adb | textbox | Weld locations (not permitted within 75mm of a bend)
29e87801-a854-55fa-80a0-a8d9349ab4d3 | textbox | 100mm single side or 55mm both sides - 6mm fillet welds between bars
b1b9b07d-bba3-5c45-9c73-8b855c607aa7 | textbox | <20 mOhm across cage Length
6a41e56b-1b8c-5be5-819e-1a135de83c34 | textbox | Checklist Completed (Headstock) (attach results)
| checkpoint | Cooling pipes are installed in accordance with Drawings
ca422c48-c38c-5d60-9ca9-b7a2b03d0b48 | note | Approval correspondence
f70af16b-db41-5d24-a428-b8b0dc8502e2 | note | Water circulating temperature monitor
2c1cb4b9-afce-540b-a08c-134720b804ed | textbox | Cooling pipes numbers
85f5f080-84a8-5d8e-862a-f87479cbed6a | textbox | Cooling pipes spacing
518513fd-3f6d-5c58-8f60-53ab050b812b | textbox | Hydraulic system in working status (no leaks in mould)
| checkpoint | All Temperature Loggers are installed as per Approved WMS (HOLD POINT FOR PERMACAST TO SIGN OFF)
4509bd10-7c88-5ae0-ae1a-a8972e032689 | textbox | Ensure All temperature Loggers are Working
1e3e5f3c-2be7-59c1-81f0-8386b9bef4c1 | textbox | Number, location and installation of loggers
0d34b945-6a22-5a50-9cb9-5cf72c506820 | textbox | Temperature logger in cover zone
19ec6e4f-be42-58d6-b7a7-b2a5fa2d1c91 | textbox | Temperature logger in core zone
95606f94-d717-5890-9a50-6545e496799e | textbox | Temperature logger in tent for ambient temperature
| checkpoint | QA Engineer Check Completed by
| checkpoint | Client Inspector (if present)
| checkpoint | Notify concrete supplier of pour
| checkpoint | Notify contractor to arrange NATA testing laboratory of pour
| section | Supervisor Release
| checkpoint | Supervisor Release to Engineering Team
| section | Casting Checklist
| checkpoint | Casting Information
70757fe9-804d-5d90-8236-7781b1c881ef | textbox | Cast Date
| checkpoint | Concrete Delivery Dockets
2aab48e9-bda0-5f87-a7fa-5b8e1560daed | textbox | Concrete Delivery Docket (list all)
| checkpoint | Total Concrete Volume
606ac0e8-0d9b-5d8c-b6ad-a0a51b6be123 | textbox | Volume (m3)
| checkpoint | Mix Design Verified
d5845f0b-845e-50da-9a5b-5c853f41d646 | textbox | Specify mix used
| checkpoint | Ambient Temperature within Limits
ff654f35-681b-5457-ac45-d69822243b99 | note | max 38°C
| checkpoint | Concrete Temperature
9903784e-bd1a-5511-8aab-3ba211c38928 | note | max 32°C
| checkpoint | Slump within Allowable Tolerance (180mm +/- 40) First truck and subsequently tested for every 20m3
9ef9ed06-5db9-5634-adce-36bcb51fd0c4 | textbox | Slump (list all)
| checkpoint | Truck Tested for strength
a57a5f32-38ee-5f40-b47b-cbd47b18fd7e | textbox | Test Report Reference Number (list all)
79ec6daf-5f82-55f1-9143-82844f2f1d26 | textbox | Number of cylinder taken
| checkpoint | Vibration adedquate
| checkpoint | Time Lag Between Trucks is not exceeded (20 minutes)
| checkpoint | Concrete Placed within allowable time from Batching Plant
| checkpoint | No Free Fall During Pour (not more than 2 metres from ground)
| checkpoint | Required Finish Applied as per Drawings
| checkpoint | Concrete Covered Overnight
| checkpoint | Cylinders Stored next to Bed
| section | Stripping Checklist
| checkpoint | Date Stripped
4c5ec57d-2f54-5869-b55c-6169d12c08e6 | textbox | Enter Date
| checkpoint | Concrete Cylinders Crushed and Checked for stripping strength (HOLD POINT FOR PERMACAST TO SIGN OFF)
2d7a69f5-50f8-5670-8679-a611438caea2 | note | Minimun cylinders (1x7d, 2x28d)
3db4fc2a-4d1f-5b2f-8e1c-b4094e53b5a3 | textbox | Stripping - 45.5MPa minimum | 8
89a3b800-3fb4-5c92-bcd9-8a63258e244c | note | Strength = Reading / 7.851
| checkpoint | Lifting Strength Achieved
| checkpoint | Lifted and Handled as per Drawings
| checkpoint | Product Clearly Labelled
| checkpoint | Storage as per Approved Temporary Works Drawings
| checkpoint | Secondary Curing as per Approved Methodology
3c54eaca-fa9b-56cc-86e3-17a9e99cd17e | note | Temperature 5 degrees less its peak
194bbe69-0030-596a-b71c-e187554d1e32 | note | Max temperature doesnot exceed 70°C
b00332e7-621a-5aa1-b395-e2188499424b | note | Differential between Core and Cover within 28 degrees
| checkpoint | Product Dimensions Achieved and are within Specified Tolerance
41fa594f-c2c9-5a34-ac70-a637694241f0 | note | Length
f6fb7add-cac2-58b2-a66c-b9de4a33a52c | note | Width
3494c289-85ce-59b8-bfa4-c594d2120cbb | note | Height
30335dc6-145f-526f-9916-058678ca456d | note | Straightness
e858fd04-568c-59f3-8160-0ac0dceb9dc0 | note | Cross-section
| checkpoint | Specified Finish Achieved
e45454c5-9883-5278-80c0-1359312f3733 | note | Rugasol applied where roughened surfaces are required
| checkpoint | Cast-in Items are all in Place and within Specified Tolerance
ae0633ef-1fe6-5293-8011-7406ad21b459 | note | Couplers
6cfd0cab-81d4-5b79-9c9b-971539f2d99e | note | Stainless Items
67567677-8c1f-5834-84d2-2ecd0532b760 | textbox | Lifters
fd04513e-dc25-5e50-9930-1de9f0676741 | textbox | Blockouts
| checkpoint | Earthing and Bonding confirmation of continuity value (HOLD POINT FOR PERMACAST TO SIGN OFF)
6c2bfc37-e12f-52f9-9618-6c087dacc1c2 | textbox | continuity value
| checkpoint | Post-Pour Works Completed (As Required)
565cd430-66c8-53f1-b913-f8d2427f8278 | textbox | Couplers are Cleaned,threaded section is fixed and capped
50c9095d-f9ab-502c-8508-772b71668f51 | textbox | Roughened Surfaces are Greencut
4ccba29e-8a0b-5305-aa56-8ebca0a5f814 | textbox | Water Removed out of Cooling Pipes
7c3bf905-f176-582b-bf3f-6a5b1310ae29 | textbox | All Miscellaneous Items are Completed
| checkpoint | Temperature Logging Completed and Conforming. Attach Results
| section | Any Defect Identified
| checkpoint | Punchlisting Completed
| checkpoint | Repairs Required (if applicable)
| checkpoint | Repairs Completed as per approved WMS (if applicable)
| checkpoint | Crack Map Completed
| checkpoint | Any NCR Required (if applicable) (HOLD POINT FOR PERMACAST/CLIENT TO SIGN OFF)
| checkpoint | NCR Approved by Client and Repairs Completed (if applicable) (HOLD POINT FOR PERMACAST/CLIENT/PTA TO SIGN OFF)
| section | As-Built Drawings
| checkpoint | As-Built Drawings Completed, Stamped and Attached
| section | Concrete Strength Test Report (HOLD POINT FOR PERMACAST TO SIGN OFF)
| checkpoint | Concrete Strength Test Report Received
1d48b7d1-ae6a-558e-80c2-d77a92b70b2d | textbox | Concrete Test Report (every 20m3) | 9
948a101b-0a5a-5adf-9ea1-7f8119b9423e | textbox | 1x 7 Day Strength (List all) | 10
f2ee51cf-775f-589e-9dac-ab97a80efd3e | textbox | 3x 28 Day Strength (List all) | 11
| section | Transportation Requirements
| checkpoint | Certificate of Conformance
| checkpoint | Inspection Release Certificate
| checkpoint | Punchlist signed copy
| checkpoint | Delivery Notes
| checkpoint | Delivery Docket
| section | Final Acceptance (HOLD POINT FOR PERMACAST/CLIENT TO SIGN OFF)
| checkpoint | Completed by
| checkpoint | Reviewed by
| checkpoint | Final Inspection Client Representative (HOLD POINT FOR PERMACAST/CLIENT TO SIGN OFF)
| checklist | Preliminary Activities and Materials Approval Checklist |  | Preliminary Activities and Materials Approval Checklist | 624ac3ef-3970-45f8-9448-86f0cea66872
| section | Preliminary Activities (Approved by Client)
| checkpoint | Compliance to AS/NZ ISO 9001:2015
| checkpoint | Permacast Project Quality Management Plan
| checkpoint | Inspection & Test Plan
| checkpoint | MDR Index
| checkpoint | Work Method Statement (WMS) - Prestress
| checkpoint | Work Method Statement (WMS) - Curing
| checkpoint | Concrete Repair Methodology
| checkpoint | Shop Drawings
| checkpoint | Test Panel Prepared and Inspected by Client
| checkpoint | All Technical Query Forms (TQs) Reviewed and Approved for Works
| section | Concrete
| checkpoint | S65 Concrete Mix Design Approved by Client
| section | Steel Reinforcement
| checkpoint | Inspection of Delivery to Confirm Compliance with Order and Drawings
| checkpoint | Cut Bar Length Tolerance +0mm -10mm, Bends in Plane, Correct Cog Lengths etc.
| section | Prestressing Tendons
| checkpoint | Inspection of Delivery to Confirm Compliance with Order and Drawings
| checkpoint | Ensure that all Coil Numbers are recorded
| checkpoint | Stressing Calculations Submitted and Approved by Client for Works
| checkpoint | Stressing Jack Calibration Certificates
| section | Lifting Anchors
| checkpoint | Lifting Design Approved by Client
| checkpoint | Lifting Devices Approved by Client
| checkpoint | Inspection of Delivery for Completeness and Quality
| section | Cast-in Items and Ferrules
| checkpoint | All Cast in Materials Approved
| checkpoint | Inspection of Delivery for Completeness and Quality