## Taxiway Lighting
|  |  |  | Process Control Plan |  | FHIMS-QA-6028 | Approved |  | Signature
|  |  |  | Contract Name: | NAL Apron Upgrade |  | FH Engineer |  | Thomas Powell
|  |  |  | Procedure: | Taxiway Lighting |  | FH Quality Manager
Inspection & Test Plan / Checklist
Lot No: |  |  |  | Corresponding Work Instruction: |  | (insert contract suffix here)-CS-7028 |  | Compliance with Work Instructions and Specifications
Detailed Location:
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | FH Initials | Design Engineer Initials (Grey if not required) | Date(s)
1 | Design | H | Ensure that Design is approved and Drawings are of the latest revision | Prior to commencement | Document Review |  | Check Drawing Register | Site Engineer
2 | Isolation Procedures | W | Ensure All AGL circuits entering the site are isolated and where possible pulled out of ducts that enter the work site. Provide insulation resistance test results for all existing AGL circuits that are to be retained at the completion of the works (including those unmodified by the project). | Prior to commencement and then monthly testing | Visual Inspection and testing | All CCRs are lockedout to prevent accidental reinstatement. | Insulation resistance test results, photos of isolated CCRs, Contract witness Point
3 | Existing light Survey | H | Prior to any pavement works, all lights, SITs and light bases affected by the reconstruction works shall be surveyed. Survey should include: – Location; – Orientation (deviation angle); – Colour pattern; – Circuit; – Labelling; and – Secondary cable route between the light and its associated SIT pit. | Prior to commencement | Survey | The survey shall be undertaken using the coordinate system employed in the design drawings. Any discrepancy in the survey with the design set out information shall be brought to the attention of the Contract Administrator for resolution in accordance with clause 6.11 of the Conditions of Contract. | Survey receipt
4 | Existing Light Removal | W | Prior to any pavement works, all lights and SITs and light bases affected by the reconstruction works shall be removed and replaced with provided temporary red lights, adjacent to the red barriers as outlined on the drawings. | Prior to commencement | Visual Inspection |  | Photographs
5 | Survey Setout | H | Confirm the location of all existing underground cables and services on site and mark them out with stakes. | Prior to commencement | Survey |  | Survey record | Site Engineer
6 | Material Compliance | H | Pipes to be encased in concrete as part of Duct Bank works shall be Class 12 PVC pipes. | Prior to supplying to site | Visual inspection/ Document review | Drawings,Pipes to AS/NZS 61386.1 or heavy-duty rigid conduit to AS/NZS 61386.1. | Delivery dockets | Site Engineer
|  |  | All new cable ducts shall be Electrical Heavy Duty type to AS 2053 coloured orange | Prior to supplying to site | Visual inspection/ Document review | AS/NZS 3000 | Delivery dockets
|  |  | Concrete | Prior to supplying to site | Visual inspection/ Document review | Concrete for duct banks should comply with section 15.3.2 of the contract specification. | Manufacturers certificate, delivery dockets
|  |  | Inspect any Cable sand Delivered to site to ensure it meets criteria. The sand shall be clean and free of organic matter or sharp stones. | On arrival at site | Visual inspection/ Document review | The bedding material shall be finely divided sand which contains at least 90% by mass passing a 2.37 mm sieve and not more than 15% by mass passing a 0.075 mm sieve. | Delivery dockets, Lab testing
7 | Trenching in Under Ground Cables | H | Where the new ducts are in the proximity of existing cables/duct, they should be seperated horizontaly by at least 1m. Excavations should be deep enough to provide a minimum cover of 750mm. | Across Each Trench | Visual inspection, measurement | Depth and distance measurements | Photographs | Site Engineer
8 | Bedding of services | H | If the excavated soil is not compatible material free of rocks, or will not pass through a 25 mm sieve then: – The bottom of the trench shall comprise a bed of 50 mm of sand placed before the first enclosure or cable is laid, and, – A layer of sand shall be placed to cover the conduit with 75 mm of sand before backfilling. | Across Each Trench | Visual inspection, measurement |  | Lab testing, Photographs
9 | Duct Inspection | H | Inspect all ducts before concrete is poured to ensure they are clean and free from burrs. Installation of ducts should comply with Section 15.2.2 of the project specification. |  |  | Witness point | Photographs
10 | Laying cable, ducts, pits and installing light foundations | H | When crossing existing cables | Whenever crossing existing cables | Testing | New Cables/ ducts must be: -Crossing below existing with a minimum vertical separation of 100mm - Provide at least 50mm of new bedding material above and below the existing cables. -The bedding material shall extend 100mm beyond the edge of the outside cables. – IR test the affected direct buried circuits immediately after the backfill to ensure the existing cables were not damaged during excavation. | Test results and Photographs
|  | H | All pit installations and amendments should occur in compliance with section 15.5 of the specification. | During installation or amendment | Visual inspection | Section 15.5 of speciifications | Photographs, ITS Pit Intallation Checksheet
|  | H | 150 mm wide PVC marker tape bearing the words "Caution - Buried Electric Cables Below" shall be laid above all new cable ducts for their entire length. | Across each trench | Visual inspection |  | Photographs | Site Engineer
11 | Duct Installation | H | Complete checksheet for Duct installation | During Construction | Visual and measurement | Complete for each run between pull pit/jointing chamber | FHIMS-CS-4048 | Site Engineer
12 | Joint Chamber/Pull Pit Installation | H | Complete checksheet for chamber and pit installation | During Construction | Visual and measurement | Complete form for each Pull Pit or Jointing Chamber installed | FHIMS-CS-4072 | Site Engineer
13 | Backfilling cable trenches | H | When not under pavement Compaction testing should be undertaken at a rate of 1 test per 400m of conduit laid per 0.5m of backfill depth (minimum 3). Compaction Testing under pavements shall be carried out every 25m and every 0.5m lift. | Along Each Trench | Clegg testing | Where trenches are under constructed pavements and shoulders, or generally in dry conditions, the backfill shall be compacted to a relative dry density of not less than 95% of maximum dry density (test No. 5.1.1 of AS1289) in the case of cohesive material, or 75% Density Index (test No. E6.1 of AS1289) in the case of cohesionless material. | Clegg testing results form
14 | Testing | H | Testing to be carried out by Subcontractor and approved Test sheets to be completed. (min. 1 per supply box) | Upon completion of installing lights | Test results | Specification requirements | Subcontractor QA forms and certificate of compliance | Site Engineer
15 | Commissioning | H | Demonstrating that specific Commissioning requirements details in the Specification have been complied with. | Upon completion of installing lights | Document review / Testing | Road lighting Specification Section 8 | Subcontractor QA forms and certificate of compliance | Site Engineer
16 | As-builts | H | Provide complete As-builts of both existing and Installed cables and ducts. | At the completion of the Lot of work | Drawings |  | Asbuilt Drawing | Site Engineer
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/OFIs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Discipline Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By Principals Rep : |  |  |  |  | Signature: |  |  | Date: