## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP030 - ALER 3 Groundworks | itp |  |  |  |  | FH-ZU2-QU-ITP030 - ALER 3 Groundworks - Rev 0
section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings.
label | – all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.3 - Definition of the work area (survey)
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
label | ○ Pits & trenches all marked out prior to excavation commencing
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 1.4 - Material submissions and pipe compliance
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Material submission of:
label | ○ Electrical
label | – Ensure uPVC conduits comply with AS 1477 or equivalent AS 2053
label | – Shall be heavy duty, orange for electrical services and white for communication services
label | – Ensure pipe diameter is correct AS per drawings
label | ○ Stormwater/Sanitary Drainage – Below Ground
label | – uPVC Non Pressure Pipes shall be DWV MIN SN8 Solvent Welded to AS 1462 with an environmental product
label | – uPVC pipe Shall be SN10 SWJ AS per DCWC Mgt-RTRFI-1317
label | ○ Cold Water – Below Ground
label | – Polyethylene pipe shall be used conforming to AS 4130 & 4131
label | Reference Documents - Drawings
label | ○ ZULU-BECA-001-SPC-00004 Cl. 3.4
label | ○ ZULU-BECA-001-SPC-00005
label | ○ Table C1710-A, AS1477, AS 2053, AS 1462, AS 4401, AS 3500.3, AS 4130, AS 4131
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference, This Signed ITP, Building Engineering ITC
label | HP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Check bedding material compliance
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Electrical
label | – Ensure that the conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification
label | ○ Stormwater/Sanitary Drainage/Water
label | – Ensure Bedding Material is Well Graded
label | – Manufactured Sand to VicRoads Specification 407 Clause 407.03(f).
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.8.3.3
label | ○ ZULU-BECA-030-DWG-00201 Note D03
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference, This Signed ITP, Building Engineering ITC
label | HP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Material Submissions and Shop Drawings
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Submission of:
label | – Spel Puraceptor for approval prior to commencing works.
label | – Septic Tank & Sewer Disposal Unit Design
label | – Pre-cast Pits for approval prior to commencing works
label | – Precast headwalls
label | Reference Documents - ZULU-BECA-001-SPC-00005
label | ○ Drawings C1700 cl. 3a AS 1546.1-2008.2
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference, Building Engineering ITC
label | HP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Permits & relevant approvals obtained
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Excavation Permit
label | – Location of services to be found and marked on the ground within the works;
label | – Contractor to obtain excavation permit from APAM prior to any demolition works.
label | – Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
label | ○ Service conduits shall be protected from damage due to subsequent construction operations as required using whatever measures are necessary. Any damaged conduits shall be removed and replaced at no cost to the Principal.
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.15
label | ○ WMS-002
label | Inspection/Test Method - Verify
label | Record of conformity - Melbourne Airport Excavation Permit, PIC
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 1.8 - Native Grass Protection
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Native grass protection installed. As per native grass model
label | Reference Documents - Relevant Native Grass Permit
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - FH-ZU2-QU-ITP038, This ITP Signed
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
section | 2.0 - Construction - Stormwater
checkpoint | 2.1 - Excavate trenches for pipes
label | Frequency - Each lot
label | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
label | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
label | Reference Documents - Drawings AS 1289
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.2 - Existing services crossing new pipes
label | Frequency - Each lot
label | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
label | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | Reference Documents - WMS002 – Working Near Existing Services
label | Inspection/Test Method - Visual inspection
label | Record of conformity - As-built survey report
label | SCP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 2.3 - Laying and jointing of pipes
label | Frequency - Each lot
label | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
label | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
label | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
label | – Lay at MIN grade 1:100 UNO.
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 2.4 - Pre-backfill inspection & testing
label | Frequency - Prior to backfilling each lot
label | Acceptance Criteria - HOLD POINT
label | ○ Backfilling of the trenches shall not proceed until the pipeline has been tested and inspected.
label | ○ Check for leaks to the requirement of clause 15.2 of AS3500.2
label | – Inspect for proper laying and jointing
label | – Pipeline has continuity in fall
label | – Expansion/swivel joints provided for all pipework
label | – Testing as per AS 3500.3 to be carried out
label | • Water Test
label | • Air Test
label | – Building Engineering to run camera through Stormwater pipeas and upload link
label | Reference Documents - Drawings
label | ○ ZULU-BECA-001-SPC-00005 C1700.8 2c, C1700.2 .2a, AS 3500.2
label | ○ Building Engineering ITC
label | Inspection/Test Method - Visual Inspection, Test Result
label | Record of conformity - This ITP signed, Building Engineering ITC
label | HP/TP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 - Construction – Sanitary Drainage
checkpoint | 3.1 - Excavate trenches for pipes
label | Frequency - Each lot
label | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
label | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
label | Reference Documents - Drawings AS 1289
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.2 - Existing services crossing new pipes
label | Frequency - Each lot
label | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
label | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | Reference Documents - WMS002 – Working Near Existing Services
label | Inspection/Test Method - Visual inspection
label | Record of conformity - As-built survey report, Building Engineering ITC
label | SCP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 3.3 - Laying and jointing of pipes
label | Frequency - Each lot
label | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
label | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
label | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
label | – Lay at MIN grade 1:100 UNO.
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 3.4 - Pre-backfill inspection and Testing
label | Frequency - Prior to backfilling each lot
label | Acceptance Criteria - HOLD POINT
label | – Pipeline will need to be tested and inspected prior to any backfilling
label | – Inspect for proper laying and jointing
label | – Pipeline has continuity in fall
label | – Expansion/swivel joints provided for all pipework
label | – Use temporary capping to isolate piping to be tested; fill piping with clean water and check for leaks to the requirement of clause 15.2 of AS 3500.2
label | – After testing, drain and reconnect the piping, flush the drains clean with water and check for fall to discharge
label | – Building Engineering to run camera through Sanitary pipes and upload link
label | Reference Documents - Building Engineering ITC, ZULU-BECA-001-SPC-00005 C1700.8 .2 C AS 3500.2
label | Inspection/Test Method - Visual Inspection, Test Result
label | Record of conformity - This ITP signed Camera Footage, Building Engineering ITC
label | HP/TP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 4.0 - Construction – Cold Water Pipes
checkpoint | 4.1 - Excavate trenches for pipes
label | Frequency - Each lot
label | Acceptance Criteria - Trenches for pipes shall be excavated to the width and depth required enabling construction of the pipes to the requirements specified on the drawings.
label | – Inconsistent, rocky or soft material at base of trench shall be excavated and replaced with compacted select fill
label | Reference Documents - Drawings AS 1289
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 4.2 - Existing services crossing new pipes
label | Frequency - Each lot
label | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
label | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | Reference Documents - WMS002 – Working Near Existing Services
label | Inspection/Test Method - Visual inspection
label | Record of conformity - As-built survey report, Building Engineering ITC
label | SCP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 4.3 - Laying and jointing of pipes
label | Frequency - Each lot
label | Acceptance Criteria - Pits, pipes & structures shall be constructed to the line, levels and dimensions shown on the drawings
label | – Pipes shall be bedded evenly on sand compacted to min 100mm thickness below the socket
label | – Pipe laying Shall be constructed at the downstream end of the pipe run. all Pipes Shall be laid with sockets pointing upstream
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 4.4 - Pre-backfill inspection and Testing
label | Frequency - Prior to backfilling each lot
label | Acceptance Criteria - HOLD POINT
label | ○ Pipeline will need to be tested and inspected prior to any backfilling
label | ○ Inspect for proper laying and jointing
label | ○ Conduct Pressure Test and Flushing of the Pipeline
label | – Prior to testing, flush all pipework and equipment with clean potable water until the flushed water runs out completely clear
label | – Pressurise with clean potable water (free of oil and other impurities) and maintain the test pressure for 2 hrs
label | – Immediately after successful testing, final flush all pipework and equipment with clean potable water at “full flow” for at least 10 minutes
label | ○ In addition to general flushing and cleaning requirement above, disinfect and passivate pipework systems in accordance with AS 3500.1 and any relevant manufacturer written instructions
label | Reference Documents - Drawings ZULU-BECA-001-SPC-00005 C1700.8 .2 a AS 3500.1
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | HP/TP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 5.0 - Construction – Electrical & Comms
checkpoint | 5.1 - Excavate trenches for conduits
label | Frequency - Each lot
label | Acceptance Criteria - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
label | – The level at the bottom of the trench shall not be above the required level at any point.
label | Reference Documents - Drawings ZULU-BECA-001-SPC-00004 cl. 3.6
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP / TP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 5.2 - Existing services crossing new conduits
label | Frequency - Each lot
label | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
label | – Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | Reference Documents - WMS002 – Working Near Existing Services
label | Inspection/Test Method - Visual inspection
label | Record of conformity - As-built survey report, Building Engineering ITC
label | SCP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 5.3 - Laying and jointing of conduits
label | Frequency - Each lot
label | Acceptance Criteria - All conduits shall be rigidly supported and positioned by concrete former or plastic spacer blocks so that no displacement occurs during backfill.
label | – Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
label | – Number of conduits and duct route to be confirmed for conformity with design.
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.7
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 5.4 - Pre-backfill inspection
label | Frequency - Prior to backfilling each lot
label | Acceptance Criteria - HOLD POINT
label | ○ All trenches shall be inspected by the Contract Administrator before backfilling takes place.
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.8.1
label | Inspection/Test Method - Inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | HP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.5 - Conduit markers & warning tape
label | Frequency - Each lot
label | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
label | – Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.11, cl. 3.12 AS 2648.1
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 5.6 - Checking of conduit lines
label | Frequency - Each lot
label | Acceptance Criteria - - Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.9
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 5.7 - Conduit draw cord
label | Frequency - Each lot
label | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
label | Reference Documents - ZULU-BECA-001-SPC-00004 cl. 3.10
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
section | 6.0 - Backfilling
checkpoint | 6.1 - Survey AS BUILT
label | Frequency - Each lot
label | Acceptance Criteria - Surveyor to pick up completed pipe/conduit runs & underground tanks before backfill
label | Reference Documents - FH QMP
label | Inspection/Test Method - Verify / Inspection
label | Record of conformity - Survey Report
label | SCP / IP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 6.2 - Backfilling Conduits/Pipes
label | Frequency - Each lot
label | Acceptance Criteria - Bedding
label | – Bedding material shall encase the pipe to 100mm compacted thickness above the pipe and be compacted simultaneously around both sides of the pipe
label | ○ Backfill
label | – Backfill remaining area with site won material from excavations and compact in minimum 200mm thick layers
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Building Engineering ITC
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 6.3 - Testing of Trench Backfill
label | Frequency - Each Lot
label | Acceptance Criteria - The minimum frequency of field density tests shall be in accordance with AS3798 table 8.1 and not less than 1 test per 50m of compacted backfill in each layer of pipe trench fill.
label | Reference Documents - Drawings AS3798 Table 8.1
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Test Results
label | TP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
checkpoint | 6.3 - Surface Reinstatement
label | Frequency - Each Lot
label | Acceptance Criteria - Pavement Areas
label | – Final backfilling in existing pavement areas shall to 100% compaction
label | – Mechanically compacted in max 150mm layers
label | – Basecourse depth shall be 400mm or existing pavement depth, whichever is greater
label | ○ Grassed Areas
label | – The final 100mm of backfilling shall be clean topsoil
label | Reference Documents - ZULU-BECA-001-SPC-000All 05 C1772.6 .1 AS 2566
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP Signed, Building Engineering ITC
label | HP*
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
section | 7.0 - Construction – Precast Pits, Headwalls, & Underground Tanks
checkpoint | 7.1 - Placement of Septic & SPEL Tanks
label | Frequency - Each lot
label | Acceptance Criteria - Ensure placement of tanks is as per manufacturer specification and as per design levels
label | Reference Documents - Drawings, Manufacturer’ s Specification
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 7.2 - Placement of Pits and Headwalls
label | Frequency - Each lot
label | Acceptance Criteria - Pits placed and levelled as per survey set out
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed.
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 7.3 - Bedding & Backfill of pit surrounds
label | Frequency - Each lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Each pit/headwall shall be bedded and be backfilled with stabilised sand for grassed areas.
label | ○ Principals Representative shall be notified to inspect installed pits with all connections prior to backfilling
label | Reference Documents - ZULU-BECA-001-SPC-00004 Drawing 00201
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | WP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
checkpoint | 7.4 - Pit Close out
label | Frequency - Each lot
label | Acceptance Criteria - Pits shall be labelled and directional markers placed. Lids to be secured and area cleaned/demolished
label | Reference Documents - ZULU-BECA-001-SPC-00004
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: