## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
1aa8fe7a-efe7-47fb-813a-536db1f77bd5 | checklist | Piling ITC-ITR | itp | Piling ITC-ITR
| section | Location Details
| checkpoint | Details
| dropdown | Site Reference | 1,2,3,4,5,6,7,8,9,10,11,12,13,14
| textbox | Row Number
| textbox | Table Number
| note | Number of Piles
| tickbox | 8 Pile
| tickbox | 16 Pile
| tickbox | Other
| textbox | Specify (if other)
a219c084-211b-497e-9655-b33b5a952115 | section | Preconstruction
df265595-fbbf-42b7-a619-0357aafb9a20 | checkpoint | Design
d9e1e7aa-82a5-57af-8949-59e70427105d | note | DETAIL - Issued For Construction Drawings:
82b203c0-a88f-5fb4-90e6-5f2157fff1b0 | note | ○ 01_Maungaturoto_FS2V-23*-12_DUO_EX
6d8cb754-792a-5dab-adf6-b40336ad1c92 | note | ○ 02_Maungaturoto_FS2V-23*-12_DUO_EX
efb8b002-06b7-522f-8478-f7abcf61ef68 | note | ○ Schletter Electronic Design Data
b0e840f2-6cd7-5f31-bac7-859691527b9f | note | ○ Schletter FS DUO - Fixed-tilt Installation Procedure
17427730-27d9-4da8-8f90-f33c2110b11e | checkpoint | Survey & Setout
861dac78-6e13-5613-a403-6898ca8bcbc8 | note | DETAIL - Schletter Electronic Design Data
a5d04b01-1ed3-5ba6-be47-0afb98c95c04 | note | – Schletter FS DUO - Fixed-tilt Installation Procedure
2ecdf5df-56c7-575f-b896-ea0871b47440 | note | Survey As Constructed Record
0e3aaac0-c076-5130-93e8-7d7223c8b768 | note | – Pile Location Spreadsheet
a9b3141c-864a-482f-937b-0655e09bef37 | checkpoint | Inspection Measuring and Test Equipment Registers (IMTE)
302074bb-3b96-5cb8-abab-e347c7eaae0b | note | DETAIL - Supply of all calibration certificates
55a020a7-eac1-4de6-a289-34e496249fc9 | section | Construction
39833662-c589-4ae9-b77d-310e57684704 | checkpoint | Pile Distribution to respective blocks
a0d8f14c-1504-528c-bc1f-a4380e6ef4fc | note | DETAIL - Survey Data
97dd043d-e46e-5c55-8d29-650df9378c92 | note | – Schletter pile location data
e8f2bbbd-9218-55f4-b008-9390c6edd6fa | note | Visual Inspection
483d876c-14e8-5566-8690-2ffac677535b | note | – Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length
4431ef6b-c534-4a65-8e19-c9ff55f11472 | checkpoint | Pile Refusal
2d9606fe-9c20-5949-bbc1-950499556ccc | note | DETAIL - Drive piles to depth until they reach the point of refusal
1bdcf022-ad39-5981-ba16-9e1a2d8db269 | note | ○ Record Pile location and mark on the drawing
3fe17daf-7603-5f6e-b40e-ff448f1d2def | note | ○ Record Actual Pile embedment Depth
c5253134-b65e-5793-aeb4-d73fbc4fd9db | note | ○ Pile refusal in accordance with pile refusal procedure
15780ad4-276a-5979-8312-3e258822617c | note | ○ Piles cut and holes drilled as per Schletter documentation
cb99b93e-48bc-525c-84b2-57b7503066f6 | note | ○ Survey Record
1c95827f-6180-5ac4-ba87-c552344aeda2 | note | ○ ITC Data Tracker Excel Pile Monitoring Sheet
d71a3ec1-557f-5cdb-a2c1-11965faa995a | note | – Embedment Depth
ace3a38c-a725-598b-aadc-60a9d0b00ad9 | note | – Reveal Height
469f3ba5-2a80-5a47-851f-86e29182b187 | note | ○ Pile Test Result documentation
219063f5-0123-4a91-b4b2-f4298c4c0121 | checkpoint | Pile Predrill to minimum embedment
8b695eba-fa50-56e1-88d4-32be98e5f007 | note | DETAIL - For Each Pile
a56820fb-f868-5ee2-a8a1-49f694cfd3da | note | ○ Pile Predrill ITC
545fce39-353b-5c82-933a-7afd912e9008 | note | ○ Piles are minimum of 1.8m deep
d1299ce2-220d-540c-a869-a7b62eb3be25 | note | ○ Predrill holes are minimum of 300mm dia
53072a89-de01-55aa-b25b-d3da1b4cec45 | note | ○ Backfilled with approved mix as per Schletters Installation Procedure
7067ddb6-176a-47f1-ac00-714b24294b99 | checkpoint | Pile Installation
4ab201b8-325d-54e1-b0e2-f4f322bda00a | note | DETAIL - Schletter FS Duo Fixed-tilt Installation Procedure
6f05d5f9-d1f1-5ceb-9a87-c3a548966842 | note | ○ Install Pile on the correct location as per Schletter drawing
e804a45d-225e-5213-b07d-0cb9b761afa8 | note | ○ Install pile within the design tolerances
94a74d95-d445-5631-af46-7930bf75e248 | note | ○ Piles should have no damage or deformation and in correct orientation
e92ff3e3-aeef-51e2-8b95-179c3815650c | note | – North/South +/- 3°
fea94fde-1aa8-5779-9967-b885429bebc4 | note | – East/West +/- 3°
192a15be-4cde-5995-858e-2d2e947d9b1b | note | – Pile Twisting from axis +/- 5°
e51c4bc9-c700-5aa7-b2f8-f14dc346381c | note | – Distance E/W +/- 100mm
4eb3bdc7-4ed0-5d56-bceb-9052de1adf78 | note | – N/S +/- 50mm
2dee765a-727a-5b66-a584-1f9fced15e2f | note | – Reveal Height +/- 100mm
336de278-b945-522e-aa46-6103c6efcbb3 | note | – Height difference foundation posts within one row +/- 50mm
8322e0ef-ed95-5187-b2e1-86ee583d440e | note | ○ Piles have no damage deformation and in correct orientation
0efebad7-58c0-4da9-be80-b1e10b0f59cd | checkpoint | Cold Galvanising Repair, if required
9056c325-4af8-5d44-a1be-f40836cf8739 | note | DETAIL - Schletter FS Duo Fixed-tilt Installation Procedure
08a45031-d583-582b-93c0-743268119f0a | note | ○ Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer
e1e83219-109a-4c69-8a3c-b26dd76c0c04 | section | Close-Out
ac7fde1b-3de6-410b-aa3b-9dba89ed61e1 | checkpoint | As Constructed - Redline Markup Drawings
21e9d27c-d547-5ac7-9465-4b6c8b6b0cfd | note | DETAIL - At completion of the the piling for each area
bc2ef1d6-024f-537e-b80a-ee0fd505268c | note | ○ Markup Redline Asbuilts if different from design and identify changes
c435b98f-14e1-47c8-af64-7205a349cdaa | checkpoint | Non-Conformance-Reports
b48e587d-20cf-55f4-9ceb-510b6fd59008 | note | DETAIL - Non-Conformances Closed Out
d908d32d-8bc9-4f1b-9a64-87b9dd64a5f7 | checkpoint | Punch List
66622c05-e3b4-5b54-a276-6f5b14b2a9a9 | note | DETAIL - Development of Punchlist with PM/CM and or Supervisor
bb9f667e-43ed-58bc-9dda-b8b6ee52febf | note | ○ Punch List closed out in a timely mannor
491ef4e9-a52b-4ac8-9e5e-037975e5e1d1 | checkpoint | Handover
bdc2a349-aa53-5a6d-9996-b06b1fed3cbb | note | DETAIL - At completion of works QA/QC Pack is handed to client
4589aa80-5f1a-5165-b7f2-026cf525acf2 | note | ○ Client Verifies Work has been completed correctly and all quality documents are in order
12f849a7-b205-4495-b696-cb187a69794d | signoff | HOLD POINT