## Piling
Piling ITC/ITR
| Heading | Detail | Buttons etc
Preconstruction
| Design | Issued For Construction Drawings: 01_Maungaturoto_FS2V-23*-12_DUO_EX 02_Maungaturoto_FS2V-23*-12_DUO_EX Schletter Electronic Design Data Schletter FS DUO - Fixed-tilt Installation Procedure | P,F,Attachment
| Survey & Setout | Schletter Electronic Design Data Schletter FS DUO - Fixed-tilt Installation Procedure Survey As Constructed Record Pile Location Spreadsheet | P,F,Attachment
| InspectionMeasuring and Test Equipment Registers (IMTE) | Supply of all calibration certificates | P,F,Attachment
Construction
| Pile Distribution to respective blocks | Survey Data Schletter pile location data Visual Inspection Piles distributed as per Schletter drawings, ie correct colour, code , dimensions and length | P,F,Attachment
| Pile Refusal | Drive piles to depth until they reach the point of refusal Record Pile location and mark on the drawing Record Actual Pile embedment Depth Pile refusal in accordance with pile refusal procedure Piles cut and holes drilled as per Schletter documentation Survey Record ITC Data Tracker Excel Pile Monitoring Sheet - Embedment Depth - Reveal Height Pile Test Result documentation | P,F,Attachment
| Pile Predrill to minimum embedment | For Each Pile Pile Predrill ITC Piles are minimum of 1.8m deep Predrill holes are minimum of 300mm dia Backfilled with approved mix as per Schletters Installation Procedure | P,F,Attachment
| Pile Installation | Schletter FS Duo Fixed-tilt Installation Procedure Install Pile on the correct location as per Schletter drawing Install pile within the design tolerances Piles should have no damage or deformation and in correct orientation North/South +/- 3° East/West +/- 3° Pile Twisting from axis +/- 5° Distance E/W +/- 100mm N/S +/- 50mm Reveal Height +/- 100mm Height difference foundation posts within one row +/- 50mm Piles have no damage deformation and in correct orientation | P,F,Attachment
| Cold Galvanising Repair, if required | Schletter FS Duo Fixed-tilt Installation Procedure Upper 30mm of the inside and outside of the pile is coated with a zinc rich primer | P,F,Attachment
Close-Out
| As Constructed - Redline Markup Drawings | At completion of the the piling for each area Markup Redline Asbuilts if different from design and identify changes | P,F,Attachment
| Non-Conformance-Reports | Non-Conformances Closed Out | P,F,Attachment
| Punch List | Development of Punchlist with PM/CM and or Supervisor Punch List closed out in a timely mannor | P,F,Attachment
| Handover | At completion of works QA/QC Pack is handed to client Client Verifies Work has been completed correctly and all quality documents are in order | HoldPoint, P,F,Attachment